## Setup
Enter Stakeholder Group Name in cell A2:
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Fuel Requirements for Black Start Resources

## 1. Interest Identification
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
OC Interest Identification
1 | Sufficient black start capabilities be available regardless of situation
2 | Improve fuel assurance for black start resources
3 | Support all fuel type eligibility for black start resources
4 | Avoid creating stringent requirements that eliminate existing black start resources
5 | Clearly define performance standards for operating hours during a restoration event for each fuel type
6 | Clearly define testing requirements related to fuel security
7 | Explore options for fuel assurance/storage requirements
8 | Determine if fuel requirements for black start resources have to be defined in the Manuals and/or the OATT
9 | In the transiton or implementation phase for existing units, include an RFP type procurement process.
10 | Ensure storage resources are included in proper compliance with order 841.
11
12
13
14
15
16
17
18
19
20

## 2. Options Matrix- Design Comp.
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
OPTIONS MATRIX
Solution Options
# | Design Components | Priority | Status Quo | A | B | C | D | E
A | Level of Fuel Assurance for Black Start resources |  | N/A | All black start resources allocated to a TO zone must be fuel assured. | Determine the number of black start resources that have to be fuel assured allocated to each TO zone based on an analysis. | X% of black start resources allocated to a TO zone must be fuel assured. | Minimum of two black start resources allocated to the TO zone at separate sites must be fuel assured. Determine the black start resources that have to be fuel assured based on an analysis.
B | Universal Black Start Fuel Assurance Requirements
1 | Duration / Run Hour requirements | High | 16 hours per blackstart resource (even if resources on the same site share a common fuel source) | 16+ Hours per blackstart resource | 24 Hours per blackstart resource
2 | Emissions Permit Limitations | Medium | Different states and black start resources have various limitations for emission waivers. PJM currently does not track. | Requirements for the fuel assured black start resources to obtain emission permit waivers to accommodate operations during a restoration situation (operating below normal economic min values), if required. | No requirement but higher weighting will be applied during the black start RFP process to resources with emission permit waivers. | PJM will provide education and awareness to states and coordinate/develop waiver process. PJM will create a template for emission waivers. | Requirements for the fuel assured black start resources to obtain operating permit conditions to accommodate operations during a restoration situation (operating below normal economic min values), if required.
3 | Non-Fuel Consumables (eg. water, ammonia) | High | None | Capable of supporting the duration of the run hour requirement.
C | Black Start Fuel Assurance Solutions by Primary Fuel Type
1 | Natural Gas | High | 16 hours of run hour requirements | Limitations based on the number of resources within the same pipeline segment | Not allowed to be a fuel assured black start without on-site fuel capability. | non-fuel assured black start must have firm gas transport
1a | Dual Fuel Capability | High | n/a | Resources must be able to start solely on onsite fuel | Secondary fuel must be stored on site for each black start resource (if they share a common fuel source) to meet the run hour requirements.
1b | Pipeline requirements | High | n/a | Primary firm gas transportation contract with an annual availability period | Primary firm gas transportation contract with a winter availability period | Physically independent connections to more than one interstate natural gas pipeline
2 | Oil | High | 16 hours of run hour requirements | oil storage on site at all times for each black start unit in a site to meet minimum run time requirements (if resources shares the same fuel source) | Firm refueling contracts | Firm oil pipeline connections
3 | Hydro (Run of River) | High | 16 hours of run hour requirements | Analysis with X % of confidence of most restrictive seasonal flow to support the assigned black start MW. | Performance verification will be based on the most limiting season of the past X years of performance history. | Single site simultaneous verification test
4 | Hydro (Pumped Storage) | High | 16 hours of run hour requirements | The pond level must be maintained to satisfy run hour requirements to meet the black start commitment. | Pond level must be maintained to satisfy run hour requirements and telemetry. | Use the 24 Hour Capacity factor rather than ICAP. If wish to use as non-assured fuel resources, then use the traditional ICAP value and have a 16 hour run requirement.
5 | Energy Storage Resources | High | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Must meet min run time duration requirements. | Use the 24 Hour Capacity factor rather than ICAP. | Stored energy must always be kept onsite for each black start unit to meet minimum run time requirements
6 | Hybrid Resources | Low | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Must meet min run time duration requirements. | Use the 24 Hour Capacity factor rather than ICAP. | A combination of onsite fuel inventory, water level, stored energy, etc. must always be kept onsite for each black start unit to meet minimum run time requirements
7 | Intermittent Resources | Low | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Analysis with X % of confidence of most restrictive season to support the assigned black start MW.
8 | DER/DR with onsite generator | Medium | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Must meet min run time duration requirements. | Not allowed to be a fuel assured black start resource without on-site fuel capability.
D | Fuel Assurance Testing & Verification Requirements
1 | Dual fuel unit testing | High | None | Separate testing for each fuel in the same year | Separate testing for each fuel on alternate years
2 | Concurrent fuel testing | High | None | All black start units connected to the same fuel source test concurrently
3 | Online fuel transition testing | Medium | None | One test per year to demonstrate the ability to switch between fuels. | Provide data on fuel switching restritctions/limitations that unit may have.
4 | Fuel inventory verification | Medium | Black start CTs reports to PJM dispatch and units are placed in max-emergency when they carry less than 10 hours of fuel (M14d). Some hydro units report pond levels via telemetry. | Fuel verification atleast at X frequency or upon PJM request | Telemetry of fuel inventory | Black start units report to PJM dispatch and units are placed in max-emergency when they carry fuel less than the minumum run hour requirement | Fuel verification on black start test forms. | Based on resource unit and fuel type, onsite fuel inventory, water level, stored energy, etc. must be confirmed to PJM on a monthly basis via eDART or telemetry if preferred.
5 | Black start MW capability determination | High | Each Unit's ICAP MW is currently used for unit compensation | Black start MW capability based on the most limiting season, if applicable. | Black start MW capability must take into account unit limitations i.e Steam bypass, if applicable
6 | Black start MW capability verification | High | The annual capacity test | All black start units connected to the same fuel source test concurrently
7 | Emission permit limitation verification |  | n/a | Black start resource owners will certify using written waivers or other applicable documentation that emission permit limitations are available during restoration operations, as applicable.
E | Fuel assurance compensation | High | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A. | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A and also by taking into account run time hours | Ability to have black start resources recover incremental capital costs solely associated with fuel assurance. | Develop a methodology to determine which portion of the incremental capital costs are solely necessary for black start fuel assurance. | PJM will determine the portion of incremental capital costs expended for fuel storage that is solely necessary for black start by netting energy revenues that are a direct result of the capital expenditures during the capital recovery period |  | Medium
1 | Minimum Tank Suction Level (MTSL) | Low | Oil , propane and LNG black start units are compensated for carrying cost of the full MTSL volume. For black start units that share tanks only one unit gets compensated. | Oil , propane and LNG tanks shared between resources will proportionally share compensation of the MTSL value. | When black start resources share a fuel tank the black start resource compensation should include only an allocated share of the MTSL equal to the BS fuel requirement for 16 hours divided by the tank capacity times the MTSL. |  |  |  | Low
2 | Onsite fuel, water level, stored energy, etc. compensation | Medium | None | Develop a methodology to compensate water storage based on opportunity costs | If the onsite fuel inventory, water level, stored energy, etc. falls below the run hour requirements for any length of time during any period, PJM must be notified immediately. Black start monthly revenues will be foregone for months in which the fuel inventory is deficient.
F | Implementation |  | N/A | [5 empty] | Medium - High
1 | Existing Black Start resources | Medium - High | None | RFP process initiated by PJM within 6 months of FERC approval of OATT changes allowing existing non-fuel assured black start resources to submit proposals to become fuel assured and other non-black start resources to submit proposals to provide fuel assured black start service
2 | New Black Start resources | High | None | Add the requirement that any submission to a future RFP must meet the fuel assurance requirements. RFP process would not change beyond that.
3 | 2018 RTO wide RFP awarded Black Start resources | High | None | Non-fuel assured resources awarded in the 2018 RTO Wide RFP may participate in the PJM initiated RFP with proposals to meet fuel assurance requirements.
4 | Procuring additional black start resources because of deficiencies created by the new rules, as needed | High | None | Existing incremental RFP process would be used with the requirement that any submitted proposal meets the fuel assurance requirements. |  |  |  |  | High

## 2a. Design Component Details
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D
A | Level of Fuel Assurance for Black Start resources |  | N/A | All black start resources allocated to a TO zone must be fuel assured. | All black start resources within each TO zone must be fuel assured. | All black start resources must be fuel assured.
B | Universal Black Start Fuel Assurance Requirements
1 | Duration / Run Hour requirements | High | 16 hours per blackstart resource (even if resources on the same site share a common fuel source) | 16 hours per blackstart resource (even if resources on the same site share a common fuel source) | 16+ Hours | 24 hours per blackstart resource (even if resources on the same site share a common fuel source)
2 | Emissions Permit Limitations | Medium | Different states and black start resources have various limitations on operations of black start resources. PJM currently does not track. | Requirements for the fuel assured black start resources to obtain operating permit conditions to accommodate operations during a restoration situation (operating below normal economic min values), if required. | Requirements for the black start resources to obtain emission permit waivers to accommodate operations during a restoration situation, if required. | Same as PJM
3 | Non-Fuel Consumables (eg. water, ammonia) | High | None | Capable of supporting the duration of the run hour requirement. | Capable of supporting the duration of the run hour requirement. | Same as PJM
C | Black Start Fuel Assurance Solutions by Primary Fuel Type
1 | Natural Gas | High | 16 hours of run hour requirements | Not allowed to be a fuel assured black start without on-site fuel capability. | Limitations based on the number of resources within the same pipeline segment | Same as PJM
1a | Dual Fuel Capability | High | N/A | Resources must be able to start solely on onsite fuel AND Secondary fuel must be stored on site for each black start resource (if they share a common fuel source) to meet the run hour requirements. | Secondary fuel must be stored on site for each black start resource (if they share a common fuel source) to meet the run hour requirements. Unit must be able to start on secondary fuel type without natural gas | Same as PJM
1b | Pipeline requirements | High | N/A | N/A | Primary firm gas transportation contract with an annual availability period | N/A |  | Low
2 | Oil | High | 16 hours of run hour requirements | oil storage on site at all times for each black start unit at a site to meet minimum run time requirements (if resources share the same fuel source) | oil storage on site at all times for each black start unit in a site to meet minimum run time requirements (if resources shares the same fuel source) | Same as PJM |  | Low - Medium
3 | Hydro (Run of River) | High | 16 hours of run hour requirements | Analysis with X% of confidence of most restrictive seasonal flow to support the assigned black start MW. | Analysis with X% of confidence of most restrictive seasonal flow to support the assigned black start MW. | 24 hours of run hours requirements |  | Low - High
4 | Hydro (Pumped Storage) | High | 16 hours of run hour requirements | The pond level must be maintained to satisfy run hour requirements to meet the black start commitment. | The pond level must be maintained to satisfy run hour requirements to meet the black start commitment. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September) |  | Medium
5 | Energy Storage Resources | High | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Stored energy must always be kept onsite for each black start unit to meet minimum run time requirements | Must meet min run time duration requirements. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September) Stored energy must always be kept onsite for each black start unit to meet minimum run time requirements. |  | Medium - High
6 | Hybrid Resources | Low | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | A combination of onsite fuel inventory, water level, stored energy, etc. must always be kept onsite for each black start unit to meet minimum run time requirements | Must meet min run time duration requirements. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September) A combination of onsite fuel inventory, water level, stored energy, etc. must always be kept onsite for each black start unit to meet minimum run time requirements |  | High
7 | Intermittent Resources | Low | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Analysis with X% of confidence of most restrictive season to support the assigned black start MW. | Must meet min run time duration requirements. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September). Must have the ability to start within 180 minutes if not in a forced or planned outage.
8 | DER/DR with onsite generator | Medium | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Not allowed to be a fuel assured black start resource without on-site fuel capability. | Must meet min run time duration requirements. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September). Must have the ability to start within 180 minutes if not in a forced or planned outage.
D | Fuel Assurance Testing & Verification Requirements
1 | Dual fuel unit testing | High | None | Separate testing for each fuel in the same year | Separate testing for each fuel in the same year | Same as PJM. Paid for testing.
2 | Concurrent fuel testing | High | None | All black start units connected to the same fuel source test concurrently | All black start units connected to the same fuel source test concurrently | Same as PJM. Applies to more than Oil/Gas units. Paid for testing.
3 | Online fuel transition testing | Medium | None | One test per year to demonstrate the ability to switch between fuels. | One test per year to demonstrate the ability to switch between fuels. | Same as PJM. Paid for testing.
4 | Fuel inventory verification | Medium | Black start CTs reports to PJM dispatch and units are placed in max-emergency when they carry less than 10 hours of fuel (M14d). Some hydro units report pond levels via telemetry. | Based on resource unit and fuel type, onsite fuel inventory, water level, stored energy, etc. must be confirmed to PJM on a monthly basis via eDART or telemetry if preferred. | Fuel verification at least at X frequency or upon PJM request | Same as PJM.
5 | Black start MW capability determination | High | Each Unit's ICAP MW is currently used for unit compensation | Black start MW capability based on the most limiting season, if applicable. | Black start MW capability based on the most limiting season, if applicable. | Black Start capability based on 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September)
6 | Black start MW capability verification | High | The annual capacity test | All black start units connected to the same fuel source test concurrently | All black start units connected to the same fuel source test concurrently | Same as PJM. Paid for testing.
7 | Emission permit limitation verification |  | n/a | Black start resource owners will certify using written waivers or other applicable documentation that emission permit limitations are available during restoration operations, as applicable. | Black start resource owners will certify using written waivers or other applicable documentation that emission permit limitations are available during restoration operations, as applicable. | Same as PJM.
E | Fuel assurance compensation | High | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A. | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A and also by taking into account run time hours AND Ability to have black start resources recover incremental capital costs solely associated with fuel assurance. PJM will determine the portion of incremental capital costs expended for fuel storage that is solely necessary for black start by netting energy revenues that are a direct result of the capital expenditures during the capital recovery period. | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A and also by taking into account run time hours | Same as PJM
1 | Minimum Tank Suction Level (MTSL) | Low | Oil , propane and LNG black start units are compensated for carrying cost of the full MTSL volume. For black start units that share tanks only one unit gets compensated. | When black start resources share a fuel tank the black start resource compensation should include only an allocated share of the MTSL equal to the BS fuel requirement for 16 hours divided by the tank capacity times the MTSL. | When black start resources share a fuel tank the black start resource compensation should include only an allocated share of the MTSL equal to the BS fuel requirement for 16 hours divided by the tank capacity times the MTSL. | When black start resources share a fuel tank the black start resource compensation should include only an allocated share of the MTSL equal to the BS fuel requirement for 24 hours divided by the average daily tank level from prior delivery year times the MTSL.
2 | Onsite fuel, water level, stored energy, etc. compensation | Medium | None | If the onsite fuel inventory, water level, stored energy, etc. falls below the run hour requirements for any length of time during any period, PJM must be notified immediately. Black start monthly revenues will be foregone for months in which the fuel inventory is deficient. |  | If the onsite fuel inventory, water level, stored energy, etc. falls below the run hour requirements for any length of time during any period, PJM must be notified immediately. Black start monthly revenues will be foregone for months in which the fuel inventory is deficient, except if do to an impplamented PAH or actual system restoration.
3 | Fuel Assurance Testing Compensation |  | None | Compensation to be similar to current Black start testing. Compensation for both tests on both fuels for dual fuel units. | Compensation to be similar to current Black start testing. Compensation for both tests on both fuels for dual fuel units.
F | Implementation |  | N/A
1 | Existing Black Start resources | Medium - High | None | RFP process initiated by PJM within 6 months of FERC approval of OATT changes allowing existing non-fuel assured black start resources to submit proposals to become fuel assured and other non-black start resources to submit proposals to provide fuel assured black start service. | RFP process initiated by PJM within 6 months of FERC approval of OATT changes allowing existing non-fuel assured black start resources to submit proposals to become fuel assured and other non-black start resources to submit proposals to provide fuel assured black start service. | Same as PJM. The cheaper of the new & existing resources will be selected, and the cost of terminating existing BS contracts will be included.
2 | New Black Start resources | High | None | New fuel assurance requirements would apply to any submission to a future RFP. RFP process would not change beyond that. | New fuel assurance requirements would apply to any submission to a future RFP. RFP process would not change beyond that. | Same as PJM.
3 | 2018 RTO wide RFP awarded Black Start resources | High | None | To be handled as Existing Black Start Resources. Non-fuel assured resources awarded in the 2018 RTO Wide RFP may participate in the PJM initiated RFP with proposals to meet fuel assurance requirements. | To be handled as Existing Black Start Resources. Non-fuel assured resources awarded in the 2018 RTO Wide RFP may participate in the PJM initiated RFP with proposals to meet fuel assurance requirements. | Same as PJM.
4 | Procuring additional black start resources because of immediate deficiencies created by the new rules, as needed | High | None | Existing incremental RFP process would be used with the requirement that any submitted proposal meets the fuel assurance requirements. | Existing incremental RFP process would be used with the requirement that any submitted proposal meets the fuel assurance requirements. | Same as PJM. The cheaper of the new & existing resources will be selected, and the cost of terminating existing BS contracts will be included.

## 3a. Package Details
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3