## 1. Interest Identification
PC - Enhanced Inverter
Interest Identification
Instructions: List interests of all parties on this page.
1 | Avoid a planning and operational issue within the eastern interconnection
2 | Proactively explore any issue effecting grid reliability
3 | Review existing standards and ensure they are relevant to emerging technologies as well
4 | Improve coordination/eliminate conflicts between interconnection standards for transmission-connected and distributed energy resources
5 | Leverage available grid-support capabilities of inverters to the extent possible
6 | Seek cost-effective solutions to reliability issues.
7 | Develop standards for PJM that have broad applicability in other regions and nationally.
8 | Extend applicability of standards to generation and storage connected at the distribution level
9 | Detailed specifications to maintain flexibility for TO voltage
10 | Develop recommenedation for over-frequency curtailment requirement
11 | Clearly define applicability as it relates to size, technology and interconnection process (transmisssion, distribution)
12 | Explore market based mechanisms to achieve the optimum result | PJM to research
13 | Explore other technology solution(s) than can provide grid services | PJM to research
14
15

## 2. Options Matrix- Design Comp.
PC - Enhanced Inverter
OPTIONS MATRIX
Strive for simplicity
Solution Options2
# | Design Components1 | Priority | Status Quo | PJM Package | B | C | D | References
1 | Active Power Control - upon request (curtailments) |  | No specific requirements for active power control for Inverter based technologies. Pool-scheduled or self-scheduled wind resources should only be eligible to receive LOC credits if they were operated according to Tariff, Operating Agreement, and PJM Manual requirements, specifically, supervisory control and data acquisition (“SCADA”) capability to transmit data and receive instructions from PJM to protect system reliability | All distributed generation connected through inverters should have the capability to receive and respond to curtailment instructions from dispatch |  |  |  | Attachement O- Schedule H of PJM Tariff; PJM Manual 14D Manual 12, Attachment B
2 | Active Power Control - automatic (e.g. for frequency control, or to limit ramp rates) |  | No specific requirements for active power control for Inverter based technologies. Pool-scheduled or self-scheduled wind resources should only be eligible to receive LOC credits if they were operated according to Tariff, Operating Agreement, and PJM Manual requirements, specifically, supervisory control and data acquisition (“SCADA”) capability to transmit data and receive instructions from PJM to protect system reliability | All distributed generation connected through inverters should have the capability to receive and respond to automated instructions from dispatch to reduce active power output. For e.g automated reduction in active power in response to high system frequency with droop characteristics |  |  |  | Attachement O- Schedule H of PJM Tariff; PJM Manual 14D
3 | Reactive Power Support / Power Factor Control - Central |  | For wind: 0.95 leading to 0.95 lagging if identified during the system impact study. For solar: No requirements | Minimum requirement is 0.95 leading to 0.95 lagging for all types of units unless system impact study establishes a need for more conservative limits |  |  |  | OATT at Part VI, Section 4.7 in Att. O, App. 2, of the Tariff for Reactive Power Requirements for new and existing facilities.
4 | Reactive Power Support / Power Factor Control - Autonomous |  | 0.95 leading to 0.95 lagging if identified during the system impact study. | Minimum requirement is 0.95 leading to 0.95 lagging for all types of units unless system impact study establishes a need for more conservative limits
5 | Voltage Ride-Through |  | Current regulations for LVRT come from FERC Order 661A and are documented in Manual 14B. LVRT requires wind turbine generators to stay connected to the grid for a number of conditions identified by FERC. This is specific for Wind Turbines and not applicable to other technologies. | Expand current Voltage ride through requirements for wind to all types of units |  |  |  | Schedule H of the PJM Tariff and Attachment G of Manual 14 B | Low
6 | Frequency Ride-Through |  | Inverter operation is mostly governed by IEEE 1547. IEEE 1547 drives inverter design more than any specific system requirements. | Adhere to NERC PRC-024 standard |  |  |  | PJM Tariff, Schedule H | Low - Medium
7 | Communication capabilities |  | Pool-scheduled or self-scheduled wind resources should only be eligible to receive LOC credits if they were operated according to Tariff, Operating Agreement, and PJM Manual requirements, specifically, supervisory control and data acquisition (“SCADA”) capability to transmit data and receive instructions from PJM to protect system reliability | Require all generation in the PJM interconnection queue greater than 20 MW to have capability to support two way communication |  |  |  | NA | Low - High
8 | Ramp rate control |  | Currently there are no PJM requirements. | Annual testing requirements to check that all types of units are able to comply with their stated ramp rate |  |  |  | NA | Medium
9 | [8 empty] | Medium - High
10 | [8 empty] | High
11
12

## 2a. Component Details
PC - Enhanced Inverter
COMPONENT DETAILS
Design Component |  | Detailed Description
1 | Active Power Control - upon request (curtailments) | Ability to limit active power output due to congestion/reliability in response to central control
2 | Active Power Control - automatic (e.g. for frequency control, or to limit ramp rates) | Ability to automatically control active power for reliability purposes
3 | Reactive Power Support / Power Factor Control - Central | Ability to absorb or generate reactive power under central control
4 | Reactive Power Support / Power Factor Control - Autonomous | Ability to absorb or generate reactive power under autonomous control
5 | Voltage Ride-Through | Ability to remain connected to the system during transient voltages
6 | Frequency Ride-Through | Ability to remain connected to the system during transient frequency
7 | Communication capabilities | Ability to have reliable and secure communication
8 | Ramp rate control | Ability to limit ramp rate in either direction

## 2b. Solution Details
PC - Enhanced Inverter
SOLUTION DETAILS
Package Solutions2
| A | B | C | D | E
1
2
3
4
5

## 3. Package Matrix
PC - Enhanced Inverter
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1
2
3
4
5
6
7
8
9 | [8 empty] | Low
10 | [8 empty] | Low - Medium
Low - High
Medium
Medium - High
High

## Parking Lot
PC - Enhanced Inverter
Interest Identification
Instructions: Use this space to document any items not specific to another topic area.
consideration for additional solutions other than inverters (ie - demand response)
inverter technolgies - what to pursue? - internal research