## Single Zone Allocations
File Posted: 11/4/2014
Revision 1 - Original Version
This document contains all of the new single zone and multiple zone cost allocations that the PJM Board is requested to approve in November 2014.
Upgrade ID | Description | Cost Estimate ($M) | Trans Owner | Required IS Date
b1793.1 | Remove the Carolina 22 SPS to include relay logic changes, minor control wiring, relay resets and SCADA programming upon completion of project | 0.025 | Dominion - 100% | 2016-05-01
b2006.2.1 | Upgrade relay at South Reading on the 1072 230 V line | 0.25 | ME - 100% | 2016-05-01
b2019.2 | Terminate Burger-Longview 138 kV, Burger-Brookside 138 kV, Burger-Cloverdale 138 kV #1, and Burger-Harmon 138 kV #2 into Holloway substation; Loop Burger-Harmon #1 138 kV and Burger-Knox 138 kV into Holloway substation | 1.5 | ATSI - 100% | 2014-06-01
b2019.3 | Reconfigure Burger 138 kV substation to accommodate two 138 kV line exits and generation facilities |  | ATSI - 100% | 2014-06-01
b2443.1 | Replace the Idylwood 230 kV breaker '203512' with 50kA breaker | 0.255 | Dominion - 100% | 2018-06-01
b2443.2 | Replace the Ox 230 kV breaker '206342' with 63kA breaker | 0.27 | Dominion - 100% | 2018-06-01
b2451 | Replace the Charles 138 kV breaker '919' with 63 kA | 0.25 | DEOK - 100% | 2018-06-01
b2452.3 | Replace the Hunterstown 115 kV breaker '96192' with 40 kA rated breaker | 0.28548 | ME - 100% | 2017-06-01
b2457 | Replace 24 115 kV wood h-frames with 230 kV Dominion pole H-frame structures on the Clubhouse - Purdy 115 kV line | 2.9 | Dominion - 100% | 2014-06-01
b2458.1 | Replace 12 wood H-frame structures with steel H-frame structures and install shunts on all conductor splices on Carolina - Woodland 115 kV | 4.9 | Dominion - 100% | 2016-05-01
b2458.2 | Upgrade all line switches and substation components at Carolina 115 kV to meet or exceed new conductor rating of 174 MVA |  | Dominion - 100% | 2016-05-01
b2458.3 | Replace 14 wood H-frame structures on Carolina - Woodland 115 kV |  | Dominion - 100% | 2016-05-01
b2458.4 | Replace 2.5 miles of static wire on Carolina - Woodland 115 kV |  | Dominion - 100% | 2016-05-01
b2460.1 | Replace Hanover 230 kV substation line switches with 3000A switches | 0.25 | Dominion - 100% | 2016-05-01
b2460.2 | Replace wave traps at Four River 230 kV and Elmont 230 kV substations with 3000A wave traps |  | Dominion - 100% | 2016-05-01
b2462 | Add two 138 kV circuit breakers at Fremont station to fix tower contingency '408_2' | 1.2 | AEP - 100% | 2015-06-01
b2463 | Rebuild and reconductor 115 kV line from East Towanda to S. Troy and upgrade terminal equipment at East Towanda, Tennessee Gas and South Troy | 40 | PENELEC - 100% | 2016-03-01
b2465 | Replace the Skokie 138 kV breaker '88 L8809' with a 63 kA breaker | 1.79 | ComEd - 100% | 2016-06-01
b2466 | Replace the Skokie 138 kV breaker '88 L8810' with 63kA breaker | 1.79 | ComEd - 100% | 2016-06-01
b2467 | Replace the Skokie 138 kV breaker '88 L11416' with 63kA breaker | 1.79 | ComEd - 100% | 2016-06-01
b2468 | Replace the Skokie 138 kV breaker '88 L8803' with 63kA breaker | 1.79 | ComEd - 100% | 2016-06-01
b2469 | Replace the Des Plaines 138 kV breaker '46 11702' with 63kA breaker | 1.88 | ComEd - 100% | 2016-06-01
b2472 | Replace the Ringgold 138 kV breaker 'RCM1' with 40kA breakers | 0.25 | APS - 100% | 2018-06-01
b2473 | Replace the Ringgold 138 kV breaker '#4 XMFR' with 40kA breakers | 0.25 | APS - 100% | 2018-06-01
b2474 | Rebuild Athenia 138 kV to 80kA | 131 | PSEG - 100% | 2018-06-01
b2475 | Construct a new line between Oak Mound 138 kV substation and Waldo Run 138 kV substation | 38 | APS - 100% | 2015-12-31
Upgrade ID | Description | Cost Estimate ($M) | Trans Owner | Required IS Date
b2492 | Replace the Beaver 138 kV breaker '426-B-2' with 63kA breaker | 0.35 | ATSI - 100% | 2016-06-01
b2493 | Replace the Hoytdale 138kV breaker '83-B-30' with 63kA breaker | 0.35 | ATSI - 100% | 2016-06-01
b2494 | Construct Warren 230 kV ring bus and install a second Warren 230/115 kV transformer | 15 | PENELEC - 100% | 2016-06-01
b2495 | Replace transformer leads on the Glen Gardner 230/34.5 kV #1 transformer | 0.1 | JCPL - 100% | 2015-06-01
b2496 | Replace Franklin 115/34.5 kV transformer #2 with 90 MVA transformer | 3 | JCPL - 100% | 2015-06-01
b2497 | Reconductor 0.9 miles of the Captive Plastics to Morris Park 34.5 kV circuit (397 ACSR) with 556 ACSR | 0.6 | JCPL - 100% | 2015-06-01
b2498 | Extend 5.8 miles of 34.5 kV circuit from North Branch substation to Lebanon substation with 397 ACSR and install 34.5 kV breaker at Lebanon substation | 2 | JCPL - 100% | 2015-06-01
b2500 | Upgrade terminal equipment at Monroe on the Englishtown to Monroe (H34) 34.5 kV circuit | 0.1 | JCPL - 100% | 2015-06-01
b2501 | Construct a new 138/69 kV Yager station by tapping 2-138 kV FE circuits (Nottingham-Cloverdale, Nottingham-Harmon) | 55 | AEP - 100% | 2014-06-01
b2501.2 | Build a new 138 kV line from new Yager station to Azalea station |  | AEP - 100% | 2014-06-01
b2501.3 | Close the 138 kV loop back into Yager 138 kV by converting part of local 69 kV facilities to 138 kV |  | AEP - 100% | 2014-06-01
b2501.4 | Build 2 new 69 kV exits to reinforce 69 kV facilities and upgrade conductor between Irish Run 69 kV Switch and Bowerstown 69 kV Switch |  | AEP - 100% | 2014-06-01
b2502.1 | Construct a new 138 kV switching station Nottingham tapping 6-138 kV FE circuits (Holloway-Brookside, Holloway-Harmon (#1&#2), Holloway-Reeds, Holloway-New Stacy, Holloway-Cloverdale). Exit 138 kV circuit from new station to Freebyrd station. | 90 | AEP - 100% | 2014-06-01
b2502.2 | Convert Freebyrd 69 kV to 138 kV |  | AEP - 100% | 2014-06-01
b2502.3 | Rebuild/convert Freebyrd - South Cadiz 69 kV circuit to 138 kV |  | AEP - 100% | 2014-06-01
b2502.4 | Upgrade South Cadiz to 138 kV breaker and a half |  | AEP - 100% | 2014-06-01
b2504 | Rebuild 115 kV Line #32 from Halifax-South Boston (6 miles) for min. of 240 MVA and transfer Welco tap to Line #32. Moving Welco to Line #32 requires disabling auto-sectionalizing scheme | 6.5 | Dominion - 100% | 2015-06-30
b2505 | Install structures in river to remove the 115 kV #65 line (Whitestone - Harmony Village 115 kV) from bridge and improve reliability of the line | 30 | Dominion - 100% | 2016-05-31
b2527 | Replace Whitpain 230 kV breaker '155' with 80kA breaker | 0.6 | PECO - 100% | 2016-06-01
b2528 | Replace Whitpain 230 kV breaker '525' with 80kA breaker | 0.6 | PECO - 100% | 2016-06-01
b2529 | Replace Whitpain 230 kV breaker '175' with 80kA breaker | 0.6 | PECO - 100% | 2016-06-01
b2530 | Replace the Sporn 138 kV breaker 'G1' with 80kA breaker | 1 | AEP - 100% | 2018-06-01
b2531 | Replace the Sporn 138 kV breaker 'D' with 80kA breaker | 1 | AEP - 100% | 2018-06-01
b2532 | Replace the Sporn 138 kV breaker 'O1' with 80kA breaker | 1 | AEP - 100% | 2018-06-01
b2533 | Replace the Sporn 138 kV breaker 'P2' with 80kA breaker | 1 | AEP - 100% | 2018-06-01
b2534 | Replace the Sporn 138 kV breaker 'U' with 80kA breaker | 1 | AEP - 100% | 2018-06-01
b2535 | Replace the Sporn 138 kV breaker 'O' with 80kA breaker | 1 | AEP - 100% | 2018-06-01
b2536 | Replace the Sporn 138 kV breaker 'O2' with 80kA breaker | 1 | AEP - 100% | 2018-06-01
b2537 | Replace the Robinson Park 138 kV breakers A1, A2, B1, B2, C1, C2, D1, D2, E1, E2, and F1 with 63 kA breakers | 15 | AEP - 100% | 2016-06-01
Upgrade ID | Description | Cost Estimate ($M) | Trans Owner | Required IS Date
b2538 | Replace the Mickleton 230kV 'MK' breaker with 63kA breaker | 0.4 | AEC - 100% | 2016-06-01
b2540 | Increase rating of Shelby-E. Sidney-Quincy-Logan 138 kV line to 224 MVA by replace/raise three pole swing out structure; push/pull/retension conductors on two spans; lower eight spans of single phase | 0.042 | Dayton - 100% | 2015-06-01
b2541 | As needed in PJM Operations connect two 30MVAR mobile shunts to Eldean and Sidney 69 kV buses; Block LTCs for Eldean 138/69 kV and Sidney 138/69kV transformers after loss of Shelby-Sidney 138 kV line | 0 | Dayton - 100% | 2014-10-01
b2544 | Increase the MOT of the 266.8 MCM ACSR section (1.4 miles), of the Kargle - KU Elizabethtown 69 kV line section to 266 degrees F | 0.0276 | EKPC - 100% | 2015-06-01
b2545.1 | Construct a new 138 kV substation (Shuman Hill substation) connected to the Fairview - Willow Island (84) 138 kV line | 40 | APS - 100% | 2015-07-01
b2545.2 | Install a ring bus station with five active positions and two 52.8 MVAR capacitors with 0.941 mH reactors |  | APS - 100% | 2016-02-01
b2545.3 | Install a +90/-30 MVAR SVC protected by a 138 kV breaker |  | APS - 100% | 2016-02-01
b2545.4 | Remove the 31.7 MVAR capacitor bank at Mobley 138 kV |  | APS - 100% | 2016-02-01
b2546 | Install a 51.8 MVAR (rated) 138 kV capacitor at Nyswaner 138 kV substation | 1 | APS - 100% | 2015-04-01
b2547.1 | Construct a new 138 kV six breaker ring bus Hillman substation | 31.5 | APS - 100% | 2016-02-01
b2547.2 | Loop Smith - Imperial 138 kV line into the new Hillman substation |  | APS - 100% | 2016-02-01
b2547.3 | Install +125/-75 MVAR SVC at Hillman substation |  | APS - 100% | 2016-02-01
b2547.4 | Install two 31.7 MVAR 138 kV capacitors |  | APS - 100% | 2016-02-01
b2548 | Eliminate clearance de-rate on Wylie Ridge - Smith 138 kV line and upgrade terminals at Smith 138 kV, new line ratings 294 MVA (Rate A)/350 MVA (Rate B) | 2.3 | APS - 100% | 2016-02-01
b2549 | Replace terminal equipment inside Chichester substation on the 220-36 (Chichester – Eddystone) 230 kV line | 0.4 | PECO - 100% | 2019-06-01
b2550 | Replace terminal equipment inside Nottingham substation on the 220-05 (Nottingham – Daleville – Bradford) 230 kV line | 0.1 | PECO - 100% | 2019-06-01
b2551 | Replace terminal equipment inside Llanerch substation on the 130-45 (Eddystone to Llanerch) 138 kV line | 0.1 | PECO - 100% | 2019-06-01
b2552 | Reconductor the North Meshoppen – Oxbow - Lackawanna 230 kV circuit and upgrade terminal equipment | 26.5 | PENELEC - 100% | 2019-06-01
b2553 | Replace Middle T3 138/69 kV transformer with 225 MVA nameplate | 7.5 | AEC - 100% | 2019-06-01
b2555 | Reconductor 0.5 miles of Tiltonsville - Windsor 138 kV and string the vacant side of the 4.5 mile section using 556 ACSR in a six wire configuration | 2 | AEP - 100% | 2019-06-01
b2556 | Install two 138 kV prop structures to increase the maximum operating temperature of the Clinch River - Clinch Field 138 kV line | 1.1 | AEP - 100% | 2019-06-01
b2557 | At Avon substation, replace the existing 345/138 kV 448 MVA #92 transformer with a 560 MVA unit | 5.4 | ATSI - 100% | 2019-06-01
b2558 | Close normally open switch A 13404 to create a Richland J Bus - Richland K Bus 138 kV line | 0.02 | ATSI - 100% | 2019-06-01
b2559 | Reconductor the Black River - Lorain 138 kV line and upgrade Black River and Lorain substation terminal end equipment | 9.6 | ATSI - 100% | 2019-06-01
Upgrade ID | Description | Cost Estimate ($M) | Trans Owner | Required IS Date
b2560 | Construct a second 138 kV line between West Fremont and Hayes substation on open tower position of the West Fremont - Groton - Hayes 138 kV line | 7.4 | ATSI - 100% | 2019-06-01
b2561 | Install a new 345 kV circuit breaker 5-7 at Elwood substation | 2.6 | ComEd - 100% | 2019-06-01
b2562 | Remove 2.0 miles of wood poles on 138 kV line 17105, erect new steel structures, and install new 1113 kcmil ACSR conductor from Roscoe Bert to Harlem | 4.6 | ComEd - 100% | 2019-06-01
b2563 | Operate with the Crescent 345/138 kV #3 autotransformer in-service by replacing 8 overdutied 138 kV breakers at Crescent, 3 138 kV breakers at Beaver Valley, install #1 section 345 kV breaker for 331 circuit at Crescent | 7.285 | DLCO - 100% | 2019-06-01
b2564 | Add two breakers at Miami Fort 138 kV | 2 | DEOK - 100% | 2019-06-01
b2565 | Replace wave trap at Carver Substation with a 2000A wave trap | 0.04 | Dominion - 100% | 2019-06-01
b2566 | Reconductor 1.41 miles of existing line between ACCA and Hermitage and upgrade associated terminal equipment | 1.82 | Dominion - 100% | 2019-06-01
b2567 | Upgrade the Riverside 115kV substation strain bus conductors on circuits 115012 and 115011 with double bundled 1272 ACSR to achieve ratings of 491/577 MVA SN/SE on both transformer leads | 1.14 | BGE - 100% | 2019-06-01
b2568 | Reconductor Northwest – Northwest #2 115kV 110574 substation tie circuit with 2167 ACSR to achieve ratings of 400/462 MVA SN/SE | 1.2 | BGE - 100% | 2019-06-01
b2569 | Replace Terminal equipment at Silverside 69 kV substation | 0.04 | DPL - 100% | 2019-06-01
b2570 | Upgrade limiting terminal facilities at Freneau, Parlin, and Williams substations | 0.6 | JCPL - 100% | 2019-06-01
b2571 | Upgrade the limiting terminal facilities at both Jackson and North Hanover | 0.1 | JCPL - 100% | 2019-06-01

## Multi-Zone Allocations
Upgrade ID | Description | Cost Estimate ($M) | Cost Allocation | Required IS Date
b2006.1.1 | Loop the 2026 (TMI - Hosensack 500 kV) line in to the Lauschtown substation and upgrade relay at TMI 500 kV | 5.25 | AEC - 0.87%, AEP - 7.21%, APS - 2.74%, ATSI - 4.15%, BGE - 10.87%, COMED - 7.02%, ConEd - 0.29%, DAYTON - 1.08%, DEOK - 1.63%, DL - 0.93%, DPL - 1.27%, DVP - 5.92%, ECP - 0.1%, EKPC - 0%, JCPL - 2.01%, ME - 11.06%, NEPTUNE - 0.21%, HTP - 0.01%, PECO - 2.72%, PENELEC - 0.98%, PEPCO - 2.06%, PPL - 33.51%, PSEG - 3.29%, RE - 0.14% | 2017-06-01
b2471 | Replace Midlothian 500 kV breaker 563T576 and motor operated switches with 3 breaker 500 kV ring bus. Terminate Lines #563 Carson - Midlothian, #576 Midlothian - North Anna, Transformer #2 in new ring | 9 | AEC - 0.87%, AEP - 7.21%, APS - 2.74%, ATSI - 4.15%, BGE - 2.16%, ComEd - 7.02%, ConEd - 0.29%, Dayton - 1.08%, DEOK - 1.63%, DL - 0.93%, DVP - 55.92%, DPL - 1.27%, ECP - 0.1%, EKPC - 0%, O66 - 0.01%, JCPL - 2.01%, ME - 0.95%, NEPTUNE - 0.21%, PECO - 2.72%, PENELEC - 0.98%, PEPCO - 2.06%, PPL - 2.33%, PSEG - 3.29%, RE - 0.14% | 2015-11-01