## FERC Form 715 Thermal
Reserved(FG# assigned by PJM) | Analysis Case | Fr Bus | Fr Name | To Bus | To Name | Tert Bus | Tert Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Cont 1 Name | Contingency 1 description | Cont 2 Name | Contingency 2 description | Transformer Capability/ Line Conductor Rating (SN/SE/WN/WE MVA) | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment | M3 Process Status
AEP-T424 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245558 | 05PITTSBUR | 245562 | 05W MT VER |  |  | 1 | 69 | 205 | 46 |  | 119.01 | N-1-1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | AEP_P1-2_#11506_934 | OPEN BRANCH FROM BUS 245547 TO BUS 247787 CKT 1 / 245547 05BLACKJRD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 247787 TO BUS 247788 CKT 1 / 247787 05COMMERCE 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 245564 TO BUS 247788 CKT 1 / 245564 05KELSEYHS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 247788 CKT 1 / 245550 05MARTINSS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 245553 CKT 1 / 245550 05MARTINSS 69.0 245553 05MT VERNO 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T429 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245558 | 05PITTSBUR | 245562 | 05W MT VER |  |  | 1 | 69 | 205 | 46 |  | 119 | N-1-1 | AEP_P1-2_#11506_934 | OPEN BRANCH FROM BUS 245547 TO BUS 247787 CKT 1 / 245547 05BLACKJRD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 247787 TO BUS 247788 CKT 1 / 247787 05COMMERCE 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 245564 TO BUS 247788 CKT 1 / 245564 05KELSEYHS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 247788 CKT 1 / 245550 05MARTINSS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 245553 CKT 1 / 245550 05MARTINSS 69.0 245553 05MT VERNO 69.0 1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T430 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245558 | 05PITTSBUR | 245562 | 05W MT VER |  |  | 1 | 69 | 205 | 46 |  | 107.6 | N-1-1 | AEP_P1-3_#11594_05SHARPR 138_1 | OPEN BRANCH FROM BUS 243098 TO BUS 247201 CKT 1 / 243098 05SHARPR 138 247201 05SHARP RD 69.0 1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T431 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245558 | 05PITTSBUR | 245562 | 05W MT VER |  |  | 1 | 69 | 205 | 46 |  | 107.6 | N-1-1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | AEP_P1-3_#11594_05SHARPR 138_1 | OPEN BRANCH FROM BUS 243098 TO BUS 247201 CKT 1 / 243098 05SHARPR 138 247201 05SHARP RD 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T464 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 46 |  | 124.79 | N-1-1 | AEP_P1-2_#11506_934 | OPEN BRANCH FROM BUS 245547 TO BUS 247787 CKT 1 / 245547 05BLACKJRD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 247787 TO BUS 247788 CKT 1 / 247787 05COMMERCE 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 245564 TO BUS 247788 CKT 1 / 245564 05KELSEYHS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 247788 CKT 1 / 245550 05MARTINSS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 245553 CKT 1 / 245550 05MARTINSS 69.0 245553 05MT VERNO 69.0 1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T466 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 46 |  | 124.79 | N-1-1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | AEP_P1-2_#11506_934 | OPEN BRANCH FROM BUS 245547 TO BUS 247787 CKT 1 / 245547 05BLACKJRD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 247787 TO BUS 247788 CKT 1 / 247787 05COMMERCE 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 245564 TO BUS 247788 CKT 1 / 245564 05KELSEYHS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 247788 CKT 1 / 245550 05MARTINSS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 245553 CKT 1 / 245550 05MARTINSS 69.0 245553 05MT VERNO 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T467 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 46 |  | 116.92 | N-1-1 | AEP_P1-3_#11594_05SHARPR 138_1 | OPEN BRANCH FROM BUS 243098 TO BUS 247201 CKT 1 / 243098 05SHARPR 138 247201 05SHARP RD 69.0 1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T469 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 46 |  | 116.92 | N-1-1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | AEP_P1-3_#11594_05SHARPR 138_1 | OPEN BRANCH FROM BUS 243098 TO BUS 247201 CKT 1 / 243098 05SHARPR 138 247201 05SHARP RD 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T470 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245562 | 05W MT VER | 245558 | 05PITTSBUR |  |  | 1 | 69 | 205 | 46 |  | 171.01 | N-1-1 | 'AEP_P1-3_#14372_05ACADEM 138_1' | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T471 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 46 |  | 166.88 | N-1-1 | 'AEP_P1-3_#14372_05ACADEM 138_1' | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T472 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245558 | 05PITTSBUR | 245559 | 05S MT VER |  |  | 1 | 69 | 205 | 46 |  | 147.67 | N-1-1 | 'AEP_P1-3_#14372_05ACADEM 138_1' | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T473 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245559 | 05S MT VER | 245556 | 05N MT VER |  |  | 1 | 69 | 205 | 46 |  | 146.4 | N-1-1 | 'AEP_P1-3_#14372_05ACADEM 138_1' | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T474 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245556 | 05N MT VER | 245553 | 05MT VERNO |  |  | 1 | 69 | 205 | 46 |  | 136.25 | N-1-1 | 'AEP_P1-3_#14372_05ACADEM 138_1' | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T475 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245562 | 05W MT VER | 245558 | 05PITTSBUR |  |  | 1 | 69 | 205 | 46 |  | 115.19 | N-1-1 | 'AEP_P1-2_#11503_2244' | OPEN BRANCH FROM BUS 245537 TO BUS 245553 CKT 1 / 245537 05ACADEMIA 69.0 245553 05MT VERNO 69.0 1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T476 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 46 |  | 109.12 | N-1-1 | 'AEP_P1-2_#11503_2244' | OPEN BRANCH FROM BUS 245537 TO BUS 245553 CKT 1 / 245537 05ACADEMIA 69.0 245553 05MT VERNO 69.0 1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T477 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245562 | 05W MT VER | 245558 | 05PITTSBUR |  |  | 1 | 69 | 205 | 46 |  | 170.96 | N-1-1 | P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 'AEP_P1-3_#14372_05ACADEM 138_1' | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T478 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 46 |  | 166.86 | N-1-1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 'AEP_P1-3_#14372_05ACADEM 138_1' | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T479 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245558 | 05PITTSBUR | 245559 | 05S MT VER |  |  | 1 | 69 | 205 | 46 |  | 147.63 | N-1-1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 'AEP_P1-3_#14372_05ACADEM 138_1' | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T480 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245559 | 05S MT VER | 245556 | 05N MT VER |  |  | 1 | 69 | 205 | 46 |  | 146.36 | N-1-1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 'AEP_P1-3_#14372_05ACADEM 138_1' | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T481 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245556 | 05N MT VER | 245553 | 05MT VERNO |  |  | 1 | 69 | 205 | 46 |  | 136.2 | N-1-1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 'AEP_P1-3_#14372_05ACADEM 138_1' | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T482 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245562 | 05W MT VER | 245558 | 05PITTSBUR |  |  | 1 | 69 | 205 | 46 |  | 115.19 | N-1-1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 'AEP_P1-2_#11503_2244' | OPEN BRANCH FROM BUS 245537 TO BUS 245553 CKT 1 / 245537 05ACADEMIA 69.0 245553 05MT VERNO 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T483 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 46 |  | 109.12 | N-1-1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 'AEP_P1-2_#11503_2244' | OPEN BRANCH FROM BUS 245537 TO BUS 245553 CKT 1 / 245537 05ACADEMIA 69.0 245553 05MT VERNO 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T484 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 51 |  | 114.82 | N-1-1 | 'AEP_P1-3_#14372_05ACADEM 138_1' | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T485 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 51 |  | 114.82 | N-1-1 | 'P1-2_COMMERCE - SHARP RD CIRCUIT OUTAGE' | OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 | 'AEP_P1-3_#14372_05ACADEM 138_1' | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T486 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245049 | 05S TORONT | 245069 | 05W TORONT |  |  | 1 | 69 | 205 | 49 |  | 106.7 | N-1-1 | 'AEP_P1-3_#11775_05E LIVR 138_1' | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 REMOVE SWSHUNT FROM BUS 245037 | 'AEP_P1-2_#11672_865' | OPEN BRANCH FROM BUS 244986 TO BUS 245079 CKT 1 OPEN BRANCH FROM BUS 245079 TO BUS 247482 CKT 1 OPEN BRANCH FROM BUS 245079 TO BUS 245080 CKT 1 OPEN BRANCH FROM BUS 245044 TO BUS 247482 CKT 1 OPEN BRANCH FROM BUS 245048 TO BUS 247482 CKT Z1 | 49/49/61/61 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | 1.0 mile section having ratings shown in the table. The branch also contains 1.7 miles of other T-line conductor with higher ratings (68/68/111/111 MVA). | Potential M-3 need identified, awaiting field and engineering analysis.
AEP-T487 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245049 | 05S TORONT | 245069 | 05W TORONT |  |  | 1 | 69 | 205 | 49 |  | 102.5 | N-1-1 | 'AEP_P1-3_#11775_05E LIVR 138_1' | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 REMOVE SWSHUNT FROM BUS 245037 | 'AEP_P1-3_#13604' | OPEN BRANCH FROM BUS 242994 TO BUS 244986 CKT 1 | 49/49/61/61 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | 1.0 mile section having ratings shown in the table. The branch also contains 1.7 miles of other T-line conductor with higher ratings (68/68/111/111 MVA). | Potential M-3 need identified, awaiting field and engineering analysis.
AEP-T488 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245040 | 05FT STB 2 | 245062 | 05SUNST BL |  |  | 1 | 69 | 205 | 54 |  | 101 | N-1-1 | 'AEP_P1-3_#11775_05E LIVR 138_1' | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 REMOVE SWSHUNT FROM BUS 245037 | 'FE-P1-2-MP-138-555T' | DISCONNECT BRANCH FROM BUS 235406 TO BUS 235421 CKT 1 DISCONNECT BRANCH FROM BUS 235406 TO BUS 235710 CKT 1 DISCONNECT BRANCH FROM BUS 235406 TO BUS 243113 CKT 1 DISCONNECT BRANCH FROM BUS 243113 TO BUS 245049 CKT 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | 0.1 mile section having ratings shown in the table. The branch also contains 4.0 miles of other T-line conductor with higher ratings (64/64/96/96 MVA). | Potential M-3 need identified, awaiting field and engineering analysis.
AEP-T489 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245049 | 05S TORONT | 245069 | 05W TORONT |  |  | 1 | 69 | 205 | 49 |  | 106.7 | N-1-1 | 'AEP_P1-2_#8991' | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 | 'AEP_P1-2_#11672_865' | OPEN BRANCH FROM BUS 244986 TO BUS 245079 CKT 1 OPEN BRANCH FROM BUS 245079 TO BUS 247482 CKT 1 OPEN BRANCH FROM BUS 245079 TO BUS 245080 CKT 1 OPEN BRANCH FROM BUS 245044 TO BUS 247482 CKT 1 OPEN BRANCH FROM BUS 245048 TO BUS 247482 CKT Z1 | 49/49/61/61 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | 1.0 mile section having ratings shown in the table. The branch also contains 1.7 miles of other T-line conductor with higher ratings (68/68/111/111 MVA). | Potential M-3 need identified, awaiting field and engineering analysis.
AEP-T490 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245049 | 05S TORONT | 245069 | 05W TORONT |  |  | 1 | 69 | 205 | 49 |  | 102.5 | N-1-1 | 'AEP_P1-2_#8991' | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 | 'AEP_P1-3_#13604' | OPEN BRANCH FROM BUS 242994 TO BUS 244986 CKT 1 | 49/49/61/61 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | 1.0 mile section having ratings shown in the table. The branch also contains 1.7 miles of other T-line conductor with higher ratings (68/68/111/111 MVA). | Potential M-3 need identified, awaiting field and engineering analysis.
AEP-T491 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245040 | 05FT STB 2 | 245062 | 05SUNST BL |  |  | 1 | 69 | 205 | 54 |  | 101 | N-1-1 | 'AEP_P1-2_#8991' | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 | 'FE-P1-2-MP-138-555T' | DISCONNECT BRANCH FROM BUS 235406 TO BUS 235421 CKT 1 DISCONNECT BRANCH FROM BUS 235406 TO BUS 235710 CKT 1 DISCONNECT BRANCH FROM BUS 235406 TO BUS 243113 CKT 1 DISCONNECT BRANCH FROM BUS 243113 TO BUS 245049 CKT 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | 0.1 mile section having ratings shown in the table. The branch also contains 4.0 miles of other T-line conductor with higher ratings (64/64/96/96 MVA). | Potential M-3 need identified, awaiting field and engineering analysis.
AEP-T492 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245049 | 05S TORONT | 245069 | 05W TORONT |  |  | 1 | 69 | 205 | 49 |  | 106.71 | N-1-1 | 'AEP_P1-2_#11672_865' | OPEN BRANCH FROM BUS 244986 TO BUS 245079 CKT 1 OPEN BRANCH FROM BUS 245079 TO BUS 247482 CKT 1 OPEN BRANCH FROM BUS 245079 TO BUS 245080 CKT 1 OPEN BRANCH FROM BUS 245044 TO BUS 247482 CKT 1 OPEN BRANCH FROM BUS 245048 TO BUS 247482 CKT Z1 | 'AEP_P1-3_#11775_05E LIVR 138_1' | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 REMOVE SWSHUNT FROM BUS 245037 | 49/49/61/61 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | 1.0 mile section having ratings shown in the table. The branch also contains 1.7 miles of other T-line conductor with higher ratings (68/68/111/111 MVA). | Potential M-3 need identified, awaiting field and engineering analysis.
AEP-T493 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245049 | 05S TORONT | 245069 | 05W TORONT |  |  | 1 | 69 | 205 | 49 |  | 106.71 | N-1-1 | 'AEP_P1-2_#11672_865' | OPEN BRANCH FROM BUS 244986 TO BUS 245079 CKT 1 OPEN BRANCH FROM BUS 245079 TO BUS 247482 CKT 1 OPEN BRANCH FROM BUS 245079 TO BUS 245080 CKT 1 OPEN BRANCH FROM BUS 245044 TO BUS 247482 CKT 1 OPEN BRANCH FROM BUS 245048 TO BUS 247482 CKT Z1 | 'AEP_P1-2_#8991' | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 | 49/49/61/61 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | 1.0 mile section having ratings shown in the table. The branch also contains 1.7 miles of other T-line conductor with higher ratings (68/68/111/111 MVA). | Potential M-3 need identified, awaiting field and engineering analysis.
AEP-T494 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245040 | 05FT STB 2 | 245062 | 05SUNST BL |  |  | 1 | 69 | 205 | 54 |  | 101 | N-1-1 | 'FE-P1-2-MP-138-555T' | DISCONNECT BRANCH FROM BUS 235406 TO BUS 235421 CKT 1 DISCONNECT BRANCH FROM BUS 235406 TO BUS 235710 CKT 1 DISCONNECT BRANCH FROM BUS 235406 TO BUS 243113 CKT 1 DISCONNECT BRANCH FROM BUS 243113 TO BUS 245049 CKT 1 | 'AEP_P1-3_#11775_05E LIVR 138_1' | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 REMOVE SWSHUNT FROM BUS 245037 | 54/54/76/76 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | 0.1 mile section having ratings shown in the table. The branch also contains 4.0 miles of other T-line conductor with higher ratings (64/64/96/96 MVA). | Potential M-3 need identified, awaiting field and engineering analysis.
AEP-T495 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245040 | 05FT STB 2 | 245062 | 05SUNST BL |  |  | 1 | 69 | 205 | 54 |  | 101 | N-1-1 | 'FE-P1-2-MP-138-555T' | DISCONNECT BRANCH FROM BUS 235406 TO BUS 235421 CKT 1 DISCONNECT BRANCH FROM BUS 235406 TO BUS 235710 CKT 1 DISCONNECT BRANCH FROM BUS 235406 TO BUS 243113 CKT 1 DISCONNECT BRANCH FROM BUS 243113 TO BUS 245049 CKT 1 | 'AEP_P1-2_#8991' | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | 0.1 mile section having ratings shown in the table. The branch also contains 4.0 miles of other T-line conductor with higher ratings (64/64/96/96 MVA). | Potential M-3 need identified, awaiting field and engineering analysis.
AEP-T496 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245049 | 05S TORONT | 245069 | 05W TORONT |  |  | 1 | 69 | 205 | 49 |  | 102.5 | N-1-1 | 'AEP_P1-3_#13604' | OPEN BRANCH FROM BUS 242994 TO BUS 244986 CKT 1 | 'AEP_P1-3_#11775_05E LIVR 138_1' | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 REMOVE SWSHUNT FROM BUS 245037 | 49/49/61/61 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | 1.0 mile section having ratings shown in the table. The branch also contains 1.7 miles of other T-line conductor with higher ratings (68/68/111/111 MVA). | Potential M-3 need identified, awaiting field and engineering analysis.
AEP-T497 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245049 | 05S TORONT | 245069 | 05W TORONT |  |  | 1 | 69 | 205 | 49 |  | 102.5 | N-1-1 | 'AEP_P1-3_#13604' | OPEN BRANCH FROM BUS 242994 TO BUS 244986 CKT 1 | 'AEP_P1-2_#8991' | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 | 49/49/61/61 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | 1.0 mile section having ratings shown in the table. The branch also contains 1.7 miles of other T-line conductor with higher ratings (68/68/111/111 MVA). | Potential M-3 need identified, awaiting field and engineering analysis.