# PJM RTEP - 2021 NJ Offshore Wind SAA TRANSMISSION Proposal Window Overview

### Introduction

PJM is soliciting project proposals to build the necessary transmission to meet New Jersey’s goal of facilitating the delivery of a total of 7,500 MW of offshore wind by 2035.

The State of New Jersey offshore wind goals consist of incorporating the addition of 3,500 MW of offshore wind by 2030 on the schedule described in Table 1, and a total addition of 7,500 MW by 2035, into their renewable resource portfolio. In order to accomplish this, the New Jersey Board of Public Utilities (“NJBPU”) has developed a schedule by which they will solicit and plan multiple phases of offshore wind generation development to place into operation. The current NJBPU solicitation schedule plan is shown in Table 1 below.

NJBPU Offshore Wind Schedule

| Solicitation | Capacity Target (MW) | Issue Date | Submittal Date | Award Date | Estimated Commercial Operation Date |
| --- | --- | --- | --- | --- | --- |
| 1 | 1,100* | Q3 2018 | Q4 2018 | Q2 2019 | 2024 |
| 2 | 2,400** | Q3 2020 | Q4 2020 | Q2 2021 | 2027 |
| 3 | 1,200*** | Q3 2022 | Q4 2022 | Q2 2023 | 2029 |
| 4 | 1,200*** | Q2 2024 | Q3 2024 | Q1 2025 | 2031 |
| 5 | 1,400*** | Q2 2026 | Q3 2026 | Q1 2027 | 2033 |
| 6 | 1,400*** | Q1 2028 | Q3 2028 | Q1 2029 | 2035 |

* Solicitation 1: Incorporates the injection of a combined total of 1,100 MW at the Oyster Creek 230 kV substation and the BL England 138 kV substation.

**Note that Solicitation Number 2 was awarded June 30, 2021 resulted in a total of 2658 MWs.

***Solicitations 3-6 timing and capacity amounts will be adjusted at a future date, such that the total capability will achieve the overall target of 7,500MWs.

In preparation for this SAA transmission solicitation, PJM performed planning studies to assess potential impacts of various injection scenarios that could cost effectively accommodate the targets and minimize the amount of transmission enhancements required.  The scenario selected by NJBPU is the subject of this competitive transmission window.

### Project Scope Overview and Description of Options

PJM is seeking proposals to address violations on existing transmission facilities resulting from modeled injections of power at the locations specified in the New Jersey BPU Order as well as proposals for new transmission lines, onshore substations, offshore substations and an offshore network.  The overall scope of work comprises the full buildout of onshore and offshore transmission needed to reliably and efficiently interconnect up to 7,500 MW of offshore wind generation, which is projected to be placed in service between 2024 and 2035.  PJM is soliciting proposals via four separate requests identified as Options 1a, 1b, 2 and 3 and as depicted illustratively in Figure 1.  The expected outcome of the SAA Proposal Window is that NJBPU may select some combination of these options, or sub-parts of options, to be considered under PJM’s SAA, i. e, Option 1a may be selected, Options 1a and 1b may be selected, Options 1a, 1b, and 2 may be selected, all four options may be selected, none may be selected, or a portion of one or more options may be selected.

The diagrams below represent examples of possible configurations associated with proposals that may be submitted by proposing entities. The diagrams are not intended to be requirements, but illustrations of the various means to connect and address the different portions of the overall design. Proposing entities are responsible to design and configure their facilities in a manner that achieves the public policy requirements. The specific configuration shall be the responsibility of the proposing entity and it may differ from these diagrams to satisfy the proposing entity’s design considerations. Each proposal submittal shall include a clear description of the configuration of the project to ensure adequate understanding of the proposal developed by the proposing entity.

Figure 1 Potential Options For the NJ Offshore Wind Transmission Solution (Concepts depicted are for illustration purposes only; details of new lines and facilities are to be provided by sponsors in proposals to meet objectives of this solicitation.)

#### The first solicitation for 1,100 MW of the 7,500 MW has already been awarded by the NJBPU.  PJM will include a set of expected required network upgrades for the first solicitation in the power flow models that are to be used to evaluate the 7,500 MW buildout.  No network upgrades have been included in the analytical files for the second and subsequent solicitations. PJM and the NJBPU are not seeking proposals to address the first solicitation by itself.

#### Solicitation 2 was awarded on June 30, 2021 for 2,568 MW at the locations shown in Table 2.  NJBPU has requested that PJM not include any network upgrades required for Solicitation 2 in the power flow models used in this window.  In addition, the NJBPU will accept proposals that shift some or all of the Solicitation 2 generation to other POIs as part of the objective to cost-effectively achieve NJ’s goal of up to 7,500 MW of OSW generation, subject to the following requirements.  Proposing entities will be responsible to (a) submit proposals that are sufficient for NJBPU to engage the Solicitation 2 OSW developers regarding use of the SAA project as described in the Solicitation 2 OSW award Orders; (b) demonstrate the alternative is lower-cost than the default POIs listed above; and (c) demonstrate that alternative will not increase overall risks (including project-on-project risks). After the final window proposals are analyzed and a recommendation is offered to the NJBPU, PJM will work with the NJBPU to make a determination regarding which of the proposals might be assignable to the Solicitation 2 queue positions and which might remain as baseline upgrades under the SAA.

Offshore Wind Assumption Changes After June 30th 2021

#### Points of Injection (POIs) for Future Offshore Wind Generation

Supported by the results of the PJM scenario planning studies, the NJBPU Order specified the following default POIs for up to 6,400MW (maximum facility output) of OSW generation which are expected to be placed in service in between 2028 and 2035:

- North New Jersey:  3,100 MW at Deans 500 kV

- Central New Jersey: 1,200 MW at Smithburg 500 kV

- Central New Jersey: 1,200 MW at Larrabee 230 kV

- South New Jersey: 900 MW at Cardiff 230 kV

After the award of Solicitation #2 on June 30, 2021, with concurrence from the NJPBU, PJM is incorporating the following changes in the models to reflect these default MW amounts.

- North New Jersey:  2,542 MW at Deans 500 kV

- Central New Jersey: 1,148 MW at Smithburg 500 kV

- Central New Jersey: 1,200 MW at Larrabee 230 kV

- South New Jersey: 1,510 MW at Cardiff 230 kV

PJM and the NJBPU will consider proposals with alternative POIs that provide a lower-cost approach to achieving NJ’s OSW objectives.

While the NJBPU proposals will not impact the requirements for interconnection of the first award to the 1,100MW Orsted’s OSW project, proposals should address future requirements beyond the scope of the interconnection studies.  As noted in the NJBPU Order, proposals can also involve alternative points of interconnections and MW amounts, under the conditions above, as long as the proposal is supported by proposer analyses documenting the advantages that the alternative proposal provides over the default POIs and injection amounts.

### Alternative Points and Amounts of Injection

Unless specified otherwise, PJM will assume that all proposals are submitted to address the default POIs and injection amounts.  As noted above, proposers may submit proposals based on POIs that differ from the default POIs specified in this request.   Should proposers elect to utilize alternative POIs or injection amounts, the project proposal must identify the alternative set of POIs and injections amounts that the proposal is associated with, address all violations that result from those injections and fully meet the system needs as defined in each of the problem statements for all options included under the alternative election.  This includes system needs that may not have been identified in the Problem Statement for the default POI Set.  If PJM does not receive proposals that address all system needs identified in the four problems statements for an alternative set of POIs then the alternative set of POIs may or may not be considered further.

#### Description of Options

PJM is seeking proposals to address the following options, which are depicted in Figure 1 and described below:

- Option 1a, Onshore Upgrades on Existing Facilities

- Option 1b, Onshore New Transmission Connection Facilities

- Option 2, Offshore New Transmission Connection Facilities

- Option 3, Offshore Network

### Interdependency of Options

PJM and the NJBPU encourage proposals that can be divided into the options described above and take into consideration that PJM and the NJBPU may combine individual proposals and conceivably parts of individual proposals together with other proposals in order to achieve a combination of proposals that best addresses all evaluation criteria that will ultimately need to be satisfied through this proposal window. However, PJM and the NJBPU also recognize that there may be dependencies or efficiencies that may arise from the interplay of proposals for the various options when they are combined together.  Project sponsors are encouraged to clearly identify and describe in the proposal submission any observed linkages with other proposals along with any related dependencies and efficiencies that may result from combining or not combining linked proposals.  Any linkages to other proposals must be specified in the proposal submission description and can be described in more detail in the BPU Supplemental Data Collection Form. PJM and the NJBPU reserve the right to take this information into account, along with any partial, incomplete, or combinations of proposed solutions.

Proposals for Option 1a should be complete and responsive in fully addressing the needs in the problem statement and not dependent on the implementation of work identified in Options 1b, 2 or 3.

Proposals for Option 1b, must be complete and responsive in fully addressing the needs in the problem statement and include all tie-in work to POI substations.

Proposals for Option 2 must be complete and responsive in fully addressing the needs in the problem statement and include all applicable tie-in work to the onshore substations in Option 1b.

Proposals for Option 3 must be complete and responsive in fully addressing the needs in the problem statement and include all tie-work to two or more offshore collector substations.

If alternative POI(s) are proposed, in order to be considered, solutions to all system needs associated with the alternative POI Set must be submitted. This includes system needs that may not have been identified in the Problem Statement for the default POI Set.

For all proposals and options, developers are encouraged to address:

- Synergies with transmission solutions from already-ongoing OSW procurements,

- Synergies with the replacement of aging transmission infrastructure,

- Solutions that achieve significant savings such as reduced OSW generation amounts,

- Proposals to ensure the energy deliverability of offshore wind and minimizing curtailment,

- Ability to expand proposed infrastructure to accommodate future increases in offshore wind above current plans, and

- Other innovative solutions to yield a transmission investment schedule that is optimally aligned with the planned schedule of offshore wind generation procurements.

#### Problem Statement of Option 1a - Onshore Upgrades on Existing Facilities

Option 1a proposals must address reliability violations on existing and planned facilities resulting from injections at identified POIs that represent the future offshore wind generation at the specified substations.  The specific Option 1a reliability violations that PJM posts for the default POIs may not be applicable to or reflect the reliability violations associated with alternative POIs, injection amounts or other assumptions that differ from those used to examine the default POIs specified.

#### Problem Statement of Option 1b – Onshore New Transmission Connection Facilities

Option 1b proposals must address onshore transmission connection needs between the POIs and required new onshore substations, if any, which may include the following components:

- New lines from existing substations (POIs) to onshore substations

- Tie-in to the existing substations (POIs)

- New onshore substations

#### Problem Statement of Option 2 - Offshore New Transmission Connection Facilities

Option 2 proposals must address landfall connections and offshore transmission connection needs from onshore substations to offshore substations, which may include the following components:

- Submarine cable from shore substation to the offshore collector substation

- Offshore collector substations (which may be substations serving several wind farms or the substations serving individual wind farms)

#### Problem Statement of Option 3 - Offshore Network

Option 3 proposals must address any offshore interconnections between offshore collector substations to:

- Provide alternate paths to inject energy from offshore generators into the onshore transmission grid in the event of a reliability issue with a cable landing

- Mitigate offshore or onshore system congestion

- Provide other quantifiable market or reliability benefits

The offshore network will connect some or all of the offshore substations in Option 2.  Option 3 proposals must also specify how much energy and capacity the offshore network would be able to transfer between the onshore POIs.

### Increase to Largest Single Contingency

In real time operations the largest single contingency may vary depending on outages and actual system conditions.  For planning purposes for this competitive solicitation, proposal sponsors should consider the largest existing single contingency on the PJM system is 1,500 MW.  If a sponsor’s proposal results in an increase to the largest single contingency, PJM will evaluate the performance of the project proposal and consider any increase in costs to all PJM customers as a result.

### Proposal Evaluation Considerations

The overall objective of this SAA transmission solicitation is to solicit full or partial solutions to the identified problem statements that yield the transmission facilities and system enhancements necessary to support New Jersey’s goal of cost-effectively procuring and delivering to its electricity customers up to 7,500 MW of offshore wind generation by 2035.  Solutions that meet all applicable PJM criteria will be evaluated from an overall New Jersey ratepayer impact and risk perspective, as described below.  Solutions can be proposed for less than what would be necessary to reach the 7,500 MW overall objective, if solutions’ reduced injection levels result in significant cost savings and other economic benefits.

Evaluation criteria for proposed solutions to meet the New Jersey public policy requirements under this State Agreement Approach may include:

PJM system reliability – ability to provide a solution to the needs defined in the problem statements, additional needs identified by the proposing entities, or the needs associated with alternative POIs and to resolve potential reliability criteria violations on PJM facilities in accordance with all applicable planning criteria (PJM, NERC, SERC, RFC, and Local Transmission Owner criteria), including the solution’s ability to (a) resolve identified PJM reliability violations and satisfy any applicable criteria that may impact the performance measurement of the project even if it was not explicitly stated as part of the original problem statement; and (b) reduce the need for must-run generation and special operating procedures, extreme weather outages and weather-related multiple unforced outages, reduced probability of common mode outages due to electrical and non-electrical causes, islanding, power quality degradation.

Project constructability – the extent to which the proposal identifies, addresses, and mitigates (through technical studies and documentation of experience with similar solutions elsewhere) the financing, constructability, execution, technology, environmental, and permitting challenges of the proposed solution, including the need for construction- or other-related outages on related transmission facilities.

Project costs – total cost of proposed solutions and individual elements (partial solutions); quality of proposed innovative cost control approaches (such as phased-in development of project segments, capped project costs or capped revenue requirements, and cost recovery for excess or unused capacity) or levelized cost recovery options (such as trended original costs, which may improve the intergenerational equity of cost recovery); financial commitments regarding rate of return, specific provisions to protect against cost overruns, or other comparable provisions designed to control costs.

Project risk mitigation – ability of the proposed solution to mitigate environmental, permitting, financing, constructability, timing, project-on-project (including the use of financial assurance mechanisms, guaranteed in-service dates or financial commitments contingent on meeting targeted commercial online dates, and delay damage payment provisions), and any other risks that could increase costs, reduce value, or delay the development and delivery of offshore wind generation for New Jersey.

Environmental benefits – ability of the proposed solution to minimize potential environmental impacts; minimize impacts to marine, nearshore, and onshore habitats, listed species, cultural resources, air (emissions) including potential benefits, water quality, noise, aesthetics, tourism, and navigation; minimize impacts related to fisheries resources and the fishing community and industry.

Permitting plan – ability of the proposed solution to minimize permitting risks, including plan for and likelihood of achieving all State and Federal necessary regulatory agency approvals, permits, or other authorizations; likelihood of meeting projected commercial operation dates, operation and maintenance plans, site control or ability to achieve site control, constructability, project longevity, and project schedule.

Quality of proposal and developer experience – quality of project documentation and proposal description, discussion of commitments and benefits, and supporting analyses and benefits quantifications (including documentation of assumptions and analyses, if any); documentation of developer experience relevant to the successful implementation of the proposed solution.

Flexibility, modularity, and option value of solutions – ability of project proposals to achieve efficient outcomes through combinations of solutions for Options 1a, 1b, 2 and 3 needs, or ways in which proposed solutions, or portions of proposed solutions, can be combined, integrated, and sequenced to more cost effectively achieve the State’s overall public policy and risk mitigation objectives; ability of the proposed solution to accommodate future increases in offshore wind generation above current plans; innovative solutions that yield a transmission investment schedule that is optimally aligned with the planned schedule of offshore wind generation procurements.

Market value of offshore wind generation – ability of the proposed solution to maximize the energy, capacity and Renewable Energy Credit (REC) values of offshore wind generation delivered to the chosen POIs, including mitigation of curtailment risks, and the level and sustainability of PJM capacity, congestion, or other rights created by the proposed solution that increase the delivered value of the wind generation or otherwise reduce the total cost of the proposal.

Additional New Jersey benefits – ability of proposed solutions and associated upgrades to provide additional onshore-grid-related benefits, resolve PJM market congestion, and/or otherwise reduce or avoid PJM-related costs and improve PJM market performance; this includes (a) energy market benefits, including energy deliverability of offshore wind production or curtailment, production cost savings, or other benefits; (b) identification of benefits to the transmission system, including synergies with transmission solutions from already-ongoing procurements, opportunistic replacement of aging transmission infrastructure, the creation of valuable transmission-related rights, and other transmission cost savings; (c) capacity market benefits (including CETL increases), improve resiliency/redundancy, avoid future costs (such as future reliability upgrades or aging facilities replacements); (d) other benefits, including state energy sufficiency, improvements in local transmission and distribution outage statistics, reduced utilization of aging infrastructure, improvements in local resiliency.

### Proposal Response Requirements

In order to accommodate the flexibility for proposers to address only selected needs of the overall objective, the following guidance is provided for responses to the individual problem statements. Any expected interdependencies with other proposals for the various options should be clearly described in the proposal.  Proposals will be selected from each option category, and compatible proposals will be combined to form sets of comprehensive transmission solution packages for the default and any alternative sets of POIs.  The comprehensive transmission solution packages will then be evaluated as described in this overview document and in the individual problem statements.

PJM will accept separate proposals for each of the four options in the manner described below.

  - Option 1a:  Proposals may resolve one or more reliability violations, whether independently or in combination with other proposals or portions of proposals.

  - Option 1b: Proposals may address one or more onshore transmission connections,  that address needs defined in the Option 1b problem statement

  - Option 2: Proposals may address one or more offshore transmission connections, that address the needs defined in the Option 2 problem statement

  - Option 3: Proposals may address an offshore network to connect some or all of the offshore substations in Option 2 as described in the Option 3 problem statement

  - PJM and NJBPU reserve the right to consider proposals that do not fall squarely within (a) – (d).

In addition to the submittal requirements that PJM normally requires for competitive windows, an additional submittal document will be required as part of the submission.

### Special TEAC Session

PJM will be conducting a Special TEAC Session on May 5, 3:00-5:00pm EPT regarding the SAA NJ OSW Window.  Interested proposers are encouraged to register to attend the meeting and submit questions in advance.

### References

- NJBPU’s Order on November 18, 2020, DOCKET NO. QO20100630

- Option 1a Problem Statement For 2021 SAA Window To Support NJ OSW

- Option 1b Problem Statement For 2021 SAA Window To Support NJ OSW

- Option 2 Problem Statement For 2021 SAA Window To Support NJ OSW

- Option 3 Problem Statement For 2021 SAA Window To Support NJ OSW

- BPU Supplemental SAA Bid Data Collection

APPENDIX: RELIABILITY ANALYSIS TO SUPPORT 2021 NJ Offshore Wind SAA TRANSMISSION Proposal Window

Scope: 2028 Summer Reliability Analysis; 2028 Winter Reliability Analysis; 2028 Light Load Reliability Analysis; 2035 Long-Term Deliverability Analysis

PJM seeks technical solutions, also called proposals, to resolve potential reliability criteria violations on PJM facilities in accordance with all applicable planning criteria (PJM, NERC, SERC, RFC, and Local Transmission Owner criteria).

#### Criterion Applied by PJM for this Proposal Window

- 2028 Summer Baseline Thermal and Voltage N-1 Contingency Analysis

- 2028 Summer Generator Deliverability and Common Mode Reliability Analysis

- 2028 Summer Load Deliverability Thermal and Voltage Analysis

- 2028 Summer N-1-1 Thermal and Voltage Analysis and Voltage Collapse

- 2028 Winter Baseline Thermal and Voltage N-1 Contingency Analysis

- 2028 Winter Generator Deliverability and Common Mode Reliability Analysis

- 2028 Winter Load Deliverability Thermal and Voltage Analysis

- 2028 Winter N-1-1 Thermal and Voltage Analysis and Voltage Collapse

- 2028 Light Load Baseline Thermal and Voltage N-1 Contingency Analysis

- 2028 Light Load Generator Deliverability and Common Mode Reliability Analysis

- 2028 FERC Form 715 Analysis

- 2035 Long-Term Deliverability Analysis

- 2025 Stability Analysis

- 2025 Short Circuit Analysis

### Terminology for Proposal Windows

Through the analyses listed above, PJM has compiled a list of criteria violations unique to the set of injection locations and amounts identified for the Public Policy Projects identified in the SAA Proposal Window Overview document. This will be referred to as the default set of POIs. The violations and the impacted facilities are identified by a table of flowgates. Descriptions of the column headings are provided below. Different analyses often use different column headings.

#### Typical thermal analysis column headings:

| Column Heading | Title | Description |
| --- | --- | --- |
| FG # | Flowgate Number | A sequential numbering of the identified potential violations |
| Fr Bus | From Bus Number | PSSE model bus number corresponding to one end of line identified as a potential violation |
| Fr Name | From Bus Name | PSSE model bus name corresponding to one end of line identified as a potential violation |
| To Bus | To Bus Number | PSSE model bus number corresponding to other end of line identified as a potential violation |
| To Name | To Bus Name | PSSE model bus name corresponding to other end of line identified as a potential violation |
| Monitored Facility | Monitored Facility | The circuit on which a potential violation is occurring |
| Base Rate (MVA) | Base Rate (MVA) | Normal Facility Rating (Rate A) |
| % Overload | Percentage Overload | Percentage above corresponding Facility Rating |
| CKT | Circuit ID | Circuit number of identified potential violation |
| KVs | Kilovolt level (A/B) | Kilovolt level of both sides of potential violation, if A does not equal B, potential violation is a transformer |
| Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line |
| Rating | Facility Rating | Applicable thermal rating (MVA) of facility |
| DC Ld(%) | Direct Current Loading percentage | Percentage above Facility Rating determined from DC testing |
| AC Ld(%) | Alternating Current Loading percentage | Percentage above Facility Rating determined from AC testing |
| Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower) |
| Cont Name | Contingency Name | Contingency name as identified in associated contingency file or embedded in the spreadsheet |
| Contingency | Contingency | Contingency description |
| Violation Date | Violation Date | Date on which violation is expected to occur |
| Analysis Case | Analysis Case | Case title to use in replicating analysis |

#### Typical voltage analysis column headings:

| Column Heading | Title | Description |
| --- | --- | --- |
| FG # | Flowgate Number | A sequential numbering of the identified potential violations |
| Bus # | Bus Number | PSSE model bus number corresponding to bus identified as a potential violation |
| KVs | Kilovolt level | Kilovolt level of bus identified as potential violation |
| Area | Area Number | Area number of bus identified as potential violation |
| ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied |
| BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied |
| Low Limit | Low Voltage Limit(P.U.) | Threshold of Per Unit Low voltage, if ContVolt is under this limit, a potential violation is identified |
| Upper Limit | High Voltage Limit(P.U.) | Threshold of Per Unit High voltage, if ContVolt is over this limit, a potential violation is identified |
| Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower) |
| Vdrop (%) | Voltage drop | The percentage that the voltage has dropped as a result of the contingency |
| Contingency | Contingency | Contingency name as identified in associated contingency file |
| Contingency 1 | First Contingency | N-1 (first) contingency identified |
| Contingency 2 | Second Contingency | N-1-1 (second) contingency identified in N-1-1 analysis |

### Proposal Window Exclusion Definitions

The following definitions explain the basis for excluding flowgates from the competitive planning process and designating projects to the incumbent Transmission Owner.

Flowgates excluded from competition will include the underlined language in the comment field.

- Below 200kV Exclusion: Due to the lower voltage level of the identified violations, these reliability violations are excluded from the competitive proposal window process. As a result, the local Transmission Owner will be the Designated Entity. Refer to Operating Agreement, Schedule 6 § 1.5.8(n).

- Substation Equipment Exclusion: For reliability violations on existing transmission substation equipment, these reliability violations are excluded from the competitive proposal window process. As a result, the local Transmission Owner will be the Designated Entity. Refer Operating Agreement, Schedule 6 § 1.5.8(p).

### Analysis Procedure

Participants are expected to develop solutions to all applicable criteria violations and perform analysis to validate that the solutions remove these violations. The competitive planning process is documented in PJM Manual 14F, which is available here: http://www.pjm.com/-/media/documents/manuals/m14f.ashx

Proposed solutions must also meet Transmission Owner Planning Criteria which is available here: http://www.pjm.com/planning/planning-criteria/to-planning-criteria.aspx

The table below provides the base case dispatch and ramping limits to be applied for the New Jersey Offshore Wind units.  This table supplements the base case dispatch and ramping limits specified in PJM Manual 14B, which is available here: https://pjm.com/-/media/documents/manuals/m14b.ashx

| Generator Deliverability Requirements For New Jersey Offshore Wind Units |  |  |  |  |
| --- | --- | --- | --- | --- |
| Season | Contingency Type | Base Case Dispatch* | Ramping Limit* |  |
| Summer | Single | 30%** | 30%** |  |
| Winter | Single | 60% | 80% |  |
| Light Load | Single | 60% | 80% |  |
| Summer | Common Mode | 30%** | 100% |  |
| Winter | Common Mode | 60% | 100% |  |
| Light Load | Common Mode | 60% | 80% |  |
| * Expressed as % of Maximum Facility Output (MFO) ** In order to reflect awarded solicitations the 30% value will be modified as follows. For Solicitation 1 both BL England and Oyster Creek will be studied at 28.1%. For Solicitation 2 at Cardiff will be studied at 18.2% and Smithburg will be studied at 28.5%. |  |  |  |  |

Although PJM does its best to provide complete and accurate results, changes to the list of violations under consideration are possible. That is, flowgates may be added or removed from consideration in the proposal window. PJM works with Transmission Owners, Generation Owners, neighboring TOs and other affected parties to verify the quality of the analysis. PJM endeavors to minimize such changes and will clearly communicate any changes to the participants.

PJM regularly updates the system model to reflect changes to the transmission system. Analyses are performed to verify that violations continue to be valid, no new violations have appeared and proposed solutions still address the targeted violation(s).

PJM shall determine the more efficient or cost-effective enhancements or expansions for any violation in consultation with the BPU to consider state preferences.

#### WHAT PJM PROVIDES:

The information listed below is provided to allow replication of PJM analyses. Some of these data are designated Critical Energy Infrastructure Information (CEII) and must be handled consistent with PJM’s CEII request process at Competitive Planning Process page on the PJM website:

- 2028 Power Flow Base Cases (summer, winter and light load). Identifies one or more system configurations to which planning criteria are applied. The default NJ OSW POIs will be included and dispatched in the models at their expected seasonal capacity factor.  These are the same power flow cases that were used to derive the flowgate violations posted for this window.

- Generator Deliverability Workbooks corresponding to the 2028 Power Flow Base Cases.

- TARA Generation Deliverability options files.

- Contingency Files: Contains all contingency types (single, bus, tower, line w/ stuck breaker).

- Subsystem Files: Identifies all subsystem zones to be considered in analysis.

- Monitor Files: Identify specific ranges of facilities by area and kV level to be considered in analysis.

- Facility Ratings: (if different from those included in the base cases)

- Violations List: Lists all criteria violations with power flow results and additional technical notes (flowgates). The results indicate the case(s) to which the criteria violations apply. Note that the criteria violations supplied are for the particular set of injection amounts and locations specified in the overall project description.

- Short Circuit Base Case. This case reflects the 2025 RTEP base case and will not include models for the NJ OSW.

- Stability Base Case: This case reflects the 2025 RTEP summer and light load stability models and will not include models for the NJ OSW.

- TO Criteria Setting Files. Lists settings used for short circuit analysis for each specific TO.

- Load Forecast Through 2035: To be used for 2035 Long-Term Deliverability Analysis.

- 2028 Load Deliverability Analytical Files: Analytical files for multiple modelled LDAs in the Mid-Atlantic Region without the NJ OSW are provided.  Additional files for the EMAAC and MAAC LDAs with the default NJ OSW POIs are also provided

- 2028 Market Efficiency Analytical & Supporting Files

### Document Revision History

4/15/2021 - V1 -      Original Problem Statement posted to the PJM Competitive Planning Process webpage: https://www.pjm.com/planning/competitive-planning-process.aspx.

7/30/2021 – V2 -      Problem Statement update to account for award of Solicitation #2 on June 30, 2021 posted to the PJM Competitive Planning Process webpage: https://www.pjm.com/planning/competitive-planning-process.aspx.

NJBPU’s Order on 11/18/2020, DOCKET NO. QO20100630, (here after, “the BPU Order”), under PJM Tariff and Operation Manuals, the PJM 2021 NJ Offshore Wind SAA Proposal Window seeks proposals that the “ build-out will meet New Jersey’s goal of facilitating the delivery of a total of 7,500 MW of offshore wind to consumers (including the 1,100 MW of offshore wind awarded in the Board’s first solicitation, as well as any awards made in the second solicitation) and facilitating the efficient delivery of the power to New Jersey consumers over the expected life of the offshore wind projects.”

Note that the capacity target and/or schedule for each solicitation is subject to change based on market conditions existing at the time, and other factors as determined by the NJBPU.

The redacted version of the New Jersey Offshore Wind Phase 2 Study Results will be included in the window materials posted at https://pjm.com/planning/competitive-planning-process

See I.M.O. The Board of Public Utilities Offshore Wind Solicitation 2 for 1,200 to 2,400 MW – Ocean Wind II, LLC (June 30, 2021) at 24-25 (“The Board encourages maximum utilization of shared offshore wind facilities, to the extent that the use of these facilities is in the best interest of New Jersey ratepayers, by delivering the OW2 Project in a lower-cost or lower-risk fashion... For any deviation from the interconnection plan approved in this Order, including for use of any SAA transmission capability, a mutually acceptable revision to this Order will be required.”); I.M.O. The Board of Public Utilities Offshore Wind Solicitation 2 for 1,200 to 2,400 MW – Atlantic Shores Offshore Wind Project 1, LLC (June 30, 2021) at 23-24 (“The Board encourages maximum utilization of shared OSW facilities, to the extent that the use of these facilities is in the best interest of New Jersey ratepayers, by delivering the Atlantic Shores Project in a lower-cost or lower-risk fashion… For any deviation from the interconnection plan approved in this Order, including for use of any SAA transmission capability, a mutually acceptable revision to this Order will be required.”).