| 2028 Overloaded Facility * | Rating (MVA) | Transmission Owner | Worst GD Test | Worst Contingency Overload % | Worst Contingency Type | Primary Facilities Outaged During Worst Contingency |
| --- | --- | --- | --- | --- | --- | --- |
| Deans-Brunswick 230 kV | 887 | PSEG | Summer | 138% 123% | Breaker | CEII |
| Cardiff-Lewis 138 kV | 400 | AE | Summer | 113% | Tower | CEII |
| Windsor-Clarksville 230 kV | 813 | JCPL / PSEG | Summer | 120% 108% | Breaker | CEII |
| Lewis No. 2-Lewis No. 1 138 kV | 287 | AE | Summer | 103% | Tower | CEII |
| Oyster Creek-Manitou 138 kV No. 1 | 817 | JCPL | Summer | 102% | Breaker | CEII |
| Oyster Creek-Manitou 138 kV No. 2 | 802 | JCPL | Summer | 101% | Breaker | CEII |
| Clarksville-Lawrence 230 kV | 869 | PSEG | Summer | 104% | Breaker | CEII |
| Peach Bottom-Conastone 500 kV | 3700 | PECO / BGE | Winter | 124% 127% | Single | CEII |
| Cardiff-New Freedom 230 kV | 692 | PSEG / AE | Winter | 117% | Tower | CEII |
| Furnace Run 500/230 kV Transformer No. 1 | 1348 | Transource | Winter | 115% 116% | Single | CEII |
| Furnace Run 500/230 kV Transformer No. 2 | 1348 | Transource | Winter | 115% 116% | Single | CEII |
| LS Power Cable East-LS Power Silver Run 230 kV | 1150 | SRE | Winter | 101% 106% | Breaker | CEII |
| Aldene-Springfield Road | 522 | PSEG | Winter | 105% 104% | Base Case | CEII |
| Hope Creek-LS Power Cable East 230 kV Circuit 1 | 575 | PSEG / SRE | Winter | 100% 104% | Single | CEII |
| Hope Creek-LS Power Cable East 230 kV Circuit 2 | 575 | PSEG / SRE | Winter | 100% 104% | Single | CEII |
| Gilbert-Springfield 230 kV | 903 | JCPL / PPL | Winter | 101% | Single | CEII |
| Lake Nelson I-Middlesex 230 kV | 819 | PSEG | Winter | 103% 104% | Single | CEII |
| Richmond-Waneeta 230 kV | 803 | PECO | Winter | 105% 103% | Base Case | CEII |
| Peach Bottom-Furnace Run 500 kV | 4323 | PECO / Transource | Winter | 102% | Single | CEII |
| Furnace Run-Conastone 230 kV Circuit 1 | 1534 | Transource / BGE | Winter | 101% | Single | CEII |
| Furnace Run-Conastone 230 kV Circuit 2 | 1534 | Transource / BGE | Winter | 101% | Single | CEII |

*This table contains the results from the 2028 generator deliverability (GD) summer, winter and light load study that considers PJM market monitored facilities and BES facilities under single and common mode contingencies; refer to PJM Manual M14b, Attachment C section C.3, Attachment D-2 and Attachment D-3 for more information about the generator deliverability test.  Note that no 2028 load deliverability violations were identified; refer to PJM Manual M14b, Attachment C section C.2 for more information about the load deliverability test.  Note also that the New Jersey Transmission Owners also performed their FERC Form 715 analysis and did not identify any reliability issues beyond those identified in this table; refer to the PJM Transmission Owner Planning Criteria posted on the PJM website for more information about these criteria.

| 2035 Overloaded Facility ** | Rating (MVA) | Transmission Owner | Worst GD Test | Worst Contingency Overload % | Worst Contingency Type | Primary Facilities Outaged During Worst Contingency |
| --- | --- | --- | --- | --- | --- | --- |
| Linden-Tosco 230 kV | 1081 | PSEG | Summer | 101% | Tower | CEII |
| Tosco-Linden VFT 230 kV | 1081 | PSEG | Summer | 101% | Tower | CEII |
| Deans-Brunswick 230 kV | 980 | PSEG | Winter Summer | 115% 116% | Single Tower | CEII |
| Aldene-Stanley Terrace 230 kV | 558 | PSEG | Summer | 102% | Single | CEII |
| Cardiff-New Freedom 230 kV | 692 | AEC | Winter | 118% | Tower | CEII |
| Peach Bottom-Conastone 500 kV | 4290 | PECO / BGE | Winter | 108% 110% | Single | CEII |
| Hope Creek-LS Power Cable East 230 kV Circuit 1 | 575 | PSEG / SRE | Winter | 104% 107% | Single | CEII |
| Hope Creek-LS Power Cable East 230 kV Circuit 2 | 575 | PSEG / SRE | Winter | 104% 107% | Single | CEII |
| LS Power Cable East-LS Power Silver Run 230 kV | 1150 | PSEG / SRE | Winter | 104% 107% | Single | CEII |
| Aldene-Springfield Road 230 kV | 522 | PSEG | Winter | 106% 105% | Base Case | CEII |
| Peach Bottom-Furnace Run 500 kV | 4403 | PECO / Transource | Winter | 101% | Single | CEII |
| Richmond-Waneeta 230 kV | 803 | PECO | Winter | 102% 101% | Base Case | CEII |
| Gilbert-Springfield 230 kV | 903 | JCPL / PPL | Winter | 101% 100% | Single | CEII |

**This table contains the results from the 2035 long-term deliverability study that considers 230 kV and up transmission lines that are beyond their conductor limit for single and tower line contingencies.  Refer to PJM Manual M14b, Attachment C section C.4 for more information. Note that no load deliverability violations were identified.