## FG 28-GD-S2-S1
****** PJM Generator Deliverability Detailed Report ****** POWER-GEM [TARA Ver 2001.1a PJMGD RC3 64-bit - Wed Aug 18 16:43:01 2021]
FG Index | 1 | Monitored Facility:218306 DEANS 230 218304 BRUNSWCK 230 1 / Contingency:PJM500_PS_P2-3_BRBG5_4-5[Breaker]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
887 | 126.01 | 123.35 | AC | 411.75 | 573.09 | 78.87 | 52.3 | 1.71 | 1117.72 | 1094.1 | 0.001481 | 0 | 12797.9 | 0 | 10196.7 | 0.05308 | 3872.23 | 2601.19 | 1271.04 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited?
900003 | DEANS E | 500 | 231 | 74 | 0 | 1779.4 | 0 | 1779.4 | FiftyFifty | 0.22876 | 407.0508 |  | 0 | 1 | 1 | NEWENERGY | OSW_DEANS
200006 | DEANS C | 500 | 231 | 74 | 0 | 762.6 | 762.6 | 762.6 | FiftyFifty | 0.22876 |  |  | 0 | 1 | 1 | CAPACITY | OSW_DEANS
900004 | SMITHBRG E | 500 | 228 | 74 | 0 | 820.4 | 0 | 820.4 | FiftyFifty | 0.2022 | 165.8839 |  | 0 | 1 | 1 | NEWENERGY | OSW_SMITHB
200017 | SMITHBRG C | 500 | 228 | 74 | 0 | 327.6 | 327.6 | 327.6 | FiftyFifty | 0.2022 |  |  | 0 | 1 | 1 | CAPACITY | OSW_SMITHB
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0 | 1.24 | FiftyFifty | 0.11045 | 0.137 |  | 0 | 1 | 1 | NEWENERGY | X2-089
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.61 | 0.76 | FiftyFifty | 0.11045 | 0.0165 |  | 0 | 1 | 1 | CAPACITY | X2-089
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0 | 1.58 | Adder/OL | 0.08617 | 0.1362 | 0.0023 | 0 |  | 1 | NEWENERGY | W1-032
901032 | W1-024E OP1 | 34.5 | 228 | 0 | 0 | 0 | 0 | 2.13 | Adder/OL | 0.07566 | 0.1608 | 0.0031 | 0 |  | 1 | NEW
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  | 645 | LTF/CMTX | 0.07305 | 47.117 | 0.9551
207419 | AB2-139 E | 34.5 | 228 | 76 | 0 | 0.21 | 0 | 0.18 | Adder/OL | 0.06867 | 0.0123 | 0.0003 | 0 |  | 1 | ENERGY | AB2-139
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0 | 4.76 | Adder/OL | 0.06683 | 0.3181 | 0.007 | 0 |  | 1 | NEWENERGY | W2-078
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0 | 4.25 | Adder/OL | 0.06683 | 0.284 | 0.0063 | 0 |  | 1 | NEWENERGY | W1-113
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0 | 6.97 | Adder/OL | 0.06653 | 0.4637 | 0.0103 | 0 |  | 1 | NEWENERGY | AC1-207
900005 | 28LARRABEE E | 230 | 228 | 74 | 0 | 840 | 0 | 714 | Adder/OL | 0.0658 | 46.9825 | 1.0572 | 0 |  | 1 | NEWENERGY | OSW_LARRAB
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 | 2.63 | Adder/OL | 0.06309 | 0.1663 | 0.0039 | 0 |  | 1 | NEWENERGY | Y2-051
919662 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 | 7 | Adder/NFTIR/OL | 0.06166 | 0.4316 | 0.0104 | 0.05 |  | 1 | MTX NFTIR | AA2-048
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 | 3.74 | Adder/OL | 0.06166 | 0.2306 | 0.0055 | 0 |  | 1 | NEWENERGY | W3-079
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0 | 8.96 | Adder/OL | 0.05983 | 0.536 | 0.0133 | 0 |  | 1 | NEWENERGY | X1-037
923293 | AB1-138 E | 34.5 | 228 | 75 | 0 | 6 | 0 | 5.1 | Adder/OL | 0.05928 | 0.3024 | 0.0076 | 0 |  | 1 | NEWENERGY | AB1-138
900002 | 28OYSTER E | 230 | 228 | 74 | 0 | 586.7 | 0 | 498.7 | Adder/OL | 0.05791 | 28.8811 | 0.7384 | 0 |  | 1 | NEWENERGY | OSW_OYSCK
923463 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0 | 4.25 | Adder/OL | 0.05602 | 0.2381 | 0.0063 | 0 |  | 1 | NEWENERGY | AB1-163
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0 | 1.7 | Adder/OL | 0.05508 | 0.0936 | 0.0025 | 0 |  | 1 | NEWENERGY | X4-031
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.6 |  | 173.6 | CLTF | 0.00447 | 0.7752 | -0.2571
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 0.00447 | 0.2486 | -0.0824
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 0.00447 | 0.2439 | -0.0808
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  | 258.3 | CLTF | 0.00443 | 1.1437 | -0.3825
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  | 210 | CLTF | 0.00435 | 0.9131 | -0.311
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 0.00428 | 0.2143 | -0.0741
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 0.00429 | 0.2131 | -0.0736
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  | 35 | CLTF | 0.00414 | 0.1448 | -0.0518
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  | 57.8 | CLTF | 0.00406 | 0.2347 | -0.0855
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  | 239.8 | LTF/CMTX | 0.00377 | 0.9044 | 0.355
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  | 55.3 | CLTF | 0.0026 | 0.1441 | -0.0819
219123 | BCRR_COGEN | 13.8 | 231 | 64 | 0 | 6 | 0 | 5.1 | Adder/OL | -0.0723 | -0.3688 | 0.0076 | 0.12623 |  | 1 | CAPACITY
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | 0.08617 |  |  | 0 |  | 1 | CAPACITY | W1-032
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 5.3 |  |  | 0.07594 |  |  | 0 |  | 1 | CAPACITY
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | 0.07566 |  |  | 0 |  | 1 | CAPACITY | W1-024
218344 | TOSCO_G6 | 18 | 231 | 2 | 90 | 180 | 144.51 |  |  | 0.07279 |  |  | 0.04435 |  | 1 | CAPACITY | TOSCO
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 309 | 248.08 |  |  | 0.07215 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | 0.07215 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | 0.07215 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | 0.07215 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC2
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | 0.07215 |  |  | 0.08446 |  | 1 | CAPACITY
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | 0.07215 |  |  | 0.08446 |  | 1 | CAPACITY
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | 0.06683 |  |  | 0 |  | 1 | CAPACITY | W2-078
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 2.25 |  |  | 0.06683 |  |  | 0 |  | 1 | CAPACITY | W1-113
207420 | AC1-207 C | 34.5 | 228 | 75 | 0 | 4.9 | 3.93 |  |  | 0.06653 |  |  | 0 |  | 1 | CAPACITY | AC1-207
206294 | 28LARRABEE C | 230 | 228 | 74 | 0 | 360 | 360 |  |  | 0.0658 |  |  | 0 |  | 1 | CAPACITY | OSW_LARRAB
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | 0.06399 |  |  | 0.08446 |  | 1 | CAPACITY
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | 0.06399 |  |  | 0.08446 |  | 1 | CAPACITY
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 61.6 | 88.4 | 70.97 |  |  | 0.06399 |  |  | 0.04435 |  | 1 | CAPACITY | LAKEWOOD
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 61.2 | 88.3 | 70.89 |  |  | 0.06399 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 76.92 |  |  | 0.06399 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | 0.06309 |  |  | 0 |  | 1 | CAPACITY | Y2-051
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | 0.06166 |  |  | 0 |  | 1 | CAPACITY | W3-079
206201 | 28JERSVGEN | 34.5 | 228 | 2 | 0 | 2 | 1.61 |  |  | 0.06129 |  |  | 0 |  | 1 | CAPACITY
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 3.37 |  |  | 0.05983 |  |  | 0 |  | 1 | CAPACITY | X1-037
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 309 | 248.08 |  |  | 0.0597 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 180 | 144.51 |  |  | 0.0597 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | 0.0597 |  |  | 0.08446 |  | 1 | CAPACITY
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | 0.0597 |  |  | 0.08446 |  | 1 | CAPACITY
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 30.03 |  |  | 0.0597 |  |  | 0.10478 |  | 1 | CAPACITY
206280 | 28LAKEHURS | 34.5 | 228 | 64 | 0 | 13.8 | 11.08 |  |  | 0.05928 |  |  | 0.08446 |  | 1 | CAPACITY
923292 | AB1-138 C | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | 0.05928 |  |  | 0 |  | 1 | CAPACITY | AB1-138
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 27.3 |  |  | 0.05791 |  |  | 0.12623 |  | 1 | CAPACITY
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 27 |  |  | 0.05791 |  |  | 0.12623 |  | 1 | CAPACITY
206302 | 28OYSTER C | 230 | 228 | 74 | 0 | 229.3 | 229.3 |  |  | 0.05791 |  |  | 0 |  | 1 | CAPACITY | OSW_OYSCK
217825 | UMD_NJ | 26 | 231 | 2 | 0 | 10.5 | 8.43 |  |  | 0.05737 |  |  | 0 |  | 1 | CAPACITY
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | 0.05118 |  |  | 0 |  | 1 | NEWENERGY | X1-085
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | 0.05118 |  |  | 0 |  | 1 | CAPACITY | X1-085
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0 |  |  | 0.05017 |  |  | 0 |  | 1 | NEWENERGY | W1-101
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.43 |  |  | 0.05017 |  |  | 0 |  | 1 | CAPACITY | W1-101
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | 0.05015 |  |  | 0 |  | 1 | NEWENERGY | W1-124
921743 | AA2-049 E | 34.5 | 228 | 76 | -3 | 3 | 0 |  |  | 0.05015 |  |  | 0 |  | 1 | MTX | AA2-049
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | 0.05015 |  |  | 0 |  | 1 | CAPACITY | W1-124
920732 | AA2-184 E | 34.5 | 228 | 75 | 0 | 20 | 0 |  |  | 0.04947 |  |  | 0 |  | 1 | NEWENERGY | AA2-184
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.04781 |  |  | 0.05 |  | 1 | MTX
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | 0.04598 |  |  | 0 |  | 1 | NEWENERGY | W1-120
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | 0.04598 |  |  | 0 |  | 1 | NEWENERGY | W1-119
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | 0.04598 |  |  | 0 |  | 1 | CAPACITY | W1-120
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | 0.04598 |  |  | 0 |  | 1 | CAPACITY | W1-119
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0 |  |  | 0.04592 |  |  | 0 |  | 1 | NEWENERGY | Z2-102
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 3.97 |  |  | 0.04592 |  |  | 0 |  | 1 | CAPACITY | Z2-102
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | 0.04397 |  |  | 0 |  | 1 | NEWENERGY | W2-082
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | 0.04397 |  |  | 0 |  | 1 | CAPACITY | W2-082
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0 |  |  | 0.04386 |  |  | 0 |  | 1 | NEWENERGY | V3-067
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0 |  |  | 0.04386 |  |  | 0 |  | 1 | NEWENERGY | V3-068
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.23 |  |  | 0.04386 |  |  | 0 |  | 1 | CAPACITY | V3-067
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | 0.04386 |  |  | 0 |  | 1 | CAPACITY | V3-068
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | 0.04373 |  |  | 0 |  | 1 | NEWENERGY | X4-015
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0 |  |  | 0.04373 |  |  | 0 |  | 1 | NEWENERGY | X2-087
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | 0.04373 |  |  | 0 |  | 1 | CAPACITY | X4-015
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 0.04373 |  |  | 0 |  | 1 | CAPACITY | X2-087
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | 0.04355 |  |  | 0 |  | 1 | NEWENERGY | W4-025
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | 0.04355 |  |  | 0 |  | 1 | NEWENERGY | W1-129
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | 0.04355 |  |  | 0 |  | 1 | CAPACITY | W4-025
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | 0.04355 |  |  | 0 |  | 1 | CAPACITY | W1-129
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0 |  |  | 0.0432 |  |  | 0 |  | 1 | NEWENERGY | W2-019
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 1.85 |  |  | 0.0432 |  |  | 0 |  | 1 | CAPACITY | W2-019
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | 0.04257 |  |  | 0.10478 |  | 1 | CAPACITY
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | 0.04255 |  |  | 0.10478 |  | 1 | CAPACITY
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 998.11 |  |  | 0.04136 |  |  | 0.01494 |  | 1 | CAPACITY
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 992.1 |  |  | 0.04136 |  |  | 0.01494 |  | 1 | CAPACITY
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | 0.04136 |  |  | 0.08446 |  | 1 | ENERGY
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1026.43 |  |  | 0.04114 |  |  | 0.01494 |  | 1 | CAPACITY
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0 |  |  | 0.04005 |  |  | 0 |  | 1 | NEWENERGY | AB1-001
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.7 |  |  | 0.04005 |  |  | 0 |  | 1 | CAPACITY | AB1-001
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0 |  |  | 0.03952 |  |  | 0 |  | 1 | NEWENERGY | W1-112
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | 0.03952 |  |  | 0 |  | 1 | CAPACITY | W1-112
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 169.24 |  |  | 0.03818 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | 0.03818 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | 0.03818 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | 0.03818 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | 0.03818 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
900000 | CARDIFF E | 230 | 234 | 74 | 0 | 1235 | 0 |  |  | 0.03785 |  |  | 0 |  | 1 | NEWENERGY | OSW_CARDIF
227900 | CARDIFF C | 230 | 234 | 74 | 0 | 275 | 275 |  |  | 0.03785 |  |  | 0 |  | 1 | CAPACITY | OSW_CARDIF
227928 | V4-067E | 12.9 | 234 | 75 | 1.6 | 1.6 | 0 |  |  | 0.03684 |  |  | 0 |  | 1 | NEWENERGY | V4-067
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0 |  |  | 0.03684 |  |  | 0 |  | 1 | NEWENERGY | AB2-122
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.79 |  |  | 0.03684 |  |  | 0 |  | 1 | CAPACITY | V4-067
924701 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.56 |  |  | 0.03684 |  |  | 0 |  | 1 | CAPACITY | AB2-122
227801 | ONTC&DCT | 13.8 | 234 | 56 | 38.6 | 38.6 | 0 |  |  | 0.03615 |  |  | 0.08446 |  | 1 | NEW
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 |  |  | 0.03615 |  |  | 0.12623 |  | 1 | ENERGY
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0 |  |  | 0.03614 |  |  | 0 |  | 1 | NEWENERGY | W2-030
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 |  |  | 0.03615 |  |  | 0.10478 |  | 1 | ENERGY
228014 | PVILLEG | 0.48 | 234 | 65 | 1.7 | 3 | 1.04 |  |  | 0.03615 |  |  | 0 |  | 1 | CAPACITY
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 2.93 |  |  | 0.03614 |  |  | 0 |  | 1 | CAPACITY | W2-030
900001 | BLE E | 138 | 234 | 74 | 0 | 310.6 | 0 |  |  | 0.03502 |  |  | 0 |  | 1 | NEWENERGY | OSW_BLE
228110 | BLE C | 138 | 234 | 74 | 0 | 121.4 | 121.4 |  |  | 0.03502 |  |  | 0 |  | 1 | CAPACITY | OSW_BLE
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.61 |  |  | 0.03437 |  |  | 0 |  | 1 | CAPACITY
934302 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0 |  |  | 0.03399 |  |  | 0 |  | 1 | NEWENERGY | AD1-054
218092 | PRIMEENG_G | 26.4 | 231 | 29 | 10 | 70.3 | 56.44 |  |  | 0.03379 |  |  | 0.10478 |  | 1 | CAPACITY
228203 | P06 | 13.8 | 234 | 57 | 80.6 | 92.7 | 80.75 |  |  | 0.03368 |  |  | 0.08446 |  | 1 | CAPACITY
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 202.48 |  |  | 0.03358 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 143.63 |  |  | 0.03358 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 143.63 |  |  | 0.03358 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN2
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0 |  |  | 0.03358 |  |  | 0 |  | 1 | NEWENERGY | X1-072
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 0.03358 |  |  | 0 |  | 1 | CAPACITY | X1-072
217850 | MONTCLAIR_U | 26 | 231 | 2 | 0 | 10.6 | 8.51 |  |  | 0.03342 |  |  | 0 |  | 1 | CAPACITY
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.74 |  |  | 0.03342 |  |  | 0 |  | 1 | CAPACITY
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0 |  |  | 0.03329 |  |  | 0 |  | 1 | NEWENERGY | W4-059
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.18 |  |  | 0.03329 |  |  | 0 |  | 1 | CAPACITY | W4-059
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 207.94 |  |  | 0.03305 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | 0.03305 |  |  | 0.04435 |  | 1 | CAPACITY | DELANCY STREET
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | 0.03305 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 70.56 |  |  | 0.03305 |  |  | 0.08446 |  | 1 | CAPACITY
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | 0.03305 |  |  | 0.04435 |  | 1 | CAPACITY | NEWARK BAY
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | 0.03305 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 27.46 |  |  | 0.03305 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.85 |  |  | 0.03305 |  |  | 0 |  | 1 | CAPACITY
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0 |  |  | 0.03305 |  |  | 0 |  | 1 | NEWENERGY | V3-065
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.17 |  |  | 0.03305 |  |  | 0 |  | 1 | CAPACITY | V3-065
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 74.48 |  |  | 0.03294 |  |  | 0.08446 |  | 1 | CAPACITY
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 76.11 |  |  | 0.03273 |  |  | 0.08446 |  | 1 | CAPACITY
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | 0.03273 |  |  | 0.08446 |  | 1 | CAPACITY
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | 0.03273 |  |  | 0.08446 |  | 1 | CAPACITY
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | 0.03273 |  |  | 0.08446 |  | 1 | CAPACITY
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | 0.03273 |  |  | 0.08446 |  | 1 | CAPACITY
217831 | PB_NUTCLIF | 26 | 231 | 2 | 0 | 10.7 | 8.59 |  |  | 0.03266 |  |  | 0 |  | 1 | CAPACITY
228712 | V2-041E | 13.2 | 234 | 75 | 2.5 | 2.48 | 0 |  |  | 0.03233 |  |  | 0 |  | 1 | NEWENERGY | V2-041
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 1.22 |  |  | 0.03233 |  |  | 0 |  | 1 | CAPACITY | V2-041
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0 |  |  | 0.03214 |  |  | 0 |  | 1 | NEWENERGY | V3-066
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | 0.03214 |  |  | 0 |  | 1 | CAPACITY | V3-066
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 73.09 |  |  | 0.03175 |  |  | 0.08446 |  | 1 | CAPACITY
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | 0.03155 |  |  | 0 |  | 1 | NEWENERGY | V2-025
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 48.35 |  |  | 0.02985 |  |  | 0.08446 |  | 1 | CAPACITY
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.5 | 18.87 |  |  | 0.0295 |  |  | 0.08446 |  | 1 | CAPACITY
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 49.65 |  |  | 0.02928 |  |  | 0.10478 |  | 1 | CAPACITY
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | 0.02889 |  |  | 0 |  | 1 | NEWENERGY | W4-060
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | 0.02889 |  |  | 0 |  | 1 | CAPACITY | W4-060
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0 |  |  | 0.02728 |  |  | 0 |  | 1 | NEWENERGY | W1-130
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 2.57 |  |  | 0.02728 |  |  | 0 |  | 1 | CAPACITY | W1-130
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0 |  |  | 0.02675 |  |  | 0 |  | 1 | NEWENERGY | V4-054
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 3.05 |  |  | 0.02675 |  |  | 0 |  | 1 | CAPACITY | V4-054
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 4.8 | 0 |  |  | 0.02672 |  |  | 0 |  | 1 | NEW
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.6 | 39.8 | 34.67 |  |  | 0.0267 |  |  | 0.08446 |  | 1 | CAPACITY
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 32.75 |  |  | 0.0267 |  |  | 0.08446 |  | 1 | CAPACITY
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | 0.02666 |  |  | 0.04435 |  | 1 | NEW | AA2-069
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 154.95 |  |  | 0.02666 |  |  | 0.04435 |  | 1 | CAPACITY | Garrison
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 93.29 |  |  | 0.02666 |  |  | 0 |  | 1 | CAPACITY | Garrison
232901 | NORTHST | 69 | 235 | 56 | 5 | 46 | 36.93 |  |  | 0.02666 |  |  | 0.08446 |  | 1 | CAPACITY
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 12.2 |  |  | 0.02666 |  |  | 0.10478 |  | 1 | CAPACITY
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 39.34 |  |  | 0.02626 |  |  | 0.08446 |  | 1 | CAPACITY
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 38.54 |  |  | 0.02626 |  |  | 0.08446 |  | 1 | CAPACITY
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 152.54 |  |  | 0.02531 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.02531 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC2
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.02531 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.02531 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 0 |  |  | 0.02496 |  |  | 0 |  | 1 | NEWENERGY | AB1-056
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 330.7 |  |  | 0.02496 |  |  | 0.10478 |  | 1 | CAPACITY
930201 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 51.71 |  |  | 0.02496 |  |  | 0 |  | 1 | CAPACITY | AB1-056
232920 | IR10 | 13.2 | 235 | 55 | 12.6 | 16.1 | 12.93 |  |  | 0.02491 |  |  | 0.08446 |  | 1 | CAPACITY
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0 |  |  | 0.02489 |  |  | 0 |  | 1 | NEWENERGY | AB1-137
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 3.37 |  |  | 0.02489 |  |  | 0 |  | 1 | CAPACITY | AB1-137
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | 0.02483 |  |  | 0.10478 |  | 1 | ENERGY
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.02483 |  |  | 0 |  | 1 | NEWENERGY | Z2-076
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.02483 |  |  | 0 |  | 1 | NEWENERGY | Z2-077
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.02483 |  |  | 0 |  | 1 | CAPACITY | Z2-077
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.02483 |  |  | 0 |  | 1 | CAPACITY | Z2-076
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.41 |  |  | 0.0248 |  |  | 0 |  | 1 | CAPACITY
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.05 |  |  | 0.0247 |  |  | 0 |  | 1 | CAPACITY
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.02465 |  |  | 0.08446 |  | 1 | CAPACITY
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.02465 |  |  | 0.08446 |  | 1 | CAPACITY
917082 | CHERRYDALE E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0245 |  |  | 0 |  | 1 | NEWENERGY | Z2-012
232915 | OH NUG4 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 39.03 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 38.94 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 38.68 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 26.05 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232905 | BAYVIEW1 | 24.9 | 235 | 65 | 0 | 12.5 | 10.04 |  |  | 0.0245 |  |  | 0.12623 |  | 1 | CAPACITY
917081 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.0245 |  |  | 0 |  | 1 | CAPACITY | Z2-012
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0245 |  |  | 0 |  | 1 | NEWENERGY | W1-004
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0245 |  |  | 0 |  | 1 | NEWENERGY | W1-003
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0245 |  |  | 0 |  | 1 | NEWENERGY | W1-006
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0245 |  |  | 0 |  | 1 | NEWENERGY | W1-005
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.0245 |  |  | 0 |  | 1 | CAPACITY | W1-006
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.0245 |  |  | 0 |  | 1 | CAPACITY | W1-004
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.0245 |  |  | 0 |  | 1 | CAPACITY | W1-005
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.0245 |  |  | 0 |  | 1 | CAPACITY | W1-003
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0 |  |  | 0.02443 |  |  | 0 |  | 1 | NEWENERGY | X1-032
293670 | O-025 C | 25 | 235 | 64 | 0 | 6 | 4.82 |  |  | 0.02443 |  |  | 0 |  | 1 | CAPACITY
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 0 |  |  | 0.02442 |  |  | 0 |  | 1 | NEWENERGY | AA1-102
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 45.76 |  |  | 0.02442 |  |  | 0 |  | 1 | CAPACITY | AA1-102
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 8.03 |  |  | 0.02442 |  |  | 0 |  | 1 | CAPACITY
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0 |  |  | 0.02434 |  |  | 0 |  | 1 | NEWENERGY | Y3-058
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 5.7 | 4.58 |  |  | 0.02434 |  |  | 0 |  | 1 | CAPACITY | Y3-058
228721 | V2-035E | 12.9 | 234 | 75 | 1.2 | 1.2 | 0 |  |  | 0.02415 |  |  | 0 |  | 1 | NEWENERGY | V2-035
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.61 |  |  | 0.02415 |  |  | 0 |  | 1 | CAPACITY | V2-035
232919 | VN10 | 13.2 | 235 | 55 | 12.4 | 14.3 | 12.46 |  |  | 0.02401 |  |  | 0 |  | 1 | CAPACITY
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 122.84 |  |  | 0.02393 |  |  | 0.10478 |  | 1 | CAPACITY
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0 |  |  | 0.02393 |  |  | 0 |  | 1 | NEWENERGY | Y1-080
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 1.03 |  |  | 0.02393 |  |  | 0 |  | 1 | CAPACITY | Y1-080
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.02365 |  |  | 0 |  | 1 | NEWENERGY | X3-008
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.02365 |  |  | 0 |  | 1 | CAPACITY | X3-008
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0 |  |  | 0.02284 |  |  | 0 |  | 1 | NEWENERGY | AB1-021
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | 0.02284 |  |  | 0 |  | 1 | CAPACITY | AB1-021
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 55.4 |  |  | 0.02274 |  |  | 0.12623 |  | 1 | CAPACITY
228343 | QUINTN#1 | 12.9 | 234 | 64 | 0 | 1.7 | 0 |  |  | 0.02269 |  |  | 0 |  | 1 | CAPACITY
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0 |  |  | 0.02219 |  |  | 0 |  | 1 | NEWENERGY | Y1-079
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.02219 |  |  | 0 |  | 1 | CAPACITY | Y1-079
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0 |  |  | 0.02184 |  |  | 0 |  | 1 | NEWENERGY | X3-066
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 2.28 | 1.83 |  |  | 0.02184 |  |  | 0 |  | 1 | CAPACITY | X3-066
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 57.24 |  |  | 0.02167 |  |  | 0.10478 |  | 1 | CAPACITY
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 45.76 |  |  | 0.02167 |  |  | 0.08446 |  | 1 | CAPACITY
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 44.16 |  |  | 0.02167 |  |  | 0.04435 |  | 1 | CAPACITY | DELAWARE CITY
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 14.29 |  |  | 0.02167 |  |  | 0.08446 |  | 1 | CAPACITY
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.02146 |  |  | 0 |  | 1 | NEWENERGY | AB1-142
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.02146 |  |  | 0 |  | 1 | NEWENERGY | AB1-141
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.02146 |  |  | 0 |  | 1 | CAPACITY | AB1-141
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.02146 |  |  | 0 |  | 1 | CAPACITY | AB1-142
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 19.11 |  |  | 0.02143 |  |  | 0.12623 |  | 1 | CAPACITY
228357 | V2-046E | 12.9 | 234 | 75 | 12.9 | 12.9 | 0 |  |  | 0.02074 |  |  | 0 |  | 1 | NEWENERGY | V2-046
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 6.26 |  |  | 0.02074 |  |  | 0 |  | 1 | CAPACITY | V2-046
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 192.69 |  |  | 0.02054 |  |  | 0.10478 |  | 1 | CAPACITY
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01924 |  |  | 0 |  | 1 | NEWENERGY | AB2-179
233931 | AB2-179 C | 0.38 | 235 | 75 | 0 | 38 | 30.51 |  |  | 0.01924 |  |  | 0 |  | 1 | CAPACITY | AB2-179
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.09 |  |  | 0.01666 |  |  | 0 |  | 1 | CAPACITY
925112 | AB2-168 E | 34.5 | 235 | 75 | 0 | 5.2 | 0 |  |  | 0.01574 |  |  | 0 |  | 1 | NEWENERGY | AB2-168
925111 | AB2-168 C | 34.5 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.01574 |  |  | 0 |  | 1 | CAPACITY | AB2-168
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 58.9 | 47.29 |  |  | 0.01454 |  |  | 0.04435 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 58.9 | 47.29 |  |  | 0.01454 |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 13.81 |  |  | 0.01439 |  |  | 0.08446 |  | 1 | CAPACITY
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 18.47 |  |  | 0.01424 |  |  | 0.08446 |  | 1 | CAPACITY
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 18.39 |  |  | 0.01424 |  |  | 0.08446 |  | 1 | CAPACITY
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 139.7 |  |  | 0.01288 |  |  | 0.10478 |  | 1 | CAPACITY
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01288 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01288 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01278 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 69.05 |  |  | 0.01278 |  |  | 0.10478 |  | 1 | CAPACITY
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 11.4 |  |  | 0.01278 |  |  | 0.08446 |  | 1 | CAPACITY
937512 | AD2-210 E | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | 0.01271 |  |  | 0 |  | 1 | MTX | AD2-210
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 175.82 |  |  | 0.01249 |  |  | 0.10478 |  | 1 | CAPACITY
219001 | SEWAREN7GT | 25 | 231 | 58 | 101.5 | 324.6 | 260.61 |  |  | 0.01192 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-089
219002 | SEWAREN7ST | 18 | 231 | 58 | 96.3 | 216.4 | 173.74 |  |  | 0.01192 |  |  | 0 |  | 1 | CAPACITY | Z2-089
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | 0.01192 |  |  | 0 |  | 1 | ENERGY | Z2-089
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | 0.01192 |  |  | 0.04435 |  | 1 | ENERGY | Z2-089
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 66.1 | 98 | 78.68 |  |  | 0.01169 |  |  | 0.08446 |  | 1 | CAPACITY
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 87.02 |  |  | 0.01169 |  |  | 0.08446 |  | 1 | CAPACITY
206327 | 28S RIV G1 | 13.8 | 228 | 57 | 86.9 | 99.9 | 87.02 |  |  | 0.01169 |  |  | 0.08446 |  | 1 | CAPACITY
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | 0.01147 |  |  | 0 |  | 1 | ENERGY
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 43.63 |  |  | 0.01132 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 46.17 |  |  | 0.01132 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
228471 | VALERO1 | 13.8 | 234 | 2 | 19.1 | 22 | 19.16 |  |  | 0.01128 |  |  | 0 |  | 1 | CAPACITY
228473 | VALERO3 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.01128 |  |  | 0 |  | 1 | CAPACITY
228484 | VALERO4 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.01128 |  |  | 0 |  | 1 | CAPACITY
228472 | VALERO2 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.01128 |  |  | 0 |  | 1 | CAPACITY
933332 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | 0.01085 |  |  | 0 |  | 1 | MTX | AC2-145
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 55.49 |  |  | 0.0105 |  |  | 0.08446 |  | 1 | CAPACITY
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0 |  |  | 0.00921 |  |  | 0 |  | 1 | NEWENERGY | W2-056
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 3.36 |  |  | 0.00921 |  |  | 0 |  | 1 | CAPACITY | W2-056
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0 |  |  | 0.00919 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 N
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 0.00919 |  |  | 0 |  | 1 | CAPACITY | AB1-025 N
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | 0.00918 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 141.3 |  |  | 0.00918 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 199.11 |  |  | 0.00811 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | 0.00811 |  |  | 0.04435 |  | 1 | CAPACITY | RED OAK
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | 0.00725 |  |  | 0.05 |  | 1 | MTX | AA2-061
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | 0.00725 |  |  | 0 |  | 1 | NEWENERGY | X1-012
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0 |  |  | 0.00725 |  |  | 0 |  | 1 | NEWENERGY | W3-106
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | 0.00725 |  |  | 0.05 |  | 1 | MTX | AA2-060
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0 |  |  | 0.00725 |  |  | 0 |  | 1 | NEWENERGY | W3-110
206742 | 28SUX_V3-011 | 34.5 | 228 | 64 | 0 | 2 | 0 |  |  | 0.00725 |  |  | 0 |  | 1 | CAPACITY
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | 0.00725 |  |  | 0 |  | 1 | NEWENERGY | W4-064
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 2.99 |  |  | 0.00726 |  |  | 0 |  | 1 | CAPACITY | Y1-020
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 2.97 |  |  | 0.00725 |  |  | 0 |  | 1 | CAPACITY | X1-012
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 2.29 |  |  | 0.00725 |  |  | 0 |  | 1 | CAPACITY | W3-110
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | 0.00725 |  |  | 0 |  | 1 | CAPACITY | W4-064
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 361.29 |  |  | 0.00708 |  |  | 0.10478 |  | 1 | CAPACITY
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 148.77 |  |  | 0.00708 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC1
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0 |  |  | 0.00688 |  |  | 0 |  | 1 | NEWENERGY | AC2-175
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0 |  |  | 0.00688 |  |  | 0 |  | 1 | NEWENERGY | AE1-081
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.77 |  |  | 0.00688 |  |  | 0 |  | 1 | CAPACITY | AE1-081
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0 |  |  | 0.0068 |  |  | 0 |  | 1 | NEWENERGY | W2-052
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | 0.0068 |  |  | 0 |  | 1 | CAPACITY | W2-052
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 369.31 |  |  | 0.00648 |  |  | 0.04435 |  | 1 | CAPACITY | Y1-065
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00648 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00648 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200055 | ROCKSP 4 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00648 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 4
200054 | ROCKSP 3 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00648 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 3
200052 | ROCKSP 1 | 18 | 225 | 57 | 145.7 | 167.5 | 145.91 |  |  | 0.00648 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 1
200053 | ROCKSP 2 | 18 | 225 | 57 | 144.9 | 166.5 | 145.04 |  |  | 0.00648 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 2
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0 |  |  | 0.00626 |  |  | 0 |  | 1 | NEWENERGY | Y1-075
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 0.00626 |  |  | 0 |  | 1 | CAPACITY | Y1-075
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 271.13 |  |  | 0.00554 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.00554 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.00554 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0 |  |  | 0.00535 |  |  | 0 |  | 1 | NEWENERGY | V4-005
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.88 |  |  | 0.00535 |  |  | 0 |  | 1 | CAPACITY | V4-005
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0 |  |  | 0.00473 |  |  | 0 |  | 1 | NEWENERGY | W2-071
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.85 |  |  | 0.00473 |  |  | 0 |  | 1 | CAPACITY | W2-071
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 245.67 |  |  | 0.00377 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | 0.00377 |  |  | 0.04435 |  | 1 | CAPACITY | RARITAN RIVER
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | 0.00377 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
207441 | AD1-113 ST | 18 | 228 | 58 | 0 | 25 | 0 |  |  | 0.00377 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207435 | AD1-113 CT2 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | 0.00377 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207434 | AD1-113 CT1 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | 0.00377 |  |  | 0.04435 |  | 1 | NEW | RARITAN RIVER
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 97.1 | 111.6 | 97.21 |  |  | 0.00377 |  |  | 0.08446 |  | 1 | CAPACITY
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 90.9 | 104.5 | 91.03 |  |  | 0.00377 |  |  | 0.08446 |  | 1 | CAPACITY
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 60.21 |  |  | 0.00372 |  |  | 0.10478 |  | 1 | CAPACITY
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.0023 |  |  | 0.04435 |  | 1 | CAPACITY | PHILLIPS ISLAND
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.0023 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213893 | PHLISST1 | 20 | 230 | 58 | 184 | 267 | 214.36 |  |  | 0.00228 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.00228 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1034.24 |  |  | 0.0014 |  |  | 0.01494 |  | 1 | CAPACITY
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 306.69 |  |  | 0.00137 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00137 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00137 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA2
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 154.95 |  |  | 0.00137 |  |  | 0 |  | 1 | CAPACITY | DELTA
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00137 |  |  | 0 |  | 1 | CAPACITY | DELTA
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00137 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00137 |  |  | 0 |  | 1 | CAPACITY | DELTA
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1049.33 |  |  | 0.00113 |  |  | 0.01494 |  | 1 | CAPACITY
933322 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | 0.00104 |  |  | 0 |  | 1 | MTX | AC2-144
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | 0.00093 |  |  | 0.0316 |  | 1 | CAPACITY
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | 0.00093 |  |  | 0.0316 |  | 1 | CAPACITY
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | 0.00093 |  |  | 0.0316 |  | 1 | CAPACITY
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0 |  |  | -8e-05 |  |  | 0 |  | 1 | NEWENERGY | Y3-087
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 1.84 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY | Y3-087
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | -0.00018 |  |  | 0.0316 |  | 1 | CAPACITY
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | -0.00018 |  |  | 0.0316 |  | 1 | CAPACITY
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | -0.00019 |  |  | 0.0316 |  | 1 | CAPACITY
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | -0.00019 |  |  | 0.0316 |  | 1 | CAPACITY
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | -0.00035 |  |  | 0.07484 |  | 1 | CAPACITY
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | -0.00035 |  |  | 0.07484 |  | 1 | CAPACITY
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 77.07 |  |  | -0.00034 |  |  | 0.07484 |  | 1 | CAPACITY
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | -0.00034 |  |  | 0.07484 |  | 1 | CAPACITY
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | -0.00034 |  |  | 0.07484 |  | 1 | CAPACITY
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 38.54 |  |  | -0.00034 |  |  | 0.07484 |  | 1 | CAPACITY
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 134 | 107.58 |  |  | -0.00074 |  |  | 0.08446 |  | 1 | CAPACITY
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEWENERGY | X1-095
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00114 |  |  | 0 |  | 1 | CAPACITY | X1-095
206747 | 28DSM_X3-029 | 34.5 | 228 | 29 | 0 | 11.15 | 0 |  |  | -0.00156 |  |  | 0.10478 |  | 1 | ENERGY
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | -0.00156 |  |  | 0.08446 |  | 1 | ENERGY
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0 |  |  | -0.00167 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 S
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00167 |  |  | 0 |  | 1 | CAPACITY | AB1-025 S
204651 | 27PORT CT | 13.8 | 227 | 56 | 4 | 35 | 28.1 |  |  | -0.00181 |  |  | 0.08446 |  | 1 | CAPACITY
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00206 |  |  | 0 |  | 1 | NEWENERGY | Y2-018
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00207 |  |  | 0 |  | 1 | NEWENERGY | Y2-081
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.00207 |  |  | 0 |  | 1 | CAPACITY | Y2-081
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 256.27 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | -0.00222 |  |  | 0.04435 |  | 1 | CAPACITY | HUNTERSTOWN
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 134.08 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0 |  |  | -0.00222 |  |  | 0 |  | 1 | NEWENERGY | X3-075
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -0.00235 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 33.72 |  |  | -0.00237 |  |  | 0.04435 |  | 1 | CAPACITY | EAGLE POINT
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 24.08 |  |  | -0.00237 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 20 | 16.06 |  |  | -0.00238 |  |  | 0.08446 |  | 1 | CAPACITY
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -0.00238 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0 |  |  | -0.00245 |  |  | 0 |  | 1 | NEWENERGY | AA2-072
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | -0.00247 |  |  | 0 |  | 1 | ENERGY
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 140.6 | 112.88 |  |  | -0.00248 |  |  | 0.08446 |  | 1 | CAPACITY
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 91.2 |  |  | -0.00248 |  |  | 0.08446 |  | 1 | CAPACITY
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 83.5 |  |  | -0.00248 |  |  | 0.08446 |  | 1 | CAPACITY
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 41.75 |  |  | -0.00248 |  |  | 0.08446 |  | 1 | CAPACITY
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.21 |  |  | -0.00248 |  |  | 0 |  | 1 | CAPACITY
220904 | CRANE G2 | 20 | 232 | 12 | 60 | 195 | 0 |  |  | -0.00253 |  |  | 0.10478 |  | 1 | NEW
220905 | CRANE GT | 4.16 | 232 | 55 | 0 | 14 | 0 |  |  | -0.00253 |  |  | 0.08446 |  | 1 | NEW
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 45.76 |  |  | -0.00254 |  |  | 0.10478 |  | 1 | CAPACITY
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.5 | 24.49 |  |  | -0.00254 |  |  | 0.08446 |  | 1 | CAPACITY
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 30 | 24.08 |  |  | -0.00254 |  |  | 0.08446 |  | 1 | CAPACITY
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 246 |  |  | -0.00256 |  |  | 0.10478 |  | 1 | CAPACITY
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 102.85 |  |  | -0.00256 |  |  | 0.10478 |  | 1 | CAPACITY
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | -0.00256 |  |  | 0.08446 |  | 1 | ENERGY
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 10.68 |  |  | -0.00256 |  |  | 0.08446 |  | 1 | CAPACITY
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 516 |  |  | -0.00259 |  |  | 0.10478 |  | 1 | CAPACITY
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 512.95 |  |  | -0.00259 |  |  | 0.10478 |  | 1 | CAPACITY
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 318.73 |  |  | -0.00259 |  |  | 0.10478 |  | 1 | CAPACITY
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 120 |  |  |  | -0.0026
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.49 |  |  | -0.00269 |  |  | 0 |  | 1 | CAPACITY
226895 | WOAKV2-037 E | 69 | 233 | 65 | 0 | 4.5 | 0 |  |  | -0.00275 |  |  | 0 |  | 1 | ENERGY
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 695.27 |  |  | -0.00281 |  |  | 0.01494 |  | 1 | CAPACITY
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 675.85 |  |  | -0.00281 |  |  | 0.01494 |  | 1 | CAPACITY
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.76 |  |  | -0.00283 |  |  | 0 |  | 1 | CAPACITY
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | -0.00284 |  |  | 0.08446 |  | 1 | ENERGY
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0 |  |  | -0.00286 |  |  | 0 |  | 1 | NEWENERGY | AB2-157
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.69 |  |  | -0.00286 |  |  | 0 |  | 1 | CAPACITY
925011 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00286 |  |  | 0 |  | 1 | CAPACITY | AB2-157
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 477.7 |  |  | -0.00287 |  |  | 0.10478 |  | 1 | CAPACITY
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 469.91 |  |  | -0.00287 |  |  | 0.10478 |  | 1 | CAPACITY
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
227024 | SMECOCT | 13.8 | 238 | 57 | 30 | 80.2 | 64.39 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 19.59 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 14.45 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 497.29 |  |  | -0.00288 |  |  | 0.10478 |  | 1 | CAPACITY
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 492.39 |  |  | -0.00288 |  |  | 0.10478 |  | 1 | CAPACITY
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 272.01 |  |  | -0.00289 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | -0.00289 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | -0.00289 |  |  | 0.04435 |  | 1 | CAPACITY | WALDORF
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 0 |  |  | -0.00288 |  |  | 0 |  | 1 | NEWENERGY | AC2-101
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 0 |  |  | -0.00288 |  |  | 0 |  | 1 | NEWENERGY | AC2-120
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00288 |  |  | 0.08446 |  | 1 | CAPACITY
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00288 |  |  | 0.08446 |  | 1 | CAPACITY
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00288 |  |  | 0.08446 |  | 1 | CAPACITY
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00288 |  |  | 0.08446 |  | 1 | CAPACITY
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | -0.00288 |  |  | 0.08446 |  | 1 | CAPACITY
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | -0.00288 |  |  | 0.08446 |  | 1 | CAPACITY
226915 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 9.92 |  |  | -0.00288 |  |  | 0 |  | 1 | CAPACITY | AC2-101
226912 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 8.39 |  |  | -0.00288 |  |  | 0 |  | 1 | CAPACITY | AC2-120
910861 | X3-087 C | 230 | 233 | 58 | 0 | 744 | 597.33 |  |  | -0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
917371 | Z2-060 | 230 | 233 | 58 | 0 | 116 | 93.13 |  |  | -0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
920642 | AA2-170 E | 230 | 233 | 58 | 0 | 19.1 | 0 |  |  | -0.00294 |  |  | 0.04435 |  | 1 | NEW | AA2-170
920641 | AA2-170 C | 230 | 233 | 58 | 0 | 92 | 73.86 |  |  | -0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-170
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 64.23 |  |  | -0.00294 |  |  | 0 |  | 1 | CAPACITY | PANDA
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | -0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | PANDA
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | -0.00294 |  |  | 0 |  | 1 | CAPACITY | PANDA
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 330 | 264.94 |  |  | -0.00296 |  |  | 0 |  | 1 | CAPACITY | X4-035
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | -0.00296 |  |  | 0.04435 |  | 1 | CAPACITY | X4-035
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | -0.00296 |  |  | 0 |  | 1 | CAPACITY | X4-035
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | -0.00298 |  |  | 0.10478 |  | 1 | ENERGY
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 4 | 3.21 |  |  | -0.00298 |  |  | 0 |  | 1 | CAPACITY
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00299 |  |  | 0 |  | 1 | NEWENERGY | W4-046
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 1.93 |  |  | -0.00299 |  |  | 0 |  | 1 | CAPACITY | W4-046
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | -0.00304 |  |  | 0 |  | 1 | ENERGY
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | -0.00312 |  |  | 0.08446 |  | 1 | CAPACITY
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | -0.00312 |  |  | 0.08446 |  | 1 | CAPACITY
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 41.75 |  |  | -0.00312 |  |  | 0.10478 |  | 1 | CAPACITY
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 14.45 |  |  | -0.00312 |  |  | 0.08446 |  | 1 | CAPACITY
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 0 |  |  | -0.00322 |  |  | 0 |  | 1 | NEWENERGY | AB2-129
924771 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 0 |  |  | -0.00322 |  |  | 0 |  | 1 | NEW | AB2-129
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 245.67 |  |  | -0.00329 |  |  | 0 |  | 1 | CAPACITY | X4-039
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.00329 |  |  | 0 |  | 1 | CAPACITY | X4-039
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.00329 |  |  | 0.04435 |  | 1 | CAPACITY | X4-039
313821 | 6PACIFIC | 230 | 345 | 75 | 0 | 0.09 | 0 |  |  | -0.00331 |  |  | 0 |  | 1 | NEWENERGY
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 31.31 |  |  | -0.00334 |  |  | 0.08446 |  | 1 | CAPACITY
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 201.52 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00334 |  |  | 0.04435 |  | 1 | CAPACITY | POSSUM POINT
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00335 |  |  | 0.10478 |  | 1 | CAPACITY
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00335 |  |  | 0.10478 |  | 1 | CAPACITY
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 28.74 |  |  | -0.00334 |  |  | 0.10478 |  | 1 | CAPACITY
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 28.66 |  |  | -0.00334 |  |  | 0.10478 |  | 1 | CAPACITY
314088 | 6VANDORN | 230 | 345 | 2 | 7 | 21 | 16.86 |  |  | -0.00335 |  |  | 0 |  | 1 | CAPACITY
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00339 |  |  | 0 |  | 1 | NEWENERGY | AC2-072
932521 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00339 |  |  | 0 |  | 1 | CAPACITY | AC2-072
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 0.68 | 0 |  |  | -0.00341 |  |  | 0 |  | 1 | NEWENERGY
235002 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEW | AC1-039
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEWENERGY | AC1-039
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEWENERGY | AA1-109
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 3.61 |  |  | -0.00343 |  |  | 0 |  | 1 | CAPACITY | AA1-109
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00344 |  |  | 0.08446 |  | 1 | CAPACITY
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00344 |  |  | 0.08446 |  | 1 | CAPACITY
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 1.61 |  |  | -0.00344 |  |  | 0 |  | 1 | CAPACITY
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.00345 |  |  | 0 |  | 1 | NEWENERGY | W1-116
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 4.27 |  |  | -0.00345 |  |  | 0 |  | 1 | CAPACITY | W1-116
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00347 |  |  | 0.08446 |  | 1 | CAPACITY
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00347 |  |  | 0.08446 |  | 1 | CAPACITY
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 128.86 |  |  | -0.00347 |  |  | 0.08446 |  | 1 | CAPACITY
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 152.3 | 122.28 |  |  | -0.00347 |  |  | 0.10478 |  | 1 | CAPACITY
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00347 |  |  | 0.10478 |  | 1 | CAPACITY
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00347 |  |  | 0.10478 |  | 1 | CAPACITY
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 120.19 |  |  | -0.00347 |  |  | 0.10478 |  | 1 | CAPACITY
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 0 |  |  | -0.00348 |  |  | 0 |  | 1 | NEWENERGY | AB2-029
314078 | 3REMNGTN | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00348 |  |  | 0 |  | 1 | CAPACITY | AB2-029
315033 | 1BIRCHWDA | 18 | 345 | 13 | 85 | 238 | 191.08 |  |  | -0.00349 |  |  | 0.10478 |  | 1 | CAPACITY
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
923213 | AB1-125 E OP | 34.5 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
923202 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AB1-096
923212 | AB1-125 C OP | 34.5 | 201 | 75 | 0 | 5.7 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 6.98 |  |  | -0.0035 |  |  | 0 |  | 1 | CAPACITY
930521 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 2.49 |  |  | -0.0035 |  |  | 0 |  | 1 | CAPACITY | AB1-096
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 2
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 1
926737 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.0035 |  |  | 0 |  | 1 | CAPACITY | AC1-158 1
926738 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.0035 |  |  | 0 |  | 1 | CAPACITY | AC1-158 2
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00351 |  |  | 0.08446 |  | 1 | CAPACITY
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00351 |  |  | 0.08446 |  | 1 | CAPACITY
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 128.94 |  |  | -0.00351 |  |  | 0.08446 |  | 1 | CAPACITY
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 128.54 |  |  | -0.00351 |  |  | 0.08446 |  | 1 | CAPACITY
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 128.3 |  |  | -0.00351 |  |  | 0.08446 |  | 1 | CAPACITY
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0 |  |  | -0.00351 |  |  | 0 |  | 1 | NEWENERGY | AC2-136
933251 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 4.41 |  |  | -0.00351 |  |  | 0 |  | 1 | CAPACITY | AC2-136
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 761.83 |  |  | -0.00352 |  |  | 0.01494 |  | 1 | CAPACITY
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 761.51 |  |  | -0.00352 |  |  | 0.01494 |  | 1 | CAPACITY
923872 | AB2-027 E | 34.5 | 201 | 75 | 0 | 5.5 | 0 |  |  | -0.00353 |  |  | 0 |  | 1 | NEWENERGY | AB2-027
235006 | AB2-027 C | 34.5 | 201 | 75 | 0 | 3.3 | 0 |  |  | -0.00353 |  |  | 0 |  | 1 | NEW | AB2-027
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00353 |  |  | 0 |  | 1 | CAPACITY
316149 | AD1-046 E | 230 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00355 |  |  | 0 |  | 1 | NEWENERGY | AD1-044
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00356 |  |  | 0 |  | 1 | NEWENERGY | W4-102
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0 |  |  | -0.00356 |  |  | 0 |  | 1 | NEWENERGY | AB2-097
237799 | 01AA2-159 C | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.00356 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
920562 | AA2-159 E | 34.5 | 201 | 75 | 0 | 7.3 | 0 |  |  | -0.00356 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00355 |  |  | 0 |  | 1 | NEWENERGY | AE1-124
316148 | AD1-046 C | 230 | 345 | 75 | 0 | 30.7 | 24.65 |  |  | -0.00355 |  |  | 0 |  | 1 | CAPACITY | AD1-044
938961 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00355 |  |  | 0 |  | 1 | CAPACITY | AE1-124
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00356 |  |  | 0 |  | 1 | CAPACITY | W4-102
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 0 |  |  | -0.00357 |  |  | 0 |  | 1 | NEWENERGY | AB2-158
925021 | AB2-158 C | 230 | 345 | 75 | 0 | 61 | 48.97 |  |  | -0.00357 |  |  | 0 |  | 1 | CAPACITY | AB2-158
314766 | 6LOUISA | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00357 |  |  | 0 |  | 1 | NEWENERGY
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 2.09 |  |  | -0.00356 |  |  | 0 |  | 1 | CAPACITY
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.88 |  |  | -0.00356 |  |  | 0 |  | 1 | CAPACITY
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0 |  |  | -0.00358 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
923192 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0 |  |  | -0.00358 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 0 |  |  | -0.00357 |  |  | 0 |  | 1 | NEWENERGY | AC1-118
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0 |  |  | -0.00358 |  |  | 0 |  | 1 | NEWENERGY | AA1-095
314190 | 6WESTMOR | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00357 |  |  | 0 |  | 1 | CAPACITY | AC1-118
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 2.33 |  |  | -0.00358 |  |  | 0 |  | 1 | CAPACITY | AA1-095
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 136.49 |  |  | -0.00359 |  |  | 0.08446 |  | 1 | CAPACITY
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.0036 |  |  | 0.08446 |  | 1 | CAPACITY
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.0036 |  |  | 0.08446 |  | 1 | CAPACITY
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 126.85 |  |  | -0.00359 |  |  | 0.08446 |  | 1 | CAPACITY
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.0036 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 5
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.0036 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 6
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00359 |  |  | 0.08446 |  | 1 | CAPACITY
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00359 |  |  | 0.08446 |  | 1 | CAPACITY
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00359 |  |  | 0.08446 |  | 1 | CAPACITY
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 61.9 |  |  | -0.00359 |  |  | 0.08446 |  | 1 | CAPACITY
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00359 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00359 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 2
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.0036 |  |  | 0 |  | 1 | NEWENERGY | AC2-138
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 19.99 |  |  | -0.0036 |  |  | 0.10478 |  | 1 | CAPACITY
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00359 |  |  | 0 |  | 1 | CAPACITY | South Anna 2
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00359 |  |  | 0 |  | 1 | CAPACITY | South Anna 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 19.27 |  |  | -0.0036 |  |  | 0.10478 |  | 1 | CAPACITY
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 6.3 | 5.06 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | AC2-138
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0 |  |  | -0.0036 |  |  | 0 |  | 1 | NEWENERGY | AA1-092
314172 | 6DUNNSVL | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0036 |  |  | 0 |  | 1 | NEWENERGY
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 6.42 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | AA1-092
314734 | 6CASHSCORNER | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00361 |  |  | 0 |  | 1 | NEWENERGY
314222 | 6HANOVER | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00362 |  |  | 0 |  | 1 | NEWENERGY
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY | AC1-112
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY | AB1-027
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY | AC2-070
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 8.83 |  |  | -0.00364 |  |  | 0.12623 |  | 1 | CAPACITY
314241 | 6OLDCHRC | 230 | 345 | 75 | 0 | 1.82 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | CAPACITY | AB1-027
932501 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 7.39 |  |  | -0.00364 |  |  | 0 |  | 1 | CAPACITY | AC2-070
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 3.21 |  |  | -0.00363 |  |  | 0 |  | 1 | CAPACITY
314213 | 3CARVER | 115 | 345 | 75 | 0 | 0 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEW | AC1-107
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00365 |  |  | 0.04435 |  | 1 | NEW | AC1-107
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEW | AC1-107
926785 | AC1-164 E | 0.44 | 345 | 75 | 0 | 99.2 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEWENERGY | AC1-164
316114 | AB2-068 ST | 22 | 345 | 58 | 0 | 492 | 395.01 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316113 | AB2-068 CT2 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316112 | AB2-068 CT1 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00365 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-068
926784 | AC1-164 C | 0.44 | 345 | 75 | 0 | 220.8 | 177.27 |  |  | -0.00365 |  |  | 0 |  | 1 | NEW | AC1-164
314189 | 6PAPERMILL | 230 | 345 | 1 | 12 | 37 | 0 |  |  | -0.00365 |  |  | 0.10478 |  | 1 | ENERGY
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY | AC1-065
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 69.05 |  |  | -0.00364 |  |  | 0.10478 |  | 1 | CAPACITY
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 68.97 |  |  | -0.00364 |  |  | 0.10478 |  | 1 | CAPACITY
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 68.72 |  |  | -0.00364 |  |  | 0.10478 |  | 1 | CAPACITY
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 68.64 |  |  | -0.00364 |  |  | 0.10478 |  | 1 | CAPACITY
925863 | AC1-065 C | 0.39 | 345 | 75 | 0 | 41.8 | 33.56 |  |  | -0.00364 |  |  | 0 |  | 1 | CAPACITY | AC1-065
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEWENERGY | AC2-137
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY | AD2-030
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEWENERGY | AE1-074
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEWENERGY | AB2-024
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY | AD1-063
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 16.06 |  |  | -0.00364 |  |  | 0.12623 |  | 1 | CAPACITY
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.3 | 13.09 |  |  | -0.00365 |  |  | 0.12623 |  | 1 | CAPACITY
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 11.96 |  |  | -0.00365 |  |  | 0.12623 |  | 1 | CAPACITY
938551 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | AE1-074
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00364 |  |  | 0 |  | 1 | CAPACITY | AD2-030
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 11.4 | 9.15 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | AC2-137
314375 | 6CORRCTN | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | AB2-024
314187 | 3WAN 176 | 115 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY
934391 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.00364 |  |  | 0 |  | 1 | CAPACITY | AD1-063
314176 | 6HARMONY | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 4.98 |  |  | -0.00364 |  |  | 0 |  | 1 | CAPACITY
315085 | 1SPRUNCC | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00365 |  |  | 0.10478 |  | 1 | NEW
315086 | 1SPRUNCD | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00365 |  |  | 0.10478 |  | 1 | NEW
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 104.93 |  |  | -0.00365 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 7
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 103.25 |  |  | -0.00365 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 8
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 53.15 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 48.17 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7
314294 | 6ENON | 230 | 345 | 75 | 0 | 0.23 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEWENERGY
313828 | 3WHITEMARSH | 115 | 345 | 75 | 0 | 0.05 | 0 |  |  | -0.00366 |  |  | 0 |  | 1 | NEWENERGY
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | -0.00367 |  |  | 0.10478 |  | 1 | ENERGY
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 101.16 |  |  | -0.00367 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00367 |  |  | 0.04435 |  | 1 | CAPACITY | HOPEWELL HCF
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00367 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00367 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00367 |  |  | 0.10478 |  | 1 | CAPACITY
314177 | 3HAYES89 | 115 | 345 | 75 | 0 | 0.31 | 0 |  |  | -0.00367 |  |  | 0 |  | 1 | NEWENERGY
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 788.9 | 633.38 |  |  | -0.00368 |  |  | 0.10478 |  | 1 | CAPACITY
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 422.86 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 0 |  |  | -0.00368 |  |  | 0 |  | 1 | NEWENERGY | AB2-134
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00368 |  |  | 0.04435 |  | 1 | CAPACITY | WARREN COUNTY CC
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00368 |  |  | 0 |  | 1 | NEWENERGY | AB2-160
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 0 |  |  | -0.00367 |  |  | 0 |  | 1 | NEWENERGY | AB2-190
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 89.92 |  |  | -0.00367 |  |  | 0 |  | 1 | CAPACITY | AB2-190
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 57.65 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | AB2-134
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 24.41 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | AB2-160
316158 | AD2-164 | 230 | 345 | 57 | 0 | 26.7 | 21.44 |  |  | -0.00368 |  |  | 0.08446 |  | 1 | CAPACITY
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 12.04 |  |  | -0.00368 |  |  | 0.12623 |  | 1 | CAPACITY
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 8.03 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY
313812 | 6ROCKLANDING | 230 | 345 | 75 | 0 | 0.11 | 0 |  |  | -0.00368 |  |  | 0 |  | 1 | NEWENERGY
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 678.09 |  |  | -0.00369 |  |  | 0.01494 |  | 1 | CAPACITY
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 677.21 |  |  | -0.00368 |  |  | 0.01494 |  | 1 | CAPACITY
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 69.77 |  |  | -0.00369 |  |  | 0.10478 |  | 1 | CAPACITY
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 69.69 |  |  | -0.00369 |  |  | 0.10478 |  | 1 | CAPACITY
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00369 |  |  | 0.10478 |  | 1 | CAPACITY
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00369 |  |  | 0.10478 |  | 1 | CAPACITY
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 23.76 |  |  | -0.00369 |  |  | 0.10478 |  | 1 | CAPACITY
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY | AB2-161
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 88.96 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 87.83 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 86.31 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
314331 | 6POE | 230 | 345 | 75 | 0 | 12.27 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY | AD1-060
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY | AE1-162
935212 | AD1-156 E | 230 | 345 | 75 | 0 | 7.92 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY | AD1-156
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AC1-147
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.00369 |  |  | 0 |  | 1 | CAPACITY | AB2-161
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 12.2 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 11.96 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 10.36 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
926661 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 10.12 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AC1-147
316258 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00369 |  |  | 0 |  | 1 | CAPACITY | AE1-162
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 9.55 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
935211 | AD1-156 C | 230 | 345 | 75 | 0 | 11.82 | 9.49 |  |  | -0.00369 |  |  | 0 |  | 1 | CAPACITY | AD1-156
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 9.05 |  |  | -0.0037 |  |  | 0.12623 |  | 1 | CAPACITY
314533 | 6SMITFLD | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY
934362 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 4.58 |  |  | -0.00369 |  |  | 0 |  | 1 | CAPACITY | AD1-060
314453 | 6CHRHLND | 230 | 345 | 75 | 0 | 0.08 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY
314487 | 3MCLAUGH | 115 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY | AA1-139
314525 | 6KINGFORK | 230 | 345 | 75 | 0 | 24.3 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY
314550 | 6HICKORY | 230 | 345 | 75 | 0 | 22.93 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 63.18 |  |  | -0.00371 |  |  | 0 |  | 1 | CAPACITY | AA1-139
314466 | 6FENTRES | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY
313717 | 6SLIGO L2192 | 230 | 345 | 75 | 0 | 12.34 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | Z1-068
316145 | AE1-027 E | 230 | 345 | 75 | 0 | 6.9 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AE1-027
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AC2-196
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AC1-027
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AB2-026
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AE1-075
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AD1-144
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AD2-215
316147 | AE1-028 E | 230 | 345 | 75 | 0 | 4.4 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AE1-028
314333 | 6POWHATN | 230 | 345 | 75 | 0 | 3.97 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AB2-026
314645 | 6SLIGO L269 | 230 | 345 | 75 | 0 | 3.22 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY
316144 | AE1-027 C | 230 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AE1-027
938561 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AE1-075
933731 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 8.03 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AC2-196
316150 | AD2-215 C | 230 | 345 | 76 | 0 | 9.8 | 7.87 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AD2-215
935111 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 7.79 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AD1-144
314491 | 3PENDLTN | 115 | 345 | 75 | 0 | 1.89 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AC1-027
316146 | AE1-028 C | 230 | 345 | 75 | 0 | 7.6 | 6.1 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AE1-028
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.2 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | Z1-068
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | NEWENERGY | Y1-086
314632 | 6AYDLETOLD | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | NEWENERGY | AB2-022
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY | Z2-030
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY | AC2-174
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | NEWENERGY | Z2-027
933571 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEW | AC2-174
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 12.04 |  |  | -0.00371 |  |  | 0.12623 |  | 1 | CAPACITY
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 10.44 |  |  | -0.00372 |  |  | 0 |  | 1 | CAPACITY | AB2-022
314648 | 6SUNBURY | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | NEWENERGY
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | MTX | Z1-082
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 3.93 |  |  | -0.00371 |  |  | 0 |  | 1 | CAPACITY
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00371 |  |  | 0 |  | 1 | CAPACITY | Z2-030
314638 | 6ELIZ CT | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | CAPACITY | Y1-086
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 1.61 |  |  | -0.00371 |  |  | 0 |  | 1 | CAPACITY
314639 | 6TANGLEW | 230 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | CAPACITY | Z2-027
314640 | 6KITTY HAWK | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY
901082 | W1-029 E | 230 | 345 | 74 | 0 | 261 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | NEWENERGY | W1-029
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00372 |  |  | 0 |  | 1 | CAPACITY | W1-029
314651 | 6WINFALL | 230 | 345 | 75 | 0 | 3.35 | 0 |  |  | -0.00373 |  |  | 0 |  | 1 | NEWENERGY
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.56 |  |  | -0.00372 |  |  | 0 |  | 1 | CAPACITY
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 0 |  |  | -0.00374 |  |  | 0 |  | 1 | NEWENERGY | Z1-036
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00374 |  |  | 0 |  | 1 | CAPACITY | Z1-036
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00373 |  |  | 0 |  | 1 | NEWENERGY | AB2-025
314435 | 6SAPONY | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00373 |  |  | 0 |  | 1 | CAPACITY | AB2-025
942852 | AE2-304 E | 230 | 345 | 75 | 0 | 1.4 | 0 |  |  | -0.00373 |  |  | 0 |  | 1 | NEWENERGY | AE2-304
942851 | AE2-304 C | 230 | 345 | 75 | 0 | 3.3 | 2.65 |  |  | -0.00373 |  |  | 0 |  | 1 | CAPACITY | AE2-304
314662 | 6S HERTFORD | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00373 |  |  | 0 |  | 1 | NEWENERGY
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | -0.00375 |  |  | 0.10478 |  | 1 | ENERGY
314637 | 6EDENTON | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00375 |  |  | 0 |  | 1 | NEWENERGY | AA2-059
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 480.11 |  |  | -0.00375 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 452.01 |  |  | -0.00376 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00375 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-086
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00375 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00375 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00376 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00376 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00376 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 0 |  |  | -0.00375 |  |  | 0 |  | 1 | NEW | AB2-015
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 0 |  |  | -0.00375 |  |  | 0 |  | 1 | NEWENERGY | AB2-015
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00376 |  |  | 0.10478 |  | 1 | CAPACITY
314541 | 3WATKINS | 115 | 345 | 1 | 0 | 4 | 0 |  |  | -0.00376 |  |  | 0 |  | 1 | ENERGY
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00377 |  |  | 0.10478 |  | 1 | CAPACITY
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00376 |  |  | 0 |  | 1 | NEWENERGY | AA2-178
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00376 |  |  | 0 |  | 1 | CAPACITY | AA2-178
314566 | 3CRESWEL | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00376 |  |  | 0 |  | 1 | NEWENERGY
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  |  |  | -0.0038
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 322.35 |  |  | -0.00377 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 0 |  |  | -0.00377 |  |  | 0 |  | 1 | NEWENERGY | AA2-088
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 198.31 |  |  | -0.00377 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00377 |  |  | 0.04435 |  | 1 | CAPACITY | BEAR GARDEN
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00377 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00377 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00377 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00377 |  |  | 0.04435 |  | 1 | CAPACITY | FLUVANNA
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 2
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | AC1-116
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 30.51 |  |  | -0.00377 |  |  | 0 |  | 1 | CAPACITY | AA2-088
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | AB2-100 1
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | AB2-100 2
926451 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 3.77 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | AC1-116
314594 | 6PLYMOTH | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00377 |  |  | 0 |  | 1 | NEWENERGY
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY | AB1-128
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY | AB1-127
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | AC2-071
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | AB2-045
314589 | 3MURPHYS | 115 | 345 | 75 | 0 | 4.66 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | V4-068
932511 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | AC2-071
314617 | 3TUNIS | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY
314677 | 6BUCKING | 230 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | AB2-045
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | V4-068
235041 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00379 |  |  | 0 |  | 1 | CAPACITY | AB1-128
235040 | 01AB1-127 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00379 |  |  | 0 |  | 1 | CAPACITY | AB1-127
314620 | 6CASHIE | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY
313826 | 6HYDRAULIC | 230 | 345 | 75 | 0 | 0.04 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 538.72 |  |  | -0.0038 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-116
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AB2-174
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY | AA1-065
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AA1-063A
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 53.6 | 43.03 |  |  | -0.00379 |  |  | 0 |  | 1 | CAPACITY | AA1-065
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 40.87 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY | AA1-063A
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 40.14 |  |  | -0.00379 |  |  | 0.19858 |  | 1 | CAPACITY
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 33.72 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY | AB2-174
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 27.3 |  |  | -0.00379 |  |  | 0.08446 |  | 1 | CAPACITY
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AB1-139
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEW
314568 | 3EARLEYS | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY | AB2-099
314551 | 3AHOSKIE | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AE1-041
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00379 |  |  | 0 |  | 1 | CAPACITY | AB2-099
314604 | 3SEABORD | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY
930901 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 2.01 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY | AB1-139
938281 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY | AE1-041
923262 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
923991 | AB2-040 C O1 | 115 | 345 | 75 | 0 | 44 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEW | AB2-040
923992 | AB2-040 E O1 | 115 | 345 | 75 | 0 | 36 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AB2-040
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY | AA2-053
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.0038 |  |  | 0.07484 |  | 1 | CAPACITY
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.0038 |  |  | 0.07484 |  | 1 | CAPACITY
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 44 |  |  | -0.00381 |  |  | 0 |  | 1 | CAPACITY | AA2-053
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 32.44 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY | AB1-173
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AB1-173
314266 | 6NORTHAMPTON | 230 | 345 | 75 | 0 | 2.47 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY
314626 | 3WOODLND | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY
314596 | 3POPLR C | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY
314762 | 3JAMES R | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.5 | 354.46 |  |  | -0.00381 |  |  | 0.10478 |  | 1 | CAPACITY
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 350.93 |  |  | -0.00381 |  |  | 0.10478 |  | 1 | CAPACITY
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00382 |  |  | 0.10478 |  | 1 | CAPACITY
925122 | AB2-169 E | 115 | 345 | 75 | 0 | 35 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY | AB2-169
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 76.6 | 61.5 |  |  | -0.00381 |  |  | 0.04435 |  | 1 | CAPACITY | ROSEMARY
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 40.38 |  |  | -0.00381 |  |  | 0.07484 |  | 1 | CAPACITY
314807 | 3MT JACK | 115 | 345 | 75 | 0 | 9.7 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 38.54 |  |  | -0.00381 |  |  | 0.07484 |  | 1 | CAPACITY
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 47.5 | 38.13 |  |  | -0.00381 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
925121 | AB2-169 C | 115 | 345 | 75 | 0 | 39 | 31.31 |  |  | -0.00381 |  |  | 0 |  | 1 | CAPACITY | AB2-169
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 35.9 | 28.82 |  |  | -0.00381 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY | AC2-074
314578 | 3HORNRTN | 115 | 345 | 75 | 0 | 5.15 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY
314579 | 6HORNRTN | 230 | 345 | 75 | 0 | 3.91 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 8.83 |  |  | -0.00381 |  |  | 0.12623 |  | 1 | CAPACITY
932541 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY | AC2-074
314559 | 3CAROLNA | 115 | 345 | 75 | 0 | 1.21 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY
314582 | 3KELFORD | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | CAPACITY | Z2-043
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY | AD1-085
314713 | 3PAMPLIN | 115 | 345 | 75 | 0 | 9.73 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY
316143 | AD1-160 E | 115 | 345 | 75 | 0 | 9.1 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY | AD1-160
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY | AD1-157
313853 | 3PONTONDP | 115 | 345 | 2 | 0 | 4 | 0 |  |  | -0.00383 |  |  | 0 |  | 1 | ENERGY
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 16 | 12.85 |  |  | -0.00383 |  |  | 0.12623 |  | 1 | CAPACITY
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 9.88 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY | AD1-085
314603 | 3SCOT NK | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY
935221 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY | AD1-157
316142 | AD1-160 C | 115 | 345 | 75 | 0 | 6.6 | 5.3 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY | AD1-160
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 1.04 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.64 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY
314593 | 3PARMELE | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY
314629 | 3MARTNCO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY | AC1-054
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY | AC1-036
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 35.73 |  |  | -0.00384 |  |  | 0 |  | 1 | CAPACITY | AC1-054
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY | AE1-099
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY | AE1-098
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00384 |  |  | 0 |  | 1 | CAPACITY | AE1-098
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00384 |  |  | 0 |  | 1 | CAPACITY | AE1-099
925611 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 6.9 |  |  | -0.00384 |  |  | 0 |  | 1 | CAPACITY | AC1-036
314798 | 3MERCK5 | 115 | 345 | 75 | 0 | 0.16 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AB2-043
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AB2-060
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 43.67 |  |  | -0.00386 |  |  | 0 |  | 1 | CAPACITY | AB2-060
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00385 |  |  | 0.08446 |  | 1 | CAPACITY
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00385 |  |  | 0.08446 |  | 1 | CAPACITY
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AB2-077
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AB2-078
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AB2-079
314574 | 6EVERETS | 230 | 345 | 75 | 0 | 5.89 | 0 |  |  | -0.00385 |  |  | 0 |  | 1 | NEWENERGY
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0 |  |  | -0.00385 |  |  | 0 |  | 1 | NEWENERGY | AA1-067
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 15.17 |  |  | -0.00386 |  |  | 0 |  | 1 | CAPACITY | AB2-043
924311 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00386 |  |  | 0 |  | 1 | NEW | AB2-078
924321 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00386 |  |  | 0 |  | 1 | NEW | AB2-079
924301 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00386 |  |  | 0 |  | 1 | NEW | AB2-077
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY | Z2-088
919702 | AA2-057 E OP | 115 | 345 | 75 | 0 | 21.1 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AA2-057
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 53 | 42.55 |  |  | -0.00387 |  |  | 0 |  | 1 | CAPACITY | Z2-088
313719 | 3CHESTNUT | 115 | 345 | 75 | 0 | 44.7 | 35.89 |  |  | -0.00386 |  |  | 0 |  | 1 | CAPACITY | AA2-057
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
314608 | 3TARBORO | 115 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY | Z2-044
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 12.04 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
314623 | 3WITAKRS | 115 | 345 | 75 | 0 | 2.51 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | CAPACITY | Z2-044
314549 | 3TOT1 | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY
314557 | 3BETHELC | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY
314607 | 3TAR RVR | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY
314545 | 3TOT5 | 115 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY
314560 | 3CNETO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00389 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 0 |  |  | -0.00388 |  |  | 0 |  | 1 | NEWENERGY | AB2-059
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00388 |  |  | 0 |  | 1 | NEWENERGY | AB1-081
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 52.99 |  |  | -0.00388 |  |  | 0 |  | 1 | CAPACITY | AB2-059
922922 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00388 |  |  | 0 |  | 1 | CAPACITY | AB1-081
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00388 |  |  | 0.08446 |  | 1 | CAPACITY
314554 | 3BTLEBRO | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00388 |  |  | 0 |  | 1 | NEWENERGY
314205 | 3HEARTS | 115 | 345 | 75 | 0 | 0.41 | 0 |  |  | -0.00388 |  |  | 0 |  | 1 | NEWENERGY
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 0 |  |  | -0.0039 |  |  | 0 |  | 1 | NEWENERGY | T157
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 238 | 191.08 |  |  | -0.0039 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00389 |  |  | 0.04435 |  | 1 | CAPACITY | LIBERTY EDDY
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 0 |  |  | -0.00389 |  |  | 0 |  | 1 | NEWENERGY | AC1-105
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 36.61 |  |  | -0.0039 |  |  | 0.10478 |  | 1 | CAPACITY
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 27.7 |  |  | -0.00389 |  |  | 0 |  | 1 | CAPACITY | AC1-105
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 16.46 |  |  | -0.0039 |  |  | 0 |  | 1 | CAPACITY | T157
315616 | AA1-038 C | 230 | 345 | 74 | 0 | 76.6 | 0 |  |  | -0.00392 |  |  | 0 |  | 1 | NEW | AA1-038
918232 | AA1-038 E | 230 | 345 | 74 | 0 | 66.7 | 0 |  |  | -0.00392 |  |  | 0 |  | 1 | NEWENERGY | AA1-038
314860 | 4E MILL | 138 | 345 | 2 | 0 | 50 | 0 |  |  | -0.00392 |  |  | 0.10478 |  | 1 | ENERGY
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 20.23 |  |  | -0.00392 |  |  | 0.10478 |  | 1 | CAPACITY
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 20.15 |  |  | -0.00392 |  |  | 0.10478 |  | 1 | CAPACITY
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00392 |  |  | 0 |  | 1 | CAPACITY
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 404.48 |  |  | -0.00393 |  |  | 0.0316 |  | 1 | CAPACITY
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 403.68 |  |  | -0.00393 |  |  | 0.0316 |  | 1 | CAPACITY
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 403.27 |  |  | -0.00393 |  |  | 0.0316 |  | 1 | CAPACITY
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 403.2 |  |  | -0.00393 |  |  | 0.0316 |  | 1 | CAPACITY
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00393 |  |  | 0.0316 |  | 1 | CAPACITY
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00393 |  |  | 0.0316 |  | 1 | CAPACITY
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 0 |  |  | -0.00394 |  |  | 0 |  | 1 | NEWENERGY | K11
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 30.67 |  |  | -0.00394 |  |  | 0 |  | 1 | CAPACITY | K11
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 443.98 |  |  | -0.00395 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM2
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 440.13 |  |  | -0.00395 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 419.81 |  |  | -0.00395 |  |  | 0.10478 |  | 1 | CAPACITY
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 9.55 |  |  | -0.00395 |  |  | 0.08446 |  | 1 | CAPACITY
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | AC1-075
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 30.75 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | AC1-075
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | AC1-080
926023 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 10.28 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | AC1-080
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 68.3 |  |  |  | -0.004
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 23.68 |  |  | -0.00401 |  |  | 0.12623 |  | 1 | CAPACITY
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 106.94 |  |  | -0.00405 |  |  | 0.07484 |  | 1 | CAPACITY
208904 | HOLT 696 | 13.2 | 229 | 60 | 23 | 58.4 | 46.89 |  |  | -0.00405 |  |  | 0.07484 |  | 1 | CAPACITY
208903 | HOLT 695 | 13.2 | 229 | 60 | 26 | 53.2 | 42.71 |  |  | -0.00405 |  |  | 0.07484 |  | 1 | CAPACITY
919535 | V4-027 E | 0 | 229 | 75 | 0 | 3.1 | 0 |  |  | -0.00405 |  |  | 0 |  | 1 | NEWENERGY | V4-027
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 3.93 |  |  | -0.00405 |  |  | 0 |  | 1 | CAPACITY | V4-027
208474 | KINZ 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00405 |  |  | 0 |  | 1 | CAPACITY
244012 | 05PINNACLE | 4 | 205 | 1 | 0 | 11 | 0 |  |  | -0.00408 |  |  | 0.10478 |  | 1 | ENERGY
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 42.07 |  |  | -0.00408 |  |  | 0.10478 |  | 1 | CAPACITY
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00409 |  |  | 0 |  | 1 | NEWENERGY | AC1-145
926645 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.00409 |  |  | 0 |  | 1 | CAPACITY | AC1-145
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.9 | 40.06 |  |  | -0.0041 |  |  | 0.07484 |  | 1 | CAPACITY
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 1044 |  |  |  | -0.0041
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 154.95 |  |  | -0.00412 |  |  | 0.0316 |  | 1 | CAPACITY
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 152.54 |  |  | -0.00412 |  |  | 0.0316 |  | 1 | CAPACITY
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 97.14 |  |  | -0.00412 |  |  | 0.0316 |  | 1 | CAPACITY
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 59.41 |  |  | -0.00412 |  |  | 0.0316 |  | 1 | CAPACITY
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 57 |  |  | -0.00412 |  |  | 0.0316 |  | 1 | CAPACITY
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 3.21 |  |  | -0.00413 |  |  | 0 |  | 1 | CAPACITY
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00418 |  |  | 0 |  | 1 | NEWENERGY | AC1-117
926461 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00418 |  |  | 0 |  | 1 | NEW | AC1-117
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 144.51 |  |  | -0.00418 |  |  | 0.10478 |  | 1 | CAPACITY
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | -0.00418 |  |  | 0.05 |  | 1 | MTX | AA1-100
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 6.42 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00423 |  |  | 0 |  | 1 | NEWENERGY | AD1-018
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.00423 |  |  | 0 |  | 1 | NEW | AD1-018
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00424 |  |  | 0.07484 |  | 1 | CAPACITY
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00424 |  |  | 0.07484 |  | 1 | CAPACITY
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00424 |  |  | 0 |  | 1 | CAPACITY | N47
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 0 |  |  | -0.00425 |  |  | 0 |  | 1 | NEWENERGY | U2-073 A
235520 | 01WVACO_S38 | 13.8 | 201 | 2 | 0 | 60 | 0 |  |  | -0.00424 |  |  | 0 |  | 1 | NEW
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 0 |  |  | -0.00425 |  |  | 0 |  | 1 | NEWENERGY | U2-073 B
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 25.9 | 20.79 |  |  | -0.00425 |  |  | 0 |  | 1 | CAPACITY | U2-073 A
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00425 |  |  | 0 |  | 1 | CAPACITY | U2-073 B
270148 | AE1-018 E | 138 | 205 | 75 | 0 | 2.2 | 0 |  |  | -0.00426 |  |  | 0 |  | 1 | NEWENERGY | AE1-018
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 3.29 |  |  | -0.00425 |  |  | 0 |  | 1 | CAPACITY
270147 | AE1-018 C | 138 | 205 | 75 | 0 | 2.8 | 2.25 |  |  | -0.00426 |  |  | 0 |  | 1 | CAPACITY | AE1-018
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 0 |  |  | -0.00427 |  |  | 0 |  | 1 | NEWENERGY | S14
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 11.24 |  |  | -0.00427 |  |  | 0 |  | 1 | CAPACITY | S14
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00428 |  |  | 0 |  | 1 | MTX | AD2-205
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 14.1 | 11.32 |  |  | -0.00428 |  |  | 0.07484 |  | 1 | CAPACITY
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.7 | 7.79 |  |  | -0.00428 |  |  | 0 |  | 1 | CAPACITY
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 0 |  |  | -0.00428 |  |  | 0 |  | 1 | NEWENERGY | Y1-006
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 0 |  |  | -0.00429 |  |  | 0 |  | 1 | NEWENERGY | U2-030
913034 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 0 |  |  | -0.00428 |  |  | 0 |  | 1 | NEW | Y1-006
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | -0.00428 |  |  | 0.07484 |  | 1 | ENERGY
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 6.26 |  |  | -0.00429 |  |  | 0 |  | 1 | CAPACITY | U2-030
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 0 |  |  | -0.0043 |  |  | 0 |  | 1 | NEWENERGY | AC1-048
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 0 |  |  | -0.0043 |  |  | 0 |  | 1 | NEW | AC1-048
205910 | AC2-053 E | 0.39 | 227 | 74 | 0 | 12.4 | 0 |  |  | -0.0043 |  |  | 0 |  | 1 | NEWENERGY | AC2-053
205909 | AC2-053 C | 0.39 | 227 | 74 | 0 | 7.6 | 0 |  |  | -0.0043 |  |  | 0 |  | 1 | NEW | AC2-053
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00433 |  |  | 0.08446 |  | 1 | CAPACITY
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00433 |  |  | 0.08446 |  | 1 | CAPACITY
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00433 |  |  | 0.08446 |  | 1 | CAPACITY
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00433 |  |  | 0.08446 |  | 1 | CAPACITY
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00433 |  |  | 0.08446 |  | 1 | CAPACITY
242677 | 05INDDRV | 138 | 205 | 64 | 0 | 45 | 36.13 |  |  | -0.00433 |  |  | 0.12623 |  | 1 | CAPACITY
923772 | AB2-011 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00433 |  |  | 0 |  | 1 | NEWENERGY | AB2-011
923771 | AB2-011 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00433 |  |  | 0 |  | 1 | NEW | AB2-011
923762 | AB2-010 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00433 |  |  | 0 |  | 1 | NEWENERGY | AB2-010
923761 | AB2-010 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00433 |  |  | 0 |  | 1 | NEW | AB2-010
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  |  |  | -0.0043
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  |  |  | -0.0043
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 489.98 |  |  | -0.00434 |  |  | 0.10478 |  | 1 | CAPACITY
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 127.4 | 102.28 |  |  | -0.00434 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 101.08 |  |  | -0.00434 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 106.7 | 85.67 |  |  | -0.00434 |  |  | 0 |  | 1 | CAPACITY
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 84.78 |  |  | -0.00434 |  |  | 0 |  | 1 | CAPACITY
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 38 |  |  |  | -0.0044
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 1.3 | 1.04 |  |  | -0.00438 |  |  | 0 |  | 1 | CAPACITY
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 0 |  |  | -0.00438 |  |  | 0 |  | 1 | NEWENERGY | K28
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 0 |  |  | -0.00438 |  |  | 0 |  | 1 | NEWENERGY | K28
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.4 | 13.97 |  |  | -0.00438 |  |  | 0 |  | 1 | CAPACITY | K28
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 896 |  |  |  | -0.0044
342442 | 2W GLASGOW | 69 | 320 | 2 | 0 | 1 | 0.8 |  |  | -0.0044 |  |  | 0 |  | 1 | CAPACITY
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 180.64 |  |  | -0.0044 |  |  | 0.10478 |  | 1 | CAPACITY
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 93.13 |  |  | -0.0044 |  |  | 0.10478 |  | 1 | CAPACITY
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 64.23 |  |  | -0.0044 |  |  | 0.07484 |  | 1 | CAPACITY
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 56.2 |  |  | -0.00441 |  |  | 0.07484 |  | 1 | CAPACITY
342070 | 2PINE GROVE | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00441 |  |  | 0 |  | 1 | CAPACITY
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00441 |  |  | 0.07484 |  | 1 | CAPACITY
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00442 |  |  | 0.07484 |  | 1 | CAPACITY
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00441 |  |  | 0 |  | 1 | CAPACITY
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 0 |  |  | -0.00442 |  |  | 0 |  | 1 | NEWENERGY | M24
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 0 |  |  | -0.00442 |  |  | 0 |  | 1 | NEWENERGY | AB1-150
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | -0.00442 |  |  | 0.05 |  | 1 | MTX | M24 BAT
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 91.93 |  |  | -0.00443 |  |  | 0.07484 |  | 1 | CAPACITY
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 61.42 |  |  | -0.00443 |  |  | 0.07484 |  | 1 | CAPACITY
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00442 |  |  | 0 |  | 1 | CAPACITY | M24
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00443 |  |  | 0 |  | 1 | NEWENERGY | W1-127
931011 | AB1-150 C | 138 | 201 | 74 | 0 | 6.7 | 5.38 |  |  | -0.00442 |  |  | 0 |  | 1 | CAPACITY | AB1-150
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0 |  |  | -0.00443 |  |  | 0 |  | 1 | NEWENERGY | U2-059
925462 | AC1-018 E | 34.5 | 228 | 75 | 0 | 0.9 | 0 |  |  | -0.00443 |  |  | 0 |  | 1 | NEWENERGY | AC1-018
925461 | AC1-018 C | 34.5 | 228 | 75 | 0 | 0.5 | 0 |  |  | -0.00443 |  |  | 0 |  | 1 | NEW | AC1-018
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00443 |  |  | 0 |  | 1 | CAPACITY | W1-127
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00443 |  |  | 0 |  | 1 | CAPACITY | U2-059
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 244.87 |  |  | -0.00444 |  |  | 0.10478 |  | 1 | CAPACITY
247225 | 05FTHLG2 | 18 | 205 | 57 | 120 | 173.8 | 139.54 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247224 | 05FTHLG1 | 18 | 205 | 57 | 120 | 173.7 | 139.46 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247232 | 05RIVRG3 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247230 | 05RIVRG1 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247231 | 05RIVRG2 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.55 |  |  | -0.00443 |  |  | 0 |  | 1 | CAPACITY
918472 | AA1-062 E | 138 | 201 | 74 | 0 | 195 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | NEWENERGY | AA1-062
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 642.29 |  |  | -0.00445 |  |  | 0.10478 |  | 1 | CAPACITY
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00445 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00445 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 2
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
292981 | N-007 E | 138 | 201 | 74 | 0 | 30.4 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | NEWENERGY | N07
235801 | 01WM_AA1_062 | 138 | 201 | 74 | 0 | 29 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | NEW | AA1-062
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 109.5 | 87.91 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
920072 | AA2-103 E | 138 | 201 | 76 | -20 | 20 | 0 |  |  | -0.00445 |  |  | 0.05 |  | 1 | MTX | AA2-103
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 60.94 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 60.78 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 60.7 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 60.53 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 72.9 | 58.53 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 72.6 | 58.29 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 11.88 |  |  | -0.00445 |  |  | 0.07484 |  | 1 | CAPACITY
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | MTX | AB1-055
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | K19
235000 | N-007 C | 138 | 201 | 74 | 0 | 7.6 | 6.1 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | N07
341329 | 2COLESBURG | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1067.8 |  |  | -0.00445 |  |  | 0.10478 |  | 1 | CAPACITY | AMG3
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  |  |  | -0.0045
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 642.29 |  |  | -0.00445 |  |  | 0.10478 |  | 1 | CAPACITY
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | NEWENERGY | P59
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 0 |  |  | -0.00446 |  |  | 0 |  | 1 | NEWENERGY | U2-061
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 152 | 122.03 |  |  | -0.00446 |  |  | 0.08446 |  | 1 | CAPACITY
206341 | 28GIL 8 | 13.8 | 228 | 58 | 69.9 | 90 | 72.26 |  |  | -0.00446 |  |  | 0.04435 |  | 1 | CAPACITY | GILBERT
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 87 | 100 | 87.11 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY | GILBERT
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 85.3 | 98 | 85.37 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY | GILBERT
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | -0.0045
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.00446 |  |  | 0 |  | 1 | NEWENERGY | W3-077
925972 | AC1-073 E | 138 | 201 | 74 | 0 | 5.9 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | NEWENERGY | AC1-073
925971 | AC1-073 C | 138 | 201 | 74 | 0 | 5.8 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | NEW | AC1-073
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 9.39 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | P59
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 5.22 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY | U2-061
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 5.7 | 4.58 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY | W3-077
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY | W2-091
342031 | 2PACTOLUS | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 62.8 |  |  |  | -0.0045
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 55 | 44.16 |  |  | -0.00446 |  |  | 0.10478 |  | 1 | CAPACITY
341200 | 2BROMLEYEK | 69 | 320 | 2 | 0 | 2 | 1.61 |  |  | -0.00447 |  |  | 0 |  | 1 | CAPACITY
237085 | AD2-192 GEN | 23 | 201 | 57 | 0 | 600 | 0 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | NEW
293798 | W4-005 E | 0.69 | 222 | 74 | 0 | 305.37 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | W4-005
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1396 | 1120.79 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | GVG2
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1371 | 1100.72 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | GVG1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1088.67 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | RKG1
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1043.71 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | RKG2
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | X2-022
274663 | QUAD CITI;2U | 18 | 222 | 48 | 150 | 911.7 | 731.97 |  |  | -0.00448 |  |  | 0.01494 |  | 1 | CAPACITY
274662 | QUAD CITI;1U | 18 | 222 | 48 | 150 | 911.1 | 731.48 |  |  | -0.00448 |  |  | 0.01494 |  | 1 | CAPACITY
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00447 |  |  | 0.10478 |  | 1 | CAPACITY
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00447 |  |  | 0.10478 |  | 1 | CAPACITY
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | W2-048
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 144.51 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00448 |  |  | 0.04435 |  | 1 | CAPACITY | CORDOVA
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 77.88 |  |  | -0.00447 |  |  | 0.07484 |  | 1 | CAPACITY
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 52.91 |  |  | -0.00447 |  |  | 0.07484 |  | 1 | CAPACITY
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 51.78 |  |  | -0.00447 |  |  | 0.07484 |  | 1 | CAPACITY
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 51.38 |  |  | -0.00447 |  |  | 0.07484 |  | 1 | CAPACITY
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 36.61 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | W4-005
341584 | 2GRIFFIN | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1356 | 1088.67 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | MTG1
274656 | BYRON ;1U | 25 | 222 | 45 | 700 | 1168.5 | 938.14 |  |  | -0.00449 |  |  | 0.01494 |  | 1 | CAPACITY
274657 | BYRON ;2U | 25 | 222 | 45 | 700 | 1141.5 | 916.46 |  |  | -0.00449 |  |  | 0.01494 |  | 1 | CAPACITY
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 200 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | Q57
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | Z2-087
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | S28
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | S27
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 124 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | ENERGY | L05_CE22
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 409.46 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | P36 2
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | P36 1
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | AC1-089
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | O29 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | P26
293516 | O-009 E1 | 0.69 | 222 | 74 | 0 | 82.04 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | O09 1
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | P11 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | P11 2
294763 | P-046 E | 12 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | P46
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | O35
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 240.86 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | O29 2
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | NQ71
293518 | O-009 E3 | 0.57 | 222 | 74 | 0 | 45.89 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | O09 3
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 45.5 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | Z1-073
916211 | Z1-072 E | 0.6 | 222 | 74 | 0 | 44.8 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | Z1-072
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | O29 3
293517 | O-009 E2 | 0.6 | 222 | 74 | 0 | 41.67 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | O09 2
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 136.16 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | NELSON
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 135.12 |  |  | -0.00448 |  |  | 0.04435 |  | 1 | CAPACITY | NELSON
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 134.32 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 134.16 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 31.5 |  |  |  | -0.0045
919221 | AA1-146 | 345 | 222 | 58 | 0 | 157 | 126.05 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CLIF1
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CLIF3
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CLIF5
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CLIF4
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF2
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CLIF6
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 99.47 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | NELSON
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 98.59 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | NELSON
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | NQ72
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00449 |  |  | 0.05 |  | 1 | MTX | AA2-123
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 133.1 | 153 | 133.28 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 129.7 | 149.1 | 129.88 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 128.6 | 147.8 | 128.75 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 67.52 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CLIF2
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF6
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF1
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF3
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF4
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF5
926103 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 45.76 |  |  | -0.00449 |  |  | 0.05 |  | 1 | NEW | AC1-089
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 36.93 |  |  | -0.00448 |  |  | 0.07484 |  | 1 | CAPACITY
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Q57
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 28.74 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | S28
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 27.94 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | S27
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | L05_CE22
274889 | BRIGHTSTK;1U | 0.7 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Z2-087
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | O29 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 17.58 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | P26
293513 | O-009 C1 | 0.69 | 222 | 74 | 0 | 20.5 | 16.46 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | O09 1
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | P11 2
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | P11 1
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 15.58 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | P46
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | P36 2
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | P36 1
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Z1-073
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 9.64 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | O29 2
293515 | O-009 C3 | 0.57 | 222 | 74 | 0 | 11.5 | 9.23 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | O09 3
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 8.91 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | O29 3
293514 | O-009 C2 | 0.6 | 222 | 74 | 0 | 10.4 | 8.35 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | O09 2
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 10.3 | 8.27 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | O35
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 10 | 8.03 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Z1-072
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.6 | 7.71 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY
295108 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 5.7 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | NQ71
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY
342550 | 4BAVARIAN LF | 138 | 320 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY
295110 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 2.57 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | NQ72
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 949.78 |  |  | -0.0045 |  |  | 0.01494 |  | 1 | CAPACITY
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 926.5 |  |  | -0.0045 |  |  | 0.01494 |  | 1 | CAPACITY
274661 | LASCO STA;2U | 25 | 222 | 49 | 150 | 1135.9 | 911.97 |  |  | -0.0045 |  |  | 0.01494 |  | 1 | CAPACITY
274660 | LASCO STA;1U | 25 | 222 | 49 | 150 | 1131.2 | 908.19 |  |  | -0.0045 |  |  | 0.01494 |  | 1 | CAPACITY
274658 | DRESDEN ;2U | 18 | 222 | 48 | 150 | 902.5 | 724.58 |  |  | -0.0045 |  |  | 0.01494 |  | 1 | CAPACITY
274659 | DRESDEN ;3U | 18 | 222 | 48 | 150 | 895.5 | 718.96 |  |  | -0.00449 |  |  | 0.01494 |  | 1 | CAPACITY
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | O50
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Q01 3
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | O22 2
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | P10
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 589.3 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | ZIMM
293799 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | S36
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | S37
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 570.03 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | AA1-018
235587 | 01HARRN3 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
235586 | 01HARRN2 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
235585 | 01HARRN1 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Q01 4
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | O51 2
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | O51 1
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | N15
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 470.47 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | ZIMM
927091 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-204
927093 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | AC1-204
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 415.88 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 415.88 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
274687 | WILL CNTY;4U | 20 | 222 | 15 | 0 | 510 | 409.46 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY | WILL4
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Q01 21
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 81.6 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | O22 1
247903 | 05FR-22G E | 0.69 | 205 | 75 | 0 | 78.8 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Q01 22
247900 | 05FR-11G E | 0.6 | 205 | 75 | 0 | 78.3 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Q01 11
930062 | AB1-014 E | 138 | 212 | 75 | 0 | 77.5 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | AB1-014
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 522.66 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Q01 12
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 284.53 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK8
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 263.34 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK7
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.00449 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-169
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 294 | 236.04 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-079
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 225.6 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | AB1-169
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 219 | 175.82 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Z1-079
274708 | KENDALL ;3C | 18 | 222 | 58 | 140 | 184.3 | 147.97 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 3
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 146.36 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 2
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 146.36 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 138 | 182.3 | 146.36 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 4
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00449 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 2
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00449 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 1
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 132.47 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | ENERGY
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 99.72 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | KYG1
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | KYG2
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | KYG5
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | KYG3
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | KYG4
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 97.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Kendall 2
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 97.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Kendall 1
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 97.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Kendall 4
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 97.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Kendall 3
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 96.42 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 115.4 | 92.65 |  |  | -0.00449 |  |  | 0.04435 |  | 1 | CAPACITY | EQUISTAR MORRIS
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 75.6 | 104 | 83.5 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 72.7 | 101.6 | 81.57 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00449 |  |  | 0.05 |  | 1 | MTX | Z1-108
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.0045 |  |  | 0.05 |  | 1 | MTX | Z1-107
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 80.93 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 71.2 | 100.6 | 80.77 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 80.21 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
243415 | 05WWVSTA | 69 | 205 | 61 | 60 | 96 | 77.08 |  |  | -0.0045 |  |  | 0.07484 |  | 1 | CAPACITY
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 65.51 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 81.5 | 65.43 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.8 | 64.87 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 64.31 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 62.14 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
250166 | HLCRST AB114 | 138 | 212 | 75 | 0 | 76 | 61.02 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | AB1-014
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 58.77 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 58.45 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | KYG1
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | KYG3
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | KYG4
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | KYG5
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | KYG2
251953 | 08MADSN2 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251954 | 08MADSN3 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251952 | 08MADSN1 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251957 | 08MADSN6 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251956 | 08MADSN5 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251955 | 08MADSN4 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251959 | 08MADSN8 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251958 | 08MADSN7 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 56.84 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 55.4 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251828 | CLNTESP1 | 34.5 | 212 | 76 | 0 | 12 | 0 |  |  | -0.00449 |  |  | 0.05 |  | 1 | MTX | Z1-080
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 43.03 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00449 |  |  | 0.05 |  | 1 | MTX | Z1-106
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00449 |  |  | 0.05 |  | 1 | MTX | Z1-106
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 40.54 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | MIDDLETOWN COKE
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | O50
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00449 |  |  | 0.07484 |  | 1 | CAPACITY
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00449 |  |  | 0.07484 |  | 1 | CAPACITY
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00449 |  |  | 0.07484 |  | 1 | CAPACITY
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 28.18 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | O22 2
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | S37
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | S36
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -0.00449 |  |  | 0.05 |  | 1 | MTX | Z1-065
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 24.08 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 23.36 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Q01 4
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 20.3 | 27.6 | 22.16 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 22 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | N15
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 21.68 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 20.63 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Q01 11
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 20.07 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | O51 2
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | O51 1
274891 | OTTER CRK;1U | 0.69 | 222 | 74 | 0 | 19.5 | 15.66 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | AA1-018
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 14.77 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | O22 1
276173 | Z2-081 | 138 | 222 | 2 | 0 | 13.3 | 10.68 |  |  | -0.00449 |  |  | 0.12623 |  | 1 | CAPACITY
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Q01 21
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Q01 22
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 10.36 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Q01 12
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Q01 3
904211 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 9.71 |  |  | -0.00449 |  |  | 0.07484 |  | 1 | CAPACITY
904201 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 8.51 |  |  | -0.0045 |  |  | 0.07484 |  | 1 | CAPACITY
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 8.19 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | P10
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | MTX | Y3-099
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | MTX | Y3-100
276159 | W4-082 | 138 | 222 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.8 | 3.85 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY
930042 | AB1-006 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | AB1-006
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | U3-002 2
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | U2-090
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | V3-007
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 159.7 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | S06
253317 | AC1-085 B_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 B
253314 | AC1-085 A_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 A
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 443.18 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 437.96 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 80 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | T126 3
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 80 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | T127 4
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 80 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | T126 2
247943 | T-127 E | 0.74 | 205 | 74 | 0 | 80 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | T127 5
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 131.75 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 130.06 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
276592 | O-012 C | 138 | 222 | 64 | 0 | 20 | 0 |  |  | -0.0045 |  |  | 0.12623 |  | 1 | ENERGY
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | AC1-085 A
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | AC1-085 B
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEWENERGY | W3-044
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 37.49 |  |  | -0.00451 |  |  | 0.07484 |  | 1 | CAPACITY
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 42.68 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 42.6 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 42.51 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | X3-005
930041 | AB1-006 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | AB1-006
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | U2-090
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | V3-007
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 20.79 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | S06
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 16.22 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | T127 5
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 12.28 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | T126 3
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 12.2 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | T126 2
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 10.6 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | U3-002 1
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 10.28 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | U3-002 2
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 9.47 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | T127 4
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY | W3-044
247968 | Z2-115 E | 12 | 205 | 74 | 0 | 1.25 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Z2-115
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 2.73 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | X3-005
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 1 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Z2-115
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1402 |  |  |  | -0.0045
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1148 | 921.68 |  |  | -0.00452 |  |  | 0.01494 |  | 1 | CAPACITY
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEWENERGY | AC2-176
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEWENERGY | S71
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 268.96 |  |  | -0.00452 |  |  | 0.08446 |  | 1 | CAPACITY
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 201.52 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY | X2-052
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 193.49 |  |  | -0.00452 |  |  | 0.08446 |  | 1 | CAPACITY
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00452 |  |  | 0.04435 |  | 1 | CAPACITY | X2-052
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY | X2-052
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 0 |  |  | -0.00452 |  |  | 0 |  | 1 | NEWENERGY | AC2-067
902531 | W2-040 C | 69 | 209 | 75 | 0 | 20 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEW | W2-040
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 80.69 |  |  | -0.00451 |  |  | 0.08446 |  | 1 | CAPACITY
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 64.23 |  |  | -0.00452 |  |  | 0.10478 |  | 1 | CAPACITY
902532 | W2-040 E | 69 | 209 | 75 | 0 | 12.4 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEWENERGY | W2-040
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 48.09 |  |  | -0.00451 |  |  | 0.08446 |  | 1 | CAPACITY
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 47.93 |  |  | -0.00451 |  |  | 0.08446 |  | 1 | CAPACITY
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 46.65 |  |  | -0.00451 |  |  | 0.08446 |  | 1 | CAPACITY
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 46.41 |  |  | -0.00451 |  |  | 0.08446 |  | 1 | CAPACITY
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 21.28 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY | AC2-067
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 19.27 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY | S71
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 22.91 |  |  | -0.00451 |  |  | 0.08446 |  | 1 | CAPACITY
933594 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 13.57 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY | AC2-176
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00452 |  |  | 0.12623 |  | 1 | CAPACITY
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 8.03 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEWENERGY | V4-073
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.76 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY
904721 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY | V4-073
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 814.5 |  |  | -0.00453 |  |  | 0.01494 |  | 1 | CAPACITY
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | AA2-116
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00453 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-116
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 267.35 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | AA2-116
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 162.9 |  |  | -0.00452 |  |  | 0.08446 |  | 1 | CAPACITY
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00453 |  |  | 0 |  | 1 | NEWENERGY | AC1-166
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00453 |  |  | 0 |  | 1 | NEWENERGY | AC1-165
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00453 |  |  | 0 |  | 1 | NEWENERGY | AC1-069
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00453 |  |  | 0 |  | 1 | NEWENERGY | AC1-068
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | AC1-068
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | AC1-069
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | AC1-166
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | AC1-165
247969 | Z2-116 E | 138 | 205 | 76 | 0 | 1.3 | 0 |  |  | -0.00452 |  |  | 0 |  | 1 | NEWENERGY | Z2-116
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 4.82 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 3.13 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.8 | 2.25 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 2.09 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.5 | 1.2 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY | Z2-116
927184 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -0.00454 |  |  | 0.05 |  | 1 | MTX | AC1-212
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00453 |  |  | 0.08446 |  | 1 | CAPACITY
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00453 |  |  | 0.08446 |  | 1 | CAPACITY
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00453 |  |  | 0.08446 |  | 1 | CAPACITY
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 65.03 |  |  | -0.00453 |  |  | 0.08446 |  | 1 | CAPACITY
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 64.23 |  |  | -0.00453 |  |  | 0.08446 |  | 1 | CAPACITY
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 63.43 |  |  | -0.00453 |  |  | 0.08446 |  | 1 | CAPACITY
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00454 |  |  | 0.12623 |  | 1 | CAPACITY
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0 |  |  | -0.00453 |  |  | 0 |  | 1 | NEWENERGY | Z2-113
AC1-212 | BATTERY_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | -0.0045
247604 | X1-042 | 12 | 205 | 64 | 0 | 3 | 2.41 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 1.85 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | Z2-113
927183 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.53 |  |  | -0.00454 |  |  | 0 |  | 1 | CAPACITY | AC1-212
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 120.8 | 0 |  |  | -0.00455 |  |  | 0 |  | 1 | NEWENERGY | R49
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 0 |  |  | -0.00454 |  |  | 0 |  | 1 | NEWENERGY | T131
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 0 |  |  | -0.00454 |  |  | 0 |  | 1 | NEWENERGY | AC1-173
247530 | 05COVRT3 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00454 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 3
247528 | 05COVRT1 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00454 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 1
247529 | 05COVRT2 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00454 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 2
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00455 |  |  | 0.08446 |  | 1 | CAPACITY
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00455 |  |  | 0.08446 |  | 1 | CAPACITY
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00455 |  |  | 0.08446 |  | 1 | CAPACITY
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00455 |  |  | 0.08446 |  | 1 | CAPACITY
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 120.19 |  |  | -0.00455 |  |  | 0.08446 |  | 1 | CAPACITY
247531 | 05COVRT4 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00454 |  |  | 0 |  | 1 | CAPACITY | Covert 1
247533 | 05COVRT6 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00454 |  |  | 0 |  | 1 | CAPACITY | Covert 3
247532 | 05COVRT5 | 16.5 | 205 | 58 | 90 | 131.2 | 105.33 |  |  | -0.00454 |  |  | 0 |  | 1 | CAPACITY | Covert 2
932312 | AC2-045 E | 69 | 205 | 75 | 0 | 6.2 | 0 |  |  | -0.00454 |  |  | 0 |  | 1 | NEWENERGY | AC2-045
247521 | T131 | 0.69 | 205 | 74 | 22.4 | 30 | 24.08 |  |  | -0.00454 |  |  | 0 |  | 1 | CAPACITY | T131
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 18.39 |  |  | -0.00455 |  |  | 0 |  | 1 | CAPACITY | R49
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00455 |  |  | 0.07484 |  | 1 | CAPACITY
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00455 |  |  | 0.07484 |  | 1 | CAPACITY
932311 | AC2-045 C | 69 | 205 | 75 | 0 | 3.8 | 0 |  |  | -0.00454 |  |  | 0 |  | 1 | NEW | AC2-045
926865 | AC1-173 C | 0.65 | 205 | 75 | 0 | 9.9 | 7.95 |  |  | -0.00454 |  |  | 0 |  | 1 | CAPACITY | AC1-173
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 94.4 | 0 |  |  | -0.00456 |  |  | 0 |  | 1 | NEWENERGY | R60 3
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00456 |  |  | 0 |  | 1 | NEWENERGY | R60 2
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00456 |  |  | 0 |  | 1 | NEWENERGY | R60 1
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00455 |  |  | 0 |  | 1 | NEWENERGY | V1-011
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 13.25 |  |  | -0.00456 |  |  | 0 |  | 1 | CAPACITY | R60 3
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00456 |  |  | 0 |  | 1 | CAPACITY | R60 2
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00456 |  |  | 0 |  | 1 | CAPACITY | R60 1
247607 | V1-011 C | 34.5 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00455 |  |  | 0 |  | 1 | CAPACITY | V1-011
294740 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -0.00455 |  |  | 0 |  | 1 | ENERGY
903052 | W2-094 E | 115 | 227 | 75 | 0 | 1.9 | 0 |  |  | -0.00456 |  |  | 0 |  | 1 | NEWENERGY | W2-094
205911 | 27W2-094 | 115 | 227 | 75 | 0 | 1.1 | 0 |  |  | -0.00456 |  |  | 0 |  | 1 | NEWENERGY | W2-094
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00457 |  |  | 0 |  | 1 | NEWENERGY | U2-072
247919 | U2-041 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00457 |  |  | 0 |  | 1 | NEWENERGY | U2-041
247506 | U2-041 C | 345 | 205 | 74 | 0 | 39 | 0 |  |  | -0.00457 |  |  | 0 |  | 1 | CAPACITY | U2-041
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00457 |  |  | 0 |  | 1 | NEWENERGY | V3-028
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 31.31 |  |  | -0.00457 |  |  | 0 |  | 1 | CAPACITY | U2-072
247549 | V3-028 C | 345 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00457 |  |  | 0 |  | 1 | CAPACITY | V3-028
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00456 |  |  | 0 |  | 1 | MTX
208876 | WLAN | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00457 |  |  | 0 |  | 1 | CAPACITY
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00458 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-067
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00458 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-044
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00458 |  |  | 0 |  | 1 | CAPACITY | AB2-067
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 292.88 |  |  | -0.00458 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00458 |  |  | 0.04435 |  | 1 | CAPACITY | WATERFORD
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00458 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00458 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00458 |  |  | 0 |  | 1 | NEWENERGY | W4-073
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.00458 |  |  | 0 |  | 1 | CAPACITY
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 238.45 |  |  | -0.00459 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00459 |  |  | 0.04435 |  | 1 | CAPACITY | WASHINGTON
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00459 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00459 |  |  | 0 |  | 1 | CAPACITY
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 618.28 |  |  | -0.00459 |  |  | 0.10478 |  | 1 | CAPACITY
893022 | V2-006 E | 138 | 205 | 74 | 0 | 130.5 | 0 |  |  | -0.00459 |  |  | 0 |  | 1 | NEWENERGY | V2-006
893021 | V2-006 C | 138 | 205 | 74 | 0 | 19.5 | 0 |  |  | -0.00459 |  |  | 0 |  | 1 | NEWENERGY | V2-006
208769 | SISO | 12.5 | 229 | 2 | 0 | 2.48 | 0 |  |  | -0.0046 |  |  | 0 |  | 1 | ENERGY
245413 | 05S FULTHA | 69 | 205 | 65 | 0 | 0.85 | 0 |  |  | -0.00459 |  |  | 0 |  | 1 | ENERGY
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 318.8 | 255.95 |  |  | -0.00461 |  |  | 0 |  | 1 | CAPACITY | RONCO
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 225.4 | 180.96 |  |  | -0.0046 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 0 |  |  | -0.0046 |  |  | 0 |  | 1 | NEWENERGY | U1-059
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00461 |  |  | 0 |  | 1 | CAPACITY | RONCO
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00461 |  |  | 0.04435 |  | 1 | CAPACITY | RONCO
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.0046 |  |  | 0.04435 |  | 1 | CAPACITY | DRESDEN
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.0046 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 0 |  |  | -0.0046 |  |  | 0 |  | 1 | NEWENERGY | W1-056
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 0 |  |  | -0.0046 |  |  | 0 |  | 1 | NEWENERGY | U1-059
930262 | AB1-065 E | 34.5 | 201 | 75 | 0 | 6.8 | 0 |  |  | -0.0046 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
235013 | 01AB1-065 C | 34.5 | 201 | 75 | 0 | 4.1 | 0 |  |  | -0.0046 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.93 |  |  | -0.0046 |  |  | 0 |  | 1 | CAPACITY | W1-056
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 533.66 |  |  | -0.00462 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-173
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.00461 |  |  | 0.08446 |  | 1 | CAPACITY
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.00461 |  |  | 0.08446 |  | 1 | CAPACITY
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.66 | 96.07 |  |  | -0.00461 |  |  | 0.08446 |  | 1 | CAPACITY
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 17.66 |  |  | -0.00461 |  |  | 0.08446 |  | 1 | CAPACITY
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 8.83 |  |  | -0.00461 |  |  | 0.10478 |  | 1 | CAPACITY
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 10.19 |  |  | -0.00464 |  |  | 0.10478 |  | 1 | CAPACITY
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00466 |  |  | 0.07484 |  | 1 | CAPACITY
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00466 |  |  | 0.07484 |  | 1 | CAPACITY
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 15.25 |  |  | -0.00466 |  |  | 0.07484 |  | 1 | CAPACITY
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 634.42 |  |  | -0.00467 |  |  | 0.10478 |  | 1 | CAPACITY
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00467 |  |  | 0 |  | 1 | NEWENERGY | U4-029
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00467 |  |  | 0 |  | 1 | NEWENERGY | U4-028
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00467 |  |  | 0.08446 |  | 1 | CAPACITY
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00467 |  |  | 0.10478 |  | 1 | CAPACITY
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00467 |  |  | 0.08446 |  | 1 | CAPACITY
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00467 |  |  | 0.10478 |  | 1 | CAPACITY
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 0 |  |  | -0.00467 |  |  | 0 |  | 1 | NEWENERGY
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00467 |  |  | 0 |  | 1 | NEW | U4-028
247552 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00467 |  |  | 0 |  | 1 | NEW | U4-029
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00467 |  |  | 0 |  | 1 | NEWENERGY | V4-010
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 261.89 |  |  | -0.00467 |  |  | 0 |  | 1 | CAPACITY | OREGON
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 248.73 |  |  | -0.00467 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00467 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00468 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-107
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00467 |  |  | 0 |  | 1 | CAPACITY | OREGON
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00467 |  |  | 0.04435 |  | 1 | CAPACITY | OREGON
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 109.19 |  |  | -0.00468 |  |  | 0.10478 |  | 1 | CAPACITY
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 0 |  |  | -0.00467 |  |  | 0 |  | 1 | NEW | V4-010
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00468 |  |  | 0.08446 |  | 1 | CAPACITY
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00468 |  |  | 0.08446 |  | 1 | CAPACITY
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 10.68 |  |  | -0.00468 |  |  | 0.10478 |  | 1 | CAPACITY
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 19.5 | 15.66 |  |  | -0.00469 |  |  | 0.08446 |  | 1 | CAPACITY
924440 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 389.39 |  |  | -0.0047 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-093
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 364.2 | 292.4 |  |  | -0.0047 |  |  | 0 |  | 1 | CAPACITY | FREMONT
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 170 | 136.49 |  |  | -0.0047 |  |  | 0.04435 |  | 1 | CAPACITY | FREMONT
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 166.4 | 133.6 |  |  | -0.0047 |  |  | 0 |  | 1 | CAPACITY | FREMONT
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 780.51 |  |  | -0.00471 |  |  | 0.01494 |  | 1 | CAPACITY
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00472 |  |  | 0.10478 |  | 1 | CAPACITY
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00472 |  |  | 0.10478 |  | 1 | CAPACITY
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 192.53 |  |  | -0.00472 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 160.57 |  |  | -0.00472 |  |  | 0.04435 |  | 1 | CAPACITY | LOWER MT BETHEL
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 160.57 |  |  | -0.00472 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 4.41 |  |  | -0.00473 |  |  | 0 |  | 1 | CAPACITY | N32
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | -0.00473 |  |  | 0 |  | 1 | NEW | AB1-069
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00473 |  |  | 0 |  | 1 | NEW | AB1-069
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00473 |  |  | 0.04435 |  | 1 | NEW | AB1-069
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 60 | 48.17 |  |  | -0.00474 |  |  | 0.08446 |  | 1 | CAPACITY
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 8.03 |  |  | -0.00473 |  |  | 0 |  | 1 | CAPACITY
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 7.95 |  |  | -0.00473 |  |  | 0 |  | 1 | CAPACITY
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 1.85 |  |  | -0.00477 |  |  | 0 |  | 1 | CAPACITY
936011 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 16.06 |  |  | -0.00478 |  |  | 0.10478 |  | 1 | CAPACITY
209030 | FRFA O01 | 12.5 | 229 | 2 | 0 | 3.2 | 0 |  |  | -0.0048 |  |  | 0 |  | 1 | NEW
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 11.24 |  |  | -0.00481 |  |  | 0.12623 |  | 1 | CAPACITY
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 0.4 | 0.32 |  |  | -0.0048 |  |  | 0 |  | 1 | CAPACITY | V3-051
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00482 |  |  | 0.10478 |  | 1 | CAPACITY
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 272 | 218.38 |  |  | -0.00483 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00483 |  |  | 0.04435 |  | 1 | CAPACITY | Y2-050
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00483 |  |  | 0 |  | 1 | CAPACITY | Y2-050
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 62.22 |  |  | -0.00483 |  |  | 0.08446 |  | 1 | CAPACITY
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00482 |  |  | 0.08446 |  | 1 | CAPACITY
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00483 |  |  | 0.08446 |  | 1 | CAPACITY
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 60.86 |  |  | -0.00483 |  |  | 0.08446 |  | 1 | CAPACITY
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 60.29 |  |  | -0.00483 |  |  | 0.08446 |  | 1 | CAPACITY
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 41.03 |  |  | -0.00482 |  |  | 0.12623 |  | 1 | CAPACITY
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 39.82 |  |  | -0.00482 |  |  | 0.12623 |  | 1 | CAPACITY
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 498.09 |  |  | -0.00483 |  |  | 0.10478 |  | 1 | CAPACITY
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00483 |  |  | 0.10478 |  | 1 | CAPACITY
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 503.47 |  |  | -0.00486 |  |  | 0.04435 |  | 1 | CAPACITY | AVON LAKE
237082 | AA2-121 | 345 | 201 | 58 | 0 | 830 | 666.37 |  |  | -0.00489 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-121
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 21 | 16.86 |  |  | -0.00489 |  |  | 0.12623 |  | 1 | CAPACITY
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0 |  |  | -0.0049 |  |  | 0 |  | 1 | NEWENERGY | W1-045
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.13 | 4.12 |  |  | -0.0049 |  |  | 0 |  | 1 | CAPACITY | W1-045
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 3.21 |  |  | -0.00489 |  |  | 0 |  | 1 | CAPACITY
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 81.57 |  |  | -0.00492 |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND
253970 | 15BI2 | 13.8 | 215 | 58 | 60 | 96.2 | 77.24 |  |  | -0.00492 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.7 | 39.1 |  |  | -0.00492 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0 |  |  | -0.00492 |  |  | 0 |  | 1 | NEWENERGY | AC2-168
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 14.53 |  |  | -0.00492 |  |  | 0.08446 |  | 1 | CAPACITY
933531 | AC2-168 C | 138 | 215 | 75 | 0 | 7.55 | 6.06 |  |  | -0.00492 |  |  | 0 |  | 1 | CAPACITY | AC2-168
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00492 |  |  | 0.10478 |  | 1 | CAPACITY
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00492 |  |  | 0.10478 |  | 1 | CAPACITY
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 455.62 |  |  | -0.00492 |  |  | 0.10478 |  | 1 | CAPACITY
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | AA1-123
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 233.87 |  |  | -0.00492 |  |  | 0.10478 |  | 1 | CAPACITY
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.00493 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-123
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00493 |  |  | 0.04435 |  | 1 | CAPACITY | Y3-103
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | Y3-103
253900 | 15BVRVL1 | 22 | 215 | 44 | 843.9 | 970 | 844.97 |  |  | -0.00493 |  |  | 0.01494 |  | 1 | CAPACITY
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 783.39 |  |  | -0.00493 |  |  | 0.01494 |  | 1 | CAPACITY
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 300.6 | 241.34 |  |  | -0.00494 |  |  | 0 |  | 1 | CAPACITY | Z2-028
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00494 |  |  | 0 |  | 1 | CAPACITY | Z2-028
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00494 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-028
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.5 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | -0.00494 |  |  | 0.10478 |  | 1 | ENERGY
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 24.6 | 19.75 |  |  | -0.00495 |  |  | 0.12623 |  | 1 | CAPACITY
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 0 |  |  | -0.00496 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 0 |  |  | -0.00496 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 329.17 |  |  | -0.00498 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00498 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00498 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-044
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 3.21 |  |  | -0.00498 |  |  | 0 |  | 1 | CAPACITY
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 16.46 |  |  | -0.005 |  |  | 0.12623 |  | 1 | CAPACITY
239023 | 02NWCAG4 | 14.4 | 202 | 58 | 20 | 92 | 73.86 |  |  | -0.00504 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 2.01 |  |  | -0.00504 |  |  | 0 |  | 1 | CAPACITY
239024 | 02NWCAG5 | 16.5 | 202 | 58 | 23 | 141 | 113.2 |  |  | -0.00504 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 1.37 |  |  | -0.00505 |  |  | 0 |  | 1 | CAPACITY | K20
239022 | 02NWCAG3 | 14.4 | 202 | 58 | 20 | 92.3 | 74.11 |  |  | -0.00505 |  |  | 0.04435 |  | 1 | CAPACITY | NEW CASTLE
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 19.6 | 15.74 |  |  | -0.00507 |  |  | 0.08446 |  | 1 | CAPACITY
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 261.73 |  |  | -0.00509 |  |  | 0 |  | 1 | CAPACITY | T-174
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00509 |  |  | 0 |  | 1 | CAPACITY | T-174
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00509 |  |  | 0.04435 |  | 1 | CAPACITY | T-174
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1086.27 |  |  | -0.0051 |  |  | 0.01494 |  | 1 | CAPACITY
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.82 |  |  | -0.00512 |  |  | 0 |  | 1 | CAPACITY
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 39.5 | 31.71 |  |  | -0.00513 |  |  | 0.08446 |  | 1 | CAPACITY
920571 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 411.86 |  |  | -0.00514 |  |  | 0.04435 |  | 1 | NEW | AA2-161
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 3.05 |  |  | -0.00517 |  |  | 0 |  | 1 | CAPACITY
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00519 |  |  | 0.08446 |  | 1 | CAPACITY
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 64.31 |  |  | -0.0052 |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 52.35 |  |  | -0.0052 |  |  | 0.04435 |  | 1 | CAPACITY | CAMDEN COGEN TECH
925391 | AC1-010 C | 26.4 | 231 | 75 | 0 | 6 | 0 |  |  | -0.0052 |  |  | 0 |  | 1 | NEW | AC1-010
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 19.27 |  |  | -0.0052 |  |  | 0.10478 |  | 1 | CAPACITY
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -0.0052 |  |  | 0 |  | 1 | NEWENERGY | AC1-010
219765 | PARADISE E | 26.4 | 231 | 75 | 0 | 3.2 | 0 |  |  | -0.0052 |  |  | 0 |  | 1 | NEWENERGY | U4-036
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.3 | 9.07 |  |  | -0.0052 |  |  | 0.10478 |  | 1 | CAPACITY
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | -0.0052 |  |  | 0 |  | 1 | MTX | X2-013
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.0052 |  |  | 0 |  | 1 | CAPACITY | U4-036
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 28.1 |  |  | -0.00523 |  |  | 0.10478 |  | 1 | CAPACITY
913142 | Y1-033 E OP1 | 115 | 226 | 74 | 0 | 34.02 | 0 |  |  | -0.00525 |  |  | 0 |  | 1 | NEWENERGY | Y1-033
207402 | 28AA2-082 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.00524 |  |  | 0.05 |  | 1 | MTX | AA2-082
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 4.01 |  |  | -0.00525 |  |  | 0 |  | 1 | CAPACITY | Y1-033
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 38.7 | 31.07 |  |  | -0.00532 |  |  | 0.08446 |  | 1 | CAPACITY
204555 | 27QUEEN ST | 115 | 227 | 74 | 0 | 5 | 0 |  |  | -0.00536 |  |  | 0 |  | 1 | NEWENERGY
204638 | 27CAT TRAC | 13.2 | 227 | 58 | 0 | 32.3 | 25.93 |  |  | -0.00539 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
204706 | 27CAT TRC2 | 13.2 | 227 | 58 | 0 | 13.9 | 11.16 |  |  | -0.00539 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 140 | 182.2 | 146.28 |  |  | -0.00541 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 118.7 | 175.2 | 140.66 |  |  | -0.00541 |  |  | 0.04435 |  | 1 | CAPACITY | AE SPRINGDALE
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 118.7 | 172.2 | 138.25 |  |  | -0.00541 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.00541 |  |  | 0.08446 |  | 1 | CAPACITY
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.00541 |  |  | 0.08446 |  | 1 | CAPACITY
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 353.26 |  |  | -0.00543 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00543 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-076
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00543 |  |  | 0 |  | 1 | CAPACITY | AA1-076
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 24.08 |  |  | -0.00545 |  |  | 0.10478 |  | 1 | CAPACITY
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 5.54 |  |  | -0.00551 |  |  | 0 |  | 1 | CAPACITY
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.33 |  |  | -0.00552 |  |  | 0 |  | 1 | CAPACITY
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00552 |  |  | 0 |  | 1 | NEWENERGY | K23
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 0 |  |  | -0.00552 |  |  | 0 |  | 1 | NEWENERGY | L13
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 0 |  |  | -0.00552 |  |  | 0 |  | 1 | NEWENERGY | O48
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | -0.00552 |  |  | 0.05 |  | 1 | MTX
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | -0.00552 |  |  | 0.05 |  | 1 | MTX
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 0 |  |  | -0.00552 |  |  | 0 |  | 1 | NEWENERGY | R40
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 5.06 |  |  | -0.00552 |  |  | 0 |  | 1 | CAPACITY | O48
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 4.74 |  |  | -0.00552 |  |  | 0 |  | 1 | CAPACITY | L13
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 5.1 | 4.09 |  |  | -0.00552 |  |  | 0 |  | 1 | CAPACITY | K23
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 6.1 |  |  | -0.00561 |  |  | 0 |  | 1 | CAPACITY
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0 |  |  | -0.00569 |  |  | 0 |  | 1 | NEWENERGY | AD2-070
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00569 |  |  | 0 |  | 1 | CAPACITY | AD2-070
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.02 |  |  | -0.0057 |  |  | 0 |  | 1 | CAPACITY
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 5.46 |  |  | -0.00572 |  |  | 0 |  | 1 | CAPACITY
208920 | WLPK | 12.5 | 229 | 60 | 0 | 40.9 | 32.84 |  |  | -0.00574 |  |  | 0.07484 |  | 1 | CAPACITY
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.45 |  |  | -0.00574 |  |  | 0 |  | 1 | CAPACITY
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.72 |  |  | -0.00574 |  |  | 0 |  | 1 | CAPACITY | K22
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 68.24 |  |  | -0.00576 |  |  | 0.10478 |  | 1 | CAPACITY
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 42.95 |  |  | -0.00575 |  |  | 0.08446 |  | 1 | CAPACITY
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 42.95 |  |  | -0.00575 |  |  | 0.08446 |  | 1 | CAPACITY
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00575 |  |  | 0.08446 |  | 1 | CAPACITY
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00575 |  |  | 0.08446 |  | 1 | CAPACITY
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00575 |  |  | 0.08446 |  | 1 | CAPACITY
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00576 |  |  | 0 |  | 1 | CAPACITY
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 16.55 |  |  | -0.00576 |  |  | 0.07484 |  | 1 | CAPACITY
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 682.91 |  |  | -0.00577 |  |  | 0.10478 |  | 1 | CAPACITY | Cone1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 682.43 |  |  | -0.00577 |  |  | 0.10478 |  | 1 | CAPACITY | Cone2
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 400 | 321.14 |  |  | -0.00578 |  |  | 0.04435 |  | 1 | CAPACITY | AD2-114
235622 | 01SBEND4 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00578 |  |  | 0.08446 |  | 1 | CAPACITY
235620 | 01SBEND2 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00578 |  |  | 0.08446 |  | 1 | CAPACITY
235621 | 01SBEND3 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00578 |  |  | 0.08446 |  | 1 | CAPACITY
235619 | 01SBEND1 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00578 |  |  | 0.08446 |  | 1 | CAPACITY
903644 | W3-099 E OP1 | 230 | 226 | 74 | 0 | 87 | 0 |  |  | -0.00578 |  |  | 0 |  | 1 | NEWENERGY | W3-099
201144 | W3-099 C OP1 | 230 | 226 | 74 | 0 | 13 | 0 |  |  | -0.00578 |  |  | 0 |  | 1 | NEW | W3-099
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 853.3 | 685.08 |  |  | -0.0058 |  |  | 0.10478 |  | 1 | CAPACITY | Keys1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 853.1 | 684.92 |  |  | -0.0058 |  |  | 0.10478 |  | 1 | CAPACITY | Keys2
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00583 |  |  | 0 |  | 1 | NEWENERGY | P60
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 6.82 |  |  | -0.00583 |  |  | 0 |  | 1 | CAPACITY | P60
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 24.24 |  |  | -0.00584 |  |  | 0.07484 |  | 1 | CAPACITY
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00589 |  |  | 0 |  | 1 | CAPACITY
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 23.2 | 0 |  |  | -0.0059 |  |  | 0 |  | 1 | NEWENERGY | K13
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.0059 |  |  | 0.12623 |  | 1 | CAPACITY
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 2.57 |  |  | -0.0059 |  |  | 0 |  | 1 | CAPACITY | K13
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 10.44 |  |  | -0.00592 |  |  | 0.12623 |  | 1 | CAPACITY
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00595 |  |  | 0.12623 |  | 1 | CAPACITY
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 422.06 |  |  | -0.00598 |  |  | 0.10478 |  | 1 | CAPACITY
200805 | 26COLVER13 | 13.2 | 226 | 12 | 77 | 110 | 88.31 |  |  | -0.00598 |  |  | 0.10478 |  | 1 | CAPACITY
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 60 | 0 |  |  | -0.006 |  |  | 0 |  | 1 | NEWENERGY | R32
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 52 | 0 |  |  | -0.006 |  |  | 0 |  | 1 | NEWENERGY | O18
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 10.19 |  |  | -0.006 |  |  | 0 |  | 1 | CAPACITY | R32
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 6.5 |  |  | -0.006 |  |  | 0 |  | 1 | CAPACITY | O18
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 497.77 |  |  | -0.00601 |  |  | 0.10478 |  | 1 | CAPACITY
200809 | 26SITHE | 138 | 226 | 15 | 0 | 36 | 28.9 |  |  | -0.00601 |  |  | 0.10478 |  | 1 | CAPACITY
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 521.86 |  |  | -0.00608 |  |  | 0.10478 |  | 1 | CAPACITY
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 492.95 |  |  | -0.00608 |  |  | 0.10478 |  | 1 | CAPACITY
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 0 |  |  | -0.00607 |  |  | 0 |  | 1 | NEWENERGY | V3-030
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 4.25 |  |  | -0.00607 |  |  | 0 |  | 1 | CAPACITY | V3-030
208946 | MACR CT | 12.5 | 229 | 55 | 0 | 72 | 57.81 |  |  | -0.00612 |  |  | 0.08446 |  | 1 | CAPACITY
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 57 | 45.76 |  |  | -0.00613 |  |  | 0.08446 |  | 1 | CAPACITY
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 48 | 0 |  |  | -0.00615 |  |  | 0 |  | 1 | NEWENERGY | Q53
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 5.14 |  |  | -0.00615 |  |  | 0 |  | 1 | CAPACITY | Q53
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00623 |  |  | 0 |  | 1 | NEWENERGY | W4-097
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00623 |  |  | 0 |  | 1 | CAPACITY | W4-097
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 0 |  |  | -0.00626 |  |  | 0 |  | 1 | NEWENERGY | N39
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00626 |  |  | 0 |  | 1 | NEWENERGY | O38
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00626 |  |  | 0 |  | 1 | CAPACITY | N39
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.4 | 7.55 |  |  | -0.00626 |  |  | 0 |  | 1 | CAPACITY | O38
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 187.87 |  |  | -0.00628 |  |  | 0.0316 |  | 1 | CAPACITY
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 177.43 |  |  | -0.00628 |  |  | 0.0316 |  | 1 | CAPACITY
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 26.13 |  |  | -0.00628 |  |  | 0.07484 |  | 1 | CAPACITY
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 601.34 |  |  | -0.0064 |  |  | 0.10478 |  | 1 | CAPACITY
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 293.93 |  |  | -0.0064 |  |  | 0.10478 |  | 1 | CAPACITY | Bris2
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 248.4 |  |  | -0.0064 |  |  | 0.10478 |  | 1 | CAPACITY | Bris1
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 40 | 0 |  |  | -0.00639 |  |  | 0 |  | 1 | NEWENERGY | Q36
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 6.66 |  |  | -0.00639 |  |  | 0 |  | 1 | CAPACITY | Q36
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 33.96 |  |  | -0.00654 |  |  | 0.10478 |  | 1 | CAPACITY
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | -0.00655 |  |  | 0 |  | 1 | ENERGY
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4.82 |  |  | -0.00659 |  |  | 0 |  | 1 | CAPACITY
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 16.86 |  |  | -0.00665 |  |  | 0.07484 |  | 1 | CAPACITY
200722 | 26SHAWVL 2 | 18 | 226 | 12 | 62 | 124.7 | 100.12 |  |  | -0.00667 |  |  | 0.10478 |  | 1 | CAPACITY
200715 | 26SHAWVL 1 | 18 | 226 | 12 | 62 | 122 | 97.95 |  |  | -0.00667 |  |  | 0.10478 |  | 1 | CAPACITY
200665 | 26SHAWVL 3 | 22 | 226 | 12 | 120 | 174.2 | 139.86 |  |  | -0.00675 |  |  | 0.10478 |  | 1 | CAPACITY
200666 | 26SHAWVL 4 | 22 | 226 | 12 | 120 | 171 | 137.29 |  |  | -0.00675 |  |  | 0.10478 |  | 1 | CAPACITY
922932 | AB1-082 OP | 46 | 201 | 55 | 0 | 19.9 | 0 |  |  | -0.0068 |  |  | 0.08446 |  | 1 | NEW
208947 | WSHO CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00682 |  |  | 0.08446 |  | 1 | CAPACITY
236828 | 01GRAYMONT | 46 | 201 | 2 | 0 | 4 | 0 |  |  | -0.0069 |  |  | 0 |  | 1 | ENERGY
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | -0.00691 |  |  | 0 |  | 1 | MTX | AC1-025
208348 | EELI | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00695 |  |  | 0 |  | 1 | CAPACITY
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 24.08 |  |  | -0.00701 |  |  | 0.10478 |  | 1 | CAPACITY
208942 | HARR CT | 12.5 | 229 | 55 | 0 | 42 | 33.72 |  |  | -0.00702 |  |  | 0.08446 |  | 1 | CAPACITY
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 9.64 |  |  | -0.00702 |  |  | 0.12623 |  | 1 | CAPACITY
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 8.19 |  |  | -0.00702 |  |  | 0.10478 |  | 1 | CAPACITY
210022 | LING 2 | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00701 |  |  | 0 |  | 1 | CAPACITY
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 0 |  |  | -0.00705 |  |  | 0 |  | 1 | NEWENERGY | Z1-069
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00705 |  |  | 0 |  | 1 | CAPACITY | Z1-069
219647 | COOPERSOLA E | 13.2 | 231 | 75 | 0 | 0.4 | 0 |  |  | -0.00711 |  |  | 0 |  | 1 | NEWENERGY | AB1-063
210319 | WCAR 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00732 |  |  | 0 |  | 1 | CAPACITY
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | -0.00748 |  |  | 0.12623 |  | 1 | ENERGY
208697 | PRIN B34 | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00748 |  |  | 0 |  | 1 | CAPACITY
208885 | WNHO | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00748 |  |  | 0 |  | 1 | CAPACITY
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | -0.00759 |  |  | 0 |  | 1 | ENERGY
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.61 |  |  | -0.00759 |  |  | 0 |  | 1 | CAPACITY
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 19 | 15.25 |  |  | -0.00763 |  |  | 0.08446 |  | 1 | CAPACITY
211065 | PSPA IPP | 13.8 | 229 | 75 | 0 | 18.4 | 6.74 |  |  | -0.00765 |  |  | 0 |  | 1 | NEWENERGY | U4-014
204663 | 27AES GEN2 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00767 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204664 | 27AES GEN3 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00767 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204662 | 27AES GEN1 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00767 |  |  | 0.04435 |  | 1 | CAPACITY | IRONWOOD
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 130.87 |  |  | -0.00768 |  |  | 0.04435 |  | 1 | CAPACITY | GRAYS FERRY
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 0 |  |  | -0.00772 |  |  | 0 |  | 1 | NEWENERGY | P47
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.8 | 12.69 |  |  | -0.00772 |  |  | 0 |  | 1 | CAPACITY | P47
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 0 |  |  | -0.0078 |  |  | 0 |  | 1 | NEWENERGY | K02
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 16.86 |  |  | -0.00788 |  |  | 0.12623 |  | 1 | CAPACITY
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 17.18 |  |  | -0.0079 |  |  | 0.12623 |  | 1 | CAPACITY
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 16.86 |  |  | -0.0079 |  |  | 0.12623 |  | 1 | CAPACITY
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.00799 |  |  | 0.08446 |  | 1 | CAPACITY
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 0 |  |  | -0.00813 |  |  | 0 |  | 1 | NEWENERGY | AA2-017
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 0 |  |  | -0.00813 |  |  | 0 |  | 1 | NEW | AA2-017
920341 | AA2-132 | 34.5 | 226 | 55 | 0 | 19.9 | 0 |  |  | -0.00815 |  |  | 0.08446 |  | 1 | NEW
919201 | AA1-144 OP | 230 | 226 | 58 | 0 | 163 | 130.87 |  |  | -0.00832 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-144
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00836 |  |  | 0 |  | 1 | CAPACITY | X1-109
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00836 |  |  | 0.04435 |  | 1 | CAPACITY | X1-109
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.04 |  |  | -0.00837 |  |  | 0 |  | 1 | CAPACITY
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | -0.00839 |  |  | 0 |  | 1 | ENERGY
208580 | MGTN 2 | 12.5 | 229 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00839 |  |  | 0 |  | 1 | CAPACITY
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.0084 |  |  | 0.08446 |  | 1 | CAPACITY
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.0084 |  |  | 0.08446 |  | 1 | CAPACITY
203932 | AA2-133 GEN | 13.8 | 226 | 55 | 0 | 19.89 | 0 |  |  | -0.00865 |  |  | 0.08446 |  | 1 | NEW
219913 | PENNSAU2 E | 26.4 | 231 | 75 | 0 | 8.2 | 0 |  |  | -0.0088 |  |  | 0 |  | 1 | NEWENERGY | AD2-042
219915 | CINNAMSOL E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.0088 |  |  | 0 |  | 1 | NEWENERGY | AD2-027
219912 | PENNSAU2 C | 26.4 | 231 | 75 | 0 | 5 | 0 |  |  | -0.0088 |  |  | 0 |  | 1 | NEW | AD2-042
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.63 | 3.72 |  |  | -0.0088 |  |  | 0 |  | 1 | CAPACITY
219914 | CINNAMSOL C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.0088 |  |  | 0 |  | 1 | CAPACITY | AD2-027
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.4 |  |  | -0.0088 |  |  | 0 |  | 1 | CAPACITY
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 389.39 |  |  | -0.00884 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-115
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 30.1 | 24.17 |  |  | -0.00898 |  |  | 0.08446 |  | 1 | CAPACITY
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 0 |  |  | -0.00899 |  |  | 0 |  | 1 | NEWENERGY | P28
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | -0.00899 |  |  | 0.10478 |  | 1 | NEW
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 47.37 |  |  | -0.00899 |  |  | 0.10478 |  | 1 | CAPACITY
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00899 |  |  | 0 |  | 1 | CAPACITY | P28
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 17.18 |  |  | -0.00899 |  |  | 0.12623 |  | 1 | CAPACITY
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 4.82 |  |  | -0.00902 |  |  | 0 |  | 1 | CAPACITY
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 6 | 4.82 |  |  | -0.00906 |  |  | 0 |  | 1 | CAPACITY
209007 | NOEN IPP | 13.8 | 229 | 12 | 80 | 111.4 | 89.44 |  |  | -0.00919 |  |  | 0.10478 |  | 1 | CAPACITY
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 152.86 |  |  | -0.00931 |  |  | 0.04435 |  | 1 | CAPACITY | ONTELAUNEE
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 152.86 |  |  | -0.00931 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 139.94 |  |  | -0.00931 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 64.23 |  |  | -0.00939 |  |  | 0.10478 |  | 1 | CAPACITY
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 69.05 |  |  | -0.00952 |  |  | 0.10478 |  | 1 | CAPACITY
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 65.83 |  |  | -0.00952 |  |  | 0.10478 |  | 1 | CAPACITY
208941 | FISH CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00952 |  |  | 0.08446 |  | 1 | CAPACITY
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.4 | 9.15 |  |  | -0.00952 |  |  | 0 |  | 1 | CAPACITY | Q27
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.81 |  |  | -0.00952 |  |  | 0 |  | 1 | CAPACITY | N14
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 18.3 | 14.69 |  |  | -0.00954 |  |  | 0.12623 |  | 1 | CAPACITY
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00964 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
211375 | BEAC | 69 | 229 | 2 | 0 | 20 | 0 |  |  | -0.00969 |  |  | 0.10478 |  | 1 | ENERGY
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 47.77 |  |  | -0.00969 |  |  | 0.08446 |  | 1 | CAPACITY
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 47.21 |  |  | -0.00969 |  |  | 0.08446 |  | 1 | CAPACITY
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 23.76 |  |  | -0.00969 |  |  | 0.08446 |  | 1 | CAPACITY
208943 | HARW CT | 12.5 | 229 | 55 | 0 | 27.2 | 21.84 |  |  | -0.00969 |  |  | 0.08446 |  | 1 | CAPACITY
211591 | HARW | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00969 |  |  | 0 |  | 1 | CAPACITY
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 34.28 |  |  | -0.00977 |  |  | 0.10478 |  | 1 | CAPACITY
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 26.09 |  |  | -0.00977 |  |  | 0.10478 |  | 1 | CAPACITY
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 6.42 |  |  | -0.00977 |  |  | 0 |  | 1 | CAPACITY
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 4.9 |  |  | -0.00977 |  |  | 0 |  | 1 | CAPACITY
208940 | ALLE CT | 12.5 | 229 | 55 | 0 | 56 | 44.96 |  |  | -0.00984 |  |  | 0.08446 |  | 1 | CAPACITY
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 608.97 |  |  | -0.01019 |  |  | 0.10478 |  | 1 | CAPACITY
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 608.49 |  |  | -0.01019 |  |  | 0.10478 |  | 1 | CAPACITY
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.01021 |  |  | 0.04435 |  | 1 | CAPACITY | MOXIE PATRIOT
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.01021 |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT
208948 | WILL CT | 12.5 | 229 | 55 | 0 | 27.4 | 22 |  |  | -0.01023 |  |  | 0.08446 |  | 1 | CAPACITY
212005 | ALWD | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.01023 |  |  | 0 |  | 1 | CAPACITY
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 11.24 |  |  | -0.01024 |  |  | 0.08446 |  | 1 | CAPACITY
212435 | SMIL | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.01025 |  |  | 0 |  | 1 | CAPACITY
209018 | SUNBIPCT | 12.5 | 229 | 55 | 0 | 36 | 28.9 |  |  | -0.01029 |  |  | 0.08446 |  | 1 | CAPACITY
212345 | PENS | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.01029 |  |  | 0 |  | 1 | CAPACITY
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.01036 |  |  | 0.05 |  | 1 | MTX | AB1-182
208944 | JENK CT | 12.5 | 229 | 55 | 0 | 28 | 22.48 |  |  | -0.01036 |  |  | 0.08446 |  | 1 | CAPACITY
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.65 |  |  | -0.01036 |  |  | 0 |  | 1 | CAPACITY | L18
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1091.76 |  |  | -0.01037 |  |  | 0.01494 |  | 1 | CAPACITY
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 35.57 |  |  | -0.01041 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 23.44 |  |  | -0.01041 |  |  | 0.04435 |  | 1 | CAPACITY | HUNLOCK
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 39.1 |  |  | -0.01041 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 38.86 |  |  | -0.01041 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 317.93 |  |  | -0.01049 |  |  | 0 |  | 1 | CAPACITY | Hummel
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 194.29 |  |  | -0.01049 |  |  | 0 |  | 1 | CAPACITY | Hummel
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.01049 |  |  | 0 |  | 1 | CAPACITY | Hummel
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.01049 |  |  | 0.04435 |  | 1 | CAPACITY | Hummel
211374 | AVOC | 12.5 | 229 | 2 | 0 | 17.4 | 13.97 |  |  | -0.01048 |  |  | 0 |  | 1 | CAPACITY
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 0 |  |  | -0.01055 |  |  | 0 |  | 1 | NEWENERGY | AC1-071
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 7.02 |  |  | -0.01055 |  |  | 0 |  | 1 | NEW | AC1-071
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.01062 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G2
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.01062 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G1
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.01062 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G3
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | -0.01062 |  |  | 0.05 |  | 1 | MTX | Z2-107
209009 | PEIP 2 | 13.8 | 229 | 56 | 0 | 43.7 | 35.08 |  |  | -0.01062 |  |  | 0.08446 |  | 1 | CAPACITY
209010 | PEIP 1 | 13.8 | 229 | 29 | 0 | 26.7 | 21.43 |  |  | -0.01062 |  |  | 0.10478 |  | 1 | CAPACITY
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 7.23 |  |  | -0.01062 |  |  | 0 |  | 1 | CAPACITY | K21
209003 | KSTN IPP | 13.8 | 229 | 65 | 0 | 4.9 | 3.93 |  |  | -0.01062 |  |  | 0 |  | 1 | CAPACITY
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.01203 |  |  | 0.08446 |  | 1 | CAPACITY
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.01203 |  |  | 0.08446 |  | 1 | CAPACITY
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 22.48 |  |  | -0.01207 |  |  | 0.10478 |  | 1 | CAPACITY
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.01227 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-046
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.01227 |  |  | 0 |  | 1 | CAPACITY | Z2-046
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.01228 |  |  | 0 |  | 1 | NEWENERGY | V4-001
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.61 |  |  | -0.01228 |  |  | 0 |  | 1 | CAPACITY | V4-001
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1090.36 |  |  | -0.01229 |  |  | 0.01494 |  | 1 | CAPACITY
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.01249 |  |  | 0.08446 |  | 1 | CAPACITY
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.01249 |  |  | 0.08446 |  | 1 | CAPACITY
214030 | WAYNEJCT | 13.8 | 230 | 2 | 0 | 8.8 | 7.07 |  |  | -0.01264 |  |  | 0 |  | 1 | CAPACITY
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 900.89 |  |  | -0.01425 |  |  | 0.01494 |  | 1 | CAPACITY
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 898.96 |  |  | -0.01483 |  |  | 0.01494 |  | 1 | CAPACITY
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.01518 |  |  | 0.08446 |  | 1 | CAPACITY
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.01573 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.01573 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.01573 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.01573 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.01573 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200044 | BETH CT1 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.01573 |  |  | 0.04435 |  | 1 | CAPACITY | BETH1234
200048 | BETH CT5 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.01573 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
219650 | TRENT_COLLEG | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.01694 |  |  | 0 |  | 1 | CAPACITY
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0 |  |  | -0.01694 |  |  | 0 |  | 1 | NEWENERGY | W4-058
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.22 |  |  | -0.01694 |  |  | 0 |  | 1 | CAPACITY | W4-058
213798 | MERCK 3 | 13.8 | 230 | 2 | 13 | 35 | 28.1 |  |  | -0.01714 |  |  | 0 |  | 1 | CAPACITY
213797 | MERCK 2 | 13.8 | 230 | 2 | 4 | 25 | 20.07 |  |  | -0.01714 |  |  | 0 |  | 1 | CAPACITY
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 3.29 |  |  | -0.01714 |  |  | 0 |  | 1 | CAPACITY
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.01898 |  |  | 0 |  | 1 | NEWENERGY | AC1-030
925561 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.01898 |  |  | 0 |  | 1 | CAPACITY | AC1-030
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0 |  |  | -0.01909 |  |  | 0 |  | 1 | NEWENERGY | X1-071
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.28 |  |  | -0.01909 |  |  | 0 |  | 1 | CAPACITY | X1-071
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.0209 |  |  | 0 |  | 1 | NEWENERGY | W2-016
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.0209 |  |  | 0 |  | 1 | CAPACITY | W2-016
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0 |  |  | -0.03025 |  |  | 0 |  | 1 | NEWENERGY | AC1-017
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0 |  |  | -0.03025 |  |  | 0 |  | 1 | NEWENERGY | X1-070
925451 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 1.12 |  |  | -0.03025 |  |  | 0 |  | 1 | CAPACITY | AC1-017
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.96 |  |  | -0.03025 |  |  | 0 |  | 1 | CAPACITY | X1-070
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  |  |  | -0.0336
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 38.54 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 260.3 | 208.98 |  |  | -0.03836 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | -0.03836 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | -0.03836 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill B
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 205.69 |  |  | -0.03839 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | -0.03839 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | -0.03839 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill A
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 0 |  |  | -0.03845 |  |  | 0 |  | 1 | NEWENERGY | W3-080
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.03845 |  |  | 0.08446 |  | 1 | CAPACITY
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.03845 |  |  | 0.08446 |  | 1 | CAPACITY
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.03845 |  |  | 0.08446 |  | 1 | CAPACITY
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.03845 |  |  | 0.08446 |  | 1 | CAPACITY
925442 | AC1-016 E | 26.4 | 231 | 75 | 0 | 5.45 | 0 |  |  | -0.03845 |  |  | 0 |  | 1 | NEWENERGY | AC1-016
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | -0.03845 |  |  | 0 |  | 1 | NEWENERGY | W4-103
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | -0.03845 |  |  | 0 |  | 1 | NEWENERGY | W2-102
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -0.03845 |  |  | 0 |  | 1 | NEWENERGY | Y3-026
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.03845 |  |  | 0 |  | 1 | CAPACITY | Y3-026
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 2.97 |  |  | -0.03845 |  |  | 0 |  | 1 | CAPACITY | W3-080
925441 | AC1-016 C | 26.4 | 231 | 75 | 0 | 3.34 | 2.68 |  |  | -0.03845 |  |  | 0 |  | 1 | CAPACITY | AC1-016
219685 | NATIONAL_GYP | 26 | 231 | 2 | 0 | 2.8 | 2.25 |  |  | -0.03845 |  |  | 0 |  | 1 | CAPACITY
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.03845 |  |  | 0 |  | 1 | CAPACITY | W4-103
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.03845 |  |  | 0 |  | 1 | CAPACITY | W2-102
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0 |  |  | -0.04128 |  |  | 0 |  | 1 | NEWENERGY | W2-080
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.04128 |  |  | 0 |  | 1 | CAPACITY | W2-080
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0 |  |  | -0.04651 |  |  | 0 |  | 1 | NEWENERGY | W2-050
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0 |  |  | -0.04858 |  |  | 0 |  | 1 | NEWENERGY | V3-070
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.04858 |  |  | 0 |  | 1 | CAPACITY | V3-070
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0 |  |  | -0.0491 |  |  | 0 |  | 1 | NEWENERGY | X2-075
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 1.83 |  |  | -0.0491 |  |  | 0 |  | 1 | CAPACITY | X2-075
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | W3-029
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | W3-003
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEW | AE1-156
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | AE1-156
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | W1-132
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | V4-070
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | W2-061
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | V4-069
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.05064 |  |  | 0 |  | 1 | CAPACITY | W3-029
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.05064 |  |  | 0 |  | 1 | CAPACITY | V4-069
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.05064 |  |  | 0 |  | 1 | CAPACITY | V4-070
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.05064 |  |  | 0 |  | 1 | CAPACITY | W2-061
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.05507 |  |  | 0.08446 |  | 1 | CAPACITY
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 1.04 |  |  | -0.05507 |  |  | 0 |  | 1 | CAPACITY | T20
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0 |  |  | -0.05648 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0 |  |  | -0.05648 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
932032 | AC2-009 E | 13.2 | 231 | 75 | -0.5 | 0.49 | 0 |  |  | -0.05648 |  |  | 0 |  | 1 | NEWENERGY | AC2-009
932031 | AC2-009 C | 13.2 | 231 | 75 | -0.1 | 0.1 | 0 |  |  | -0.05648 |  |  | 0 |  | 1 | NEW | AC2-009
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.05648 |  |  | 0 |  | 1 | CAPACITY | AA2-058
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0 |  |  | -0.07377 |  |  | 0 |  | 1 | NEWENERGY | W2-036
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.07377 |  |  | 0 |  | 1 | CAPACITY | W2-036
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0 |  |  | -0.10269 |  |  | 0 |  | 1 | NEWENERGY | W1-121 Z
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.10269 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.10269 |  |  | 0 |  | 1 | CAPACITY | W1-121 Z
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.46 |  |  | -0.10269 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 35.24 |  |  | -0.11211 |  |  | 0.10478 |  | 1 | CAPACITY
218780 | PRINCENTON_U | 26 | 231 | 2 | 0 | 31.56 | 25.34 |  |  | -0.13126 |  |  | 0 |  | 1 | CAPACITY
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0 |  |  | -0.13126 |  |  | 0 |  | 1 | NEWENERGY | Z1-096
219622 | TRENT_BIOGAS | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.13126 |  |  | 0 |  | 1 | CAPACITY
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 2.39 |  |  | -0.13126 |  |  | 0 |  | 1 | CAPACITY | Z1-096
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0 |  |  | -0.2107 |  |  | 0 |  | 1 | NEWENERGY | V2-009 3
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0 |  |  | -0.2107 |  |  | 0 |  | 1 | NEWENERGY | V2-009 4
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 1.92 |  |  | -0.2107 |  |  | 0 |  | 1 | CAPACITY | V2-009 3
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 1.15 |  |  | -0.2107 |  |  | 0 |  | 1 | CAPACITY | V2-009 4
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0 |  |  | -0.23582 |  |  | 0 |  | 1 | NEWENERGY | W3-124
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0 |  |  | -0.23582 |  |  | 0 |  | 1 | NEWENERGY | V2-009 1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.87 |  |  | -0.23582 |  |  | 0 |  | 1 | CAPACITY | W3-124
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.23582 |  |  | 0 |  | 1 | CAPACITY | V2-009 1
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.23653 |  |  | 0 |  | 1 | NEWENERGY | V3-024
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0 |  |  | -0.23653 |  |  | 0 |  | 1 | NEWENERGY | V2-009 2
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0 |  |  | -0.23653 |  |  | 0 |  | 1 | NEWENERGY | X2-088
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.23653 |  |  | 0 |  | 1 | CAPACITY | V3-024
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 1.52 |  |  | -0.23653 |  |  | 0 |  | 1 | CAPACITY | V2-009 2
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.72 |  |  | -0.23653 |  |  | 0 |  | 1 | CAPACITY | X2-088
218455 | CINNBAY_CGEN | 26.4 | 231 | 75 | 0 | 9 | 0 |  |  | -0.28851 |  |  | 0 |  | 1 | NEWENERGY
924132 | NEWROADSO E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.28851 |  |  | 0 |  | 1 | NEWENERGY | AB2-057
217199 | EDGEBORO_2E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.28851 |  |  | 0 |  | 1 | NEWENERGY | V3-059
217198 | EDGEBORO_1E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.28851 |  |  | 0 |  | 1 | NEWENERGY | V3-058
924131 | NEWROADSO C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.28851 |  |  | 0 |  | 1 | CAPACITY | AB2-057
218781 | BRIS_MYERS | 26 | 231 | 2 | 0 | 3 | 2.41 |  |  | -0.28851 |  |  | 0 |  | 1 | CAPACITY

## FG 28-GD-S2-S2
****** PJM Generator Deliverability Detailed Report ****** POWER-GEM [TARA Ver 2001.1a PJMGD RC3 64-bit - Wed Aug 18 16:43:31 2021]
FG Index | 2 | Monitored Facility:218306 DEANS 230 218304 BRUNSWCK 230 1 / Contingency:PJM500_P2-3_BRBG5_3-4[Breaker]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
887 | 126.01 | 123.35 | AC | 411.75 | 573.09 | 78.87 | 52.3 | 1.71 | 1117.72 | 1094.1 | 0.001481 | 0 | 12797.9 | 0 | 10196.7 | 0.05308 | 3872.23 | 2601.19 | 1271.04 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited?
900003 | DEANS E | 500 | 231 | 74 | 0 | 1779.4 | 0 | 1779.4 | FiftyFifty | 0.22876 | 407.0508 |  | 0 | 1 | 1 | NEWENERGY | OSW_DEANS
200006 | DEANS C | 500 | 231 | 74 | 0 | 762.6 | 762.6 | 762.6 | FiftyFifty | 0.22876 |  |  | 0 | 1 | 1 | CAPACITY | OSW_DEANS
900004 | SMITHBRG E | 500 | 228 | 74 | 0 | 820.4 | 0 | 820.4 | FiftyFifty | 0.2022 | 165.8839 |  | 0 | 1 | 1 | NEWENERGY | OSW_SMITHB
200017 | SMITHBRG C | 500 | 228 | 74 | 0 | 327.6 | 327.6 | 327.6 | FiftyFifty | 0.2022 |  |  | 0 | 1 | 1 | CAPACITY | OSW_SMITHB
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0 | 1.24 | FiftyFifty | 0.11045 | 0.137 |  | 0 | 1 | 1 | NEWENERGY | X2-089
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.61 | 0.76 | FiftyFifty | 0.11045 | 0.0165 |  | 0 | 1 | 1 | CAPACITY | X2-089
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0 | 1.58 | Adder/OL | 0.08617 | 0.1362 | 0.0023 | 0 |  | 1 | NEWENERGY | W1-032
901032 | W1-024E OP1 | 34.5 | 228 | 0 | 0 | 0 | 0 | 2.13 | Adder/OL | 0.07566 | 0.1608 | 0.0031 | 0 |  | 1 | NEW
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  | 645 | LTF/CMTX | 0.07305 | 47.117 | 0.9551
207419 | AB2-139 E | 34.5 | 228 | 76 | 0 | 0.21 | 0 | 0.18 | Adder/OL | 0.06867 | 0.0123 | 0.0003 | 0 |  | 1 | ENERGY | AB2-139
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0 | 4.76 | Adder/OL | 0.06683 | 0.3181 | 0.007 | 0 |  | 1 | NEWENERGY | W2-078
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0 | 4.25 | Adder/OL | 0.06683 | 0.284 | 0.0063 | 0 |  | 1 | NEWENERGY | W1-113
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0 | 6.97 | Adder/OL | 0.06653 | 0.4637 | 0.0103 | 0 |  | 1 | NEWENERGY | AC1-207
900005 | 28LARRABEE E | 230 | 228 | 74 | 0 | 840 | 0 | 714 | Adder/OL | 0.0658 | 46.9825 | 1.0572 | 0 |  | 1 | NEWENERGY | OSW_LARRAB
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 | 2.63 | Adder/OL | 0.06309 | 0.1663 | 0.0039 | 0 |  | 1 | NEWENERGY | Y2-051
919662 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 | 7 | Adder/NFTIR/OL | 0.06166 | 0.4316 | 0.0104 | 0.05 |  | 1 | MTX NFTIR | AA2-048
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 | 3.74 | Adder/OL | 0.06166 | 0.2306 | 0.0055 | 0 |  | 1 | NEWENERGY | W3-079
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0 | 8.96 | Adder/OL | 0.05983 | 0.536 | 0.0133 | 0 |  | 1 | NEWENERGY | X1-037
923293 | AB1-138 E | 34.5 | 228 | 75 | 0 | 6 | 0 | 5.1 | Adder/OL | 0.05928 | 0.3024 | 0.0076 | 0 |  | 1 | NEWENERGY | AB1-138
900002 | 28OYSTER E | 230 | 228 | 74 | 0 | 586.7 | 0 | 498.7 | Adder/OL | 0.05791 | 28.8811 | 0.7384 | 0 |  | 1 | NEWENERGY | OSW_OYSCK
923463 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0 | 4.25 | Adder/OL | 0.05602 | 0.2381 | 0.0063 | 0 |  | 1 | NEWENERGY | AB1-163
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0 | 1.7 | Adder/OL | 0.05508 | 0.0936 | 0.0025 | 0 |  | 1 | NEWENERGY | X4-031
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.6 |  | 173.6 | CLTF | 0.00447 | 0.7752 | -0.2571
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 0.00447 | 0.2486 | -0.0824
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 0.00447 | 0.2439 | -0.0808
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  | 258.3 | CLTF | 0.00443 | 1.1437 | -0.3825
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  | 210 | CLTF | 0.00435 | 0.9131 | -0.311
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 0.00428 | 0.2143 | -0.0741
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 0.00429 | 0.2131 | -0.0736
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  | 35 | CLTF | 0.00414 | 0.1448 | -0.0518
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  | 57.8 | CLTF | 0.00406 | 0.2347 | -0.0855
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  | 239.8 | LTF/CMTX | 0.00377 | 0.9044 | 0.355
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  | 55.3 | CLTF | 0.0026 | 0.1441 | -0.0819
219123 | BCRR_COGEN | 13.8 | 231 | 64 | 0 | 6 | 0 | 5.1 | Adder/OL | -0.0723 | -0.3688 | 0.0076 | 0.12623 |  | 1 | CAPACITY
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | 0.08617 |  |  | 0 |  | 1 | CAPACITY | W1-032
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 5.3 |  |  | 0.07594 |  |  | 0 |  | 1 | CAPACITY
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | 0.07566 |  |  | 0 |  | 1 | CAPACITY | W1-024
218344 | TOSCO_G6 | 18 | 231 | 2 | 90 | 180 | 144.51 |  |  | 0.07279 |  |  | 0.04435 |  | 1 | CAPACITY | TOSCO
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 309 | 248.08 |  |  | 0.07215 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | 0.07215 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | 0.07215 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | 0.07215 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC2
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | 0.07215 |  |  | 0.08446 |  | 1 | CAPACITY
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | 0.07215 |  |  | 0.08446 |  | 1 | CAPACITY
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | 0.06683 |  |  | 0 |  | 1 | CAPACITY | W2-078
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 2.25 |  |  | 0.06683 |  |  | 0 |  | 1 | CAPACITY | W1-113
207420 | AC1-207 C | 34.5 | 228 | 75 | 0 | 4.9 | 3.93 |  |  | 0.06653 |  |  | 0 |  | 1 | CAPACITY | AC1-207
206294 | 28LARRABEE C | 230 | 228 | 74 | 0 | 360 | 360 |  |  | 0.0658 |  |  | 0 |  | 1 | CAPACITY | OSW_LARRAB
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | 0.06399 |  |  | 0.08446 |  | 1 | CAPACITY
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | 0.06399 |  |  | 0.08446 |  | 1 | CAPACITY
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 61.6 | 88.4 | 70.97 |  |  | 0.06399 |  |  | 0.04435 |  | 1 | CAPACITY | LAKEWOOD
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 61.2 | 88.3 | 70.89 |  |  | 0.06399 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 76.92 |  |  | 0.06399 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | 0.06309 |  |  | 0 |  | 1 | CAPACITY | Y2-051
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | 0.06166 |  |  | 0 |  | 1 | CAPACITY | W3-079
206201 | 28JERSVGEN | 34.5 | 228 | 2 | 0 | 2 | 1.61 |  |  | 0.06129 |  |  | 0 |  | 1 | CAPACITY
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 3.37 |  |  | 0.05983 |  |  | 0 |  | 1 | CAPACITY | X1-037
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 309 | 248.08 |  |  | 0.0597 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 180 | 144.51 |  |  | 0.0597 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | 0.0597 |  |  | 0.08446 |  | 1 | CAPACITY
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | 0.0597 |  |  | 0.08446 |  | 1 | CAPACITY
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 30.03 |  |  | 0.0597 |  |  | 0.10478 |  | 1 | CAPACITY
206280 | 28LAKEHURS | 34.5 | 228 | 64 | 0 | 13.8 | 11.08 |  |  | 0.05928 |  |  | 0.08446 |  | 1 | CAPACITY
923292 | AB1-138 C | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | 0.05928 |  |  | 0 |  | 1 | CAPACITY | AB1-138
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 27.3 |  |  | 0.05791 |  |  | 0.12623 |  | 1 | CAPACITY
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 27 |  |  | 0.05791 |  |  | 0.12623 |  | 1 | CAPACITY
206302 | 28OYSTER C | 230 | 228 | 74 | 0 | 229.3 | 229.3 |  |  | 0.05791 |  |  | 0 |  | 1 | CAPACITY | OSW_OYSCK
217825 | UMD_NJ | 26 | 231 | 2 | 0 | 10.5 | 8.43 |  |  | 0.05737 |  |  | 0 |  | 1 | CAPACITY
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | 0.05118 |  |  | 0 |  | 1 | NEWENERGY | X1-085
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | 0.05118 |  |  | 0 |  | 1 | CAPACITY | X1-085
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0 |  |  | 0.05017 |  |  | 0 |  | 1 | NEWENERGY | W1-101
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.43 |  |  | 0.05017 |  |  | 0 |  | 1 | CAPACITY | W1-101
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | 0.05015 |  |  | 0 |  | 1 | NEWENERGY | W1-124
921743 | AA2-049 E | 34.5 | 228 | 76 | -3 | 3 | 0 |  |  | 0.05015 |  |  | 0 |  | 1 | MTX | AA2-049
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | 0.05015 |  |  | 0 |  | 1 | CAPACITY | W1-124
920732 | AA2-184 E | 34.5 | 228 | 75 | 0 | 20 | 0 |  |  | 0.04947 |  |  | 0 |  | 1 | NEWENERGY | AA2-184
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | 0.04781 |  |  | 0.05 |  | 1 | MTX
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | 0.04598 |  |  | 0 |  | 1 | NEWENERGY | W1-120
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | 0.04598 |  |  | 0 |  | 1 | NEWENERGY | W1-119
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | 0.04598 |  |  | 0 |  | 1 | CAPACITY | W1-120
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | 0.04598 |  |  | 0 |  | 1 | CAPACITY | W1-119
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0 |  |  | 0.04592 |  |  | 0 |  | 1 | NEWENERGY | Z2-102
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 3.97 |  |  | 0.04592 |  |  | 0 |  | 1 | CAPACITY | Z2-102
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | 0.04397 |  |  | 0 |  | 1 | NEWENERGY | W2-082
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | 0.04397 |  |  | 0 |  | 1 | CAPACITY | W2-082
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0 |  |  | 0.04386 |  |  | 0 |  | 1 | NEWENERGY | V3-067
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0 |  |  | 0.04386 |  |  | 0 |  | 1 | NEWENERGY | V3-068
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.23 |  |  | 0.04386 |  |  | 0 |  | 1 | CAPACITY | V3-067
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | 0.04386 |  |  | 0 |  | 1 | CAPACITY | V3-068
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | 0.04373 |  |  | 0 |  | 1 | NEWENERGY | X4-015
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0 |  |  | 0.04373 |  |  | 0 |  | 1 | NEWENERGY | X2-087
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | 0.04373 |  |  | 0 |  | 1 | CAPACITY | X4-015
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 0.04373 |  |  | 0 |  | 1 | CAPACITY | X2-087
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | 0.04355 |  |  | 0 |  | 1 | NEWENERGY | W4-025
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | 0.04355 |  |  | 0 |  | 1 | NEWENERGY | W1-129
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | 0.04355 |  |  | 0 |  | 1 | CAPACITY | W4-025
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | 0.04355 |  |  | 0 |  | 1 | CAPACITY | W1-129
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0 |  |  | 0.0432 |  |  | 0 |  | 1 | NEWENERGY | W2-019
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 1.85 |  |  | 0.0432 |  |  | 0 |  | 1 | CAPACITY | W2-019
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | 0.04257 |  |  | 0.10478 |  | 1 | CAPACITY
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | 0.04255 |  |  | 0.10478 |  | 1 | CAPACITY
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 998.11 |  |  | 0.04136 |  |  | 0.01494 |  | 1 | CAPACITY
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 992.1 |  |  | 0.04136 |  |  | 0.01494 |  | 1 | CAPACITY
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | 0.04136 |  |  | 0.08446 |  | 1 | ENERGY
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1026.43 |  |  | 0.04114 |  |  | 0.01494 |  | 1 | CAPACITY
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0 |  |  | 0.04005 |  |  | 0 |  | 1 | NEWENERGY | AB1-001
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.7 |  |  | 0.04005 |  |  | 0 |  | 1 | CAPACITY | AB1-001
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0 |  |  | 0.03952 |  |  | 0 |  | 1 | NEWENERGY | W1-112
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | 0.03952 |  |  | 0 |  | 1 | CAPACITY | W1-112
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 169.24 |  |  | 0.03818 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | 0.03818 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | 0.03818 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | 0.03818 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | 0.03818 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
900000 | CARDIFF E | 230 | 234 | 74 | 0 | 1235 | 0 |  |  | 0.03785 |  |  | 0 |  | 1 | NEWENERGY | OSW_CARDIF
227900 | CARDIFF C | 230 | 234 | 74 | 0 | 275 | 275 |  |  | 0.03785 |  |  | 0 |  | 1 | CAPACITY | OSW_CARDIF
227928 | V4-067E | 12.9 | 234 | 75 | 1.6 | 1.6 | 0 |  |  | 0.03684 |  |  | 0 |  | 1 | NEWENERGY | V4-067
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0 |  |  | 0.03684 |  |  | 0 |  | 1 | NEWENERGY | AB2-122
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.79 |  |  | 0.03684 |  |  | 0 |  | 1 | CAPACITY | V4-067
924701 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.56 |  |  | 0.03684 |  |  | 0 |  | 1 | CAPACITY | AB2-122
227801 | ONTC&DCT | 13.8 | 234 | 56 | 38.6 | 38.6 | 0 |  |  | 0.03615 |  |  | 0.08446 |  | 1 | NEW
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 |  |  | 0.03615 |  |  | 0.12623 |  | 1 | ENERGY
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0 |  |  | 0.03614 |  |  | 0 |  | 1 | NEWENERGY | W2-030
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 |  |  | 0.03615 |  |  | 0.10478 |  | 1 | ENERGY
228014 | PVILLEG | 0.48 | 234 | 65 | 1.7 | 3 | 1.04 |  |  | 0.03615 |  |  | 0 |  | 1 | CAPACITY
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 2.93 |  |  | 0.03614 |  |  | 0 |  | 1 | CAPACITY | W2-030
900001 | BLE E | 138 | 234 | 74 | 0 | 310.6 | 0 |  |  | 0.03502 |  |  | 0 |  | 1 | NEWENERGY | OSW_BLE
228110 | BLE C | 138 | 234 | 74 | 0 | 121.4 | 121.4 |  |  | 0.03502 |  |  | 0 |  | 1 | CAPACITY | OSW_BLE
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.61 |  |  | 0.03437 |  |  | 0 |  | 1 | CAPACITY
934302 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0 |  |  | 0.03399 |  |  | 0 |  | 1 | NEWENERGY | AD1-054
218092 | PRIMEENG_G | 26.4 | 231 | 29 | 10 | 70.3 | 56.44 |  |  | 0.03379 |  |  | 0.10478 |  | 1 | CAPACITY
228203 | P06 | 13.8 | 234 | 57 | 80.6 | 92.7 | 80.75 |  |  | 0.03368 |  |  | 0.08446 |  | 1 | CAPACITY
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 202.48 |  |  | 0.03358 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 143.63 |  |  | 0.03358 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 143.63 |  |  | 0.03358 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN2
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0 |  |  | 0.03358 |  |  | 0 |  | 1 | NEWENERGY | X1-072
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 0.03358 |  |  | 0 |  | 1 | CAPACITY | X1-072
217850 | MONTCLAIR_U | 26 | 231 | 2 | 0 | 10.6 | 8.51 |  |  | 0.03342 |  |  | 0 |  | 1 | CAPACITY
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.74 |  |  | 0.03342 |  |  | 0 |  | 1 | CAPACITY
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0 |  |  | 0.03329 |  |  | 0 |  | 1 | NEWENERGY | W4-059
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.18 |  |  | 0.03329 |  |  | 0 |  | 1 | CAPACITY | W4-059
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 207.94 |  |  | 0.03305 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | 0.03305 |  |  | 0.04435 |  | 1 | CAPACITY | DELANCY STREET
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | 0.03305 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 70.56 |  |  | 0.03305 |  |  | 0.08446 |  | 1 | CAPACITY
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | 0.03305 |  |  | 0.04435 |  | 1 | CAPACITY | NEWARK BAY
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | 0.03305 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 27.46 |  |  | 0.03305 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.85 |  |  | 0.03305 |  |  | 0 |  | 1 | CAPACITY
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0 |  |  | 0.03305 |  |  | 0 |  | 1 | NEWENERGY | V3-065
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.17 |  |  | 0.03305 |  |  | 0 |  | 1 | CAPACITY | V3-065
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 74.48 |  |  | 0.03294 |  |  | 0.08446 |  | 1 | CAPACITY
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 76.11 |  |  | 0.03273 |  |  | 0.08446 |  | 1 | CAPACITY
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | 0.03273 |  |  | 0.08446 |  | 1 | CAPACITY
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | 0.03273 |  |  | 0.08446 |  | 1 | CAPACITY
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | 0.03273 |  |  | 0.08446 |  | 1 | CAPACITY
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | 0.03273 |  |  | 0.08446 |  | 1 | CAPACITY
217831 | PB_NUTCLIF | 26 | 231 | 2 | 0 | 10.7 | 8.59 |  |  | 0.03266 |  |  | 0 |  | 1 | CAPACITY
228712 | V2-041E | 13.2 | 234 | 75 | 2.5 | 2.48 | 0 |  |  | 0.03233 |  |  | 0 |  | 1 | NEWENERGY | V2-041
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 1.22 |  |  | 0.03233 |  |  | 0 |  | 1 | CAPACITY | V2-041
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0 |  |  | 0.03214 |  |  | 0 |  | 1 | NEWENERGY | V3-066
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | 0.03214 |  |  | 0 |  | 1 | CAPACITY | V3-066
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 73.09 |  |  | 0.03175 |  |  | 0.08446 |  | 1 | CAPACITY
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | 0.03155 |  |  | 0 |  | 1 | NEWENERGY | V2-025
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 48.35 |  |  | 0.02985 |  |  | 0.08446 |  | 1 | CAPACITY
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.5 | 18.87 |  |  | 0.0295 |  |  | 0.08446 |  | 1 | CAPACITY
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 49.65 |  |  | 0.02928 |  |  | 0.10478 |  | 1 | CAPACITY
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | 0.02889 |  |  | 0 |  | 1 | NEWENERGY | W4-060
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | 0.02889 |  |  | 0 |  | 1 | CAPACITY | W4-060
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0 |  |  | 0.02728 |  |  | 0 |  | 1 | NEWENERGY | W1-130
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 2.57 |  |  | 0.02728 |  |  | 0 |  | 1 | CAPACITY | W1-130
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0 |  |  | 0.02675 |  |  | 0 |  | 1 | NEWENERGY | V4-054
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 3.05 |  |  | 0.02675 |  |  | 0 |  | 1 | CAPACITY | V4-054
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 4.8 | 0 |  |  | 0.02672 |  |  | 0 |  | 1 | NEW
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.6 | 39.8 | 34.67 |  |  | 0.0267 |  |  | 0.08446 |  | 1 | CAPACITY
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 32.75 |  |  | 0.0267 |  |  | 0.08446 |  | 1 | CAPACITY
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | 0.02666 |  |  | 0.04435 |  | 1 | NEW | AA2-069
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 154.95 |  |  | 0.02666 |  |  | 0.04435 |  | 1 | CAPACITY | Garrison
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 93.29 |  |  | 0.02666 |  |  | 0 |  | 1 | CAPACITY | Garrison
232901 | NORTHST | 69 | 235 | 56 | 5 | 46 | 36.93 |  |  | 0.02666 |  |  | 0.08446 |  | 1 | CAPACITY
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 12.2 |  |  | 0.02666 |  |  | 0.10478 |  | 1 | CAPACITY
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 39.34 |  |  | 0.02626 |  |  | 0.08446 |  | 1 | CAPACITY
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 38.54 |  |  | 0.02626 |  |  | 0.08446 |  | 1 | CAPACITY
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 152.54 |  |  | 0.02531 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.02531 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC2
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.02531 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.02531 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 0 |  |  | 0.02496 |  |  | 0 |  | 1 | NEWENERGY | AB1-056
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 330.7 |  |  | 0.02496 |  |  | 0.10478 |  | 1 | CAPACITY
930201 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 51.71 |  |  | 0.02496 |  |  | 0 |  | 1 | CAPACITY | AB1-056
232920 | IR10 | 13.2 | 235 | 55 | 12.6 | 16.1 | 12.93 |  |  | 0.02491 |  |  | 0.08446 |  | 1 | CAPACITY
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0 |  |  | 0.02489 |  |  | 0 |  | 1 | NEWENERGY | AB1-137
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 3.37 |  |  | 0.02489 |  |  | 0 |  | 1 | CAPACITY | AB1-137
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | 0.02483 |  |  | 0.10478 |  | 1 | ENERGY
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.02483 |  |  | 0 |  | 1 | NEWENERGY | Z2-076
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.02483 |  |  | 0 |  | 1 | NEWENERGY | Z2-077
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.02483 |  |  | 0 |  | 1 | CAPACITY | Z2-077
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.02483 |  |  | 0 |  | 1 | CAPACITY | Z2-076
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.41 |  |  | 0.0248 |  |  | 0 |  | 1 | CAPACITY
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.05 |  |  | 0.0247 |  |  | 0 |  | 1 | CAPACITY
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.02465 |  |  | 0.08446 |  | 1 | CAPACITY
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.02465 |  |  | 0.08446 |  | 1 | CAPACITY
917082 | CHERRYDALE E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0245 |  |  | 0 |  | 1 | NEWENERGY | Z2-012
232915 | OH NUG4 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 39.03 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 38.94 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 38.68 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 26.05 |  |  | 0.0245 |  |  | 0.08446 |  | 1 | CAPACITY
232905 | BAYVIEW1 | 24.9 | 235 | 65 | 0 | 12.5 | 10.04 |  |  | 0.0245 |  |  | 0.12623 |  | 1 | CAPACITY
917081 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.0245 |  |  | 0 |  | 1 | CAPACITY | Z2-012
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0245 |  |  | 0 |  | 1 | NEWENERGY | W1-004
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0245 |  |  | 0 |  | 1 | NEWENERGY | W1-003
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0245 |  |  | 0 |  | 1 | NEWENERGY | W1-006
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0245 |  |  | 0 |  | 1 | NEWENERGY | W1-005
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.0245 |  |  | 0 |  | 1 | CAPACITY | W1-006
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.0245 |  |  | 0 |  | 1 | CAPACITY | W1-004
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.0245 |  |  | 0 |  | 1 | CAPACITY | W1-005
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.0245 |  |  | 0 |  | 1 | CAPACITY | W1-003
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0 |  |  | 0.02443 |  |  | 0 |  | 1 | NEWENERGY | X1-032
293670 | O-025 C | 25 | 235 | 64 | 0 | 6 | 4.82 |  |  | 0.02443 |  |  | 0 |  | 1 | CAPACITY
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 0 |  |  | 0.02442 |  |  | 0 |  | 1 | NEWENERGY | AA1-102
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 45.76 |  |  | 0.02442 |  |  | 0 |  | 1 | CAPACITY | AA1-102
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 8.03 |  |  | 0.02442 |  |  | 0 |  | 1 | CAPACITY
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0 |  |  | 0.02434 |  |  | 0 |  | 1 | NEWENERGY | Y3-058
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 5.7 | 4.58 |  |  | 0.02434 |  |  | 0 |  | 1 | CAPACITY | Y3-058
228721 | V2-035E | 12.9 | 234 | 75 | 1.2 | 1.2 | 0 |  |  | 0.02415 |  |  | 0 |  | 1 | NEWENERGY | V2-035
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.61 |  |  | 0.02415 |  |  | 0 |  | 1 | CAPACITY | V2-035
232919 | VN10 | 13.2 | 235 | 55 | 12.4 | 14.3 | 12.46 |  |  | 0.02401 |  |  | 0 |  | 1 | CAPACITY
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 122.84 |  |  | 0.02393 |  |  | 0.10478 |  | 1 | CAPACITY
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0 |  |  | 0.02393 |  |  | 0 |  | 1 | NEWENERGY | Y1-080
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 1.03 |  |  | 0.02393 |  |  | 0 |  | 1 | CAPACITY | Y1-080
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.02365 |  |  | 0 |  | 1 | NEWENERGY | X3-008
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.02365 |  |  | 0 |  | 1 | CAPACITY | X3-008
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0 |  |  | 0.02284 |  |  | 0 |  | 1 | NEWENERGY | AB1-021
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | 0.02284 |  |  | 0 |  | 1 | CAPACITY | AB1-021
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 55.4 |  |  | 0.02274 |  |  | 0.12623 |  | 1 | CAPACITY
228343 | QUINTN#1 | 12.9 | 234 | 64 | 0 | 1.7 | 0 |  |  | 0.02269 |  |  | 0 |  | 1 | CAPACITY
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0 |  |  | 0.02219 |  |  | 0 |  | 1 | NEWENERGY | Y1-079
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.02219 |  |  | 0 |  | 1 | CAPACITY | Y1-079
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0 |  |  | 0.02184 |  |  | 0 |  | 1 | NEWENERGY | X3-066
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 2.28 | 1.83 |  |  | 0.02184 |  |  | 0 |  | 1 | CAPACITY | X3-066
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 57.24 |  |  | 0.02167 |  |  | 0.10478 |  | 1 | CAPACITY
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 45.76 |  |  | 0.02167 |  |  | 0.08446 |  | 1 | CAPACITY
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 44.16 |  |  | 0.02167 |  |  | 0.04435 |  | 1 | CAPACITY | DELAWARE CITY
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 14.29 |  |  | 0.02167 |  |  | 0.08446 |  | 1 | CAPACITY
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.02146 |  |  | 0 |  | 1 | NEWENERGY | AB1-142
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.02146 |  |  | 0 |  | 1 | NEWENERGY | AB1-141
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.02146 |  |  | 0 |  | 1 | CAPACITY | AB1-141
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.02146 |  |  | 0 |  | 1 | CAPACITY | AB1-142
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 19.11 |  |  | 0.02143 |  |  | 0.12623 |  | 1 | CAPACITY
228357 | V2-046E | 12.9 | 234 | 75 | 12.9 | 12.9 | 0 |  |  | 0.02074 |  |  | 0 |  | 1 | NEWENERGY | V2-046
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 6.26 |  |  | 0.02074 |  |  | 0 |  | 1 | CAPACITY | V2-046
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 192.69 |  |  | 0.02054 |  |  | 0.10478 |  | 1 | CAPACITY
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01924 |  |  | 0 |  | 1 | NEWENERGY | AB2-179
233931 | AB2-179 C | 0.38 | 235 | 75 | 0 | 38 | 30.51 |  |  | 0.01924 |  |  | 0 |  | 1 | CAPACITY | AB2-179
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.09 |  |  | 0.01666 |  |  | 0 |  | 1 | CAPACITY
925112 | AB2-168 E | 34.5 | 235 | 75 | 0 | 5.2 | 0 |  |  | 0.01574 |  |  | 0 |  | 1 | NEWENERGY | AB2-168
925111 | AB2-168 C | 34.5 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.01574 |  |  | 0 |  | 1 | CAPACITY | AB2-168
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 58.9 | 47.29 |  |  | 0.01454 |  |  | 0.04435 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 58.9 | 47.29 |  |  | 0.01454 |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 13.81 |  |  | 0.01439 |  |  | 0.08446 |  | 1 | CAPACITY
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 18.47 |  |  | 0.01424 |  |  | 0.08446 |  | 1 | CAPACITY
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 18.39 |  |  | 0.01424 |  |  | 0.08446 |  | 1 | CAPACITY
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 139.7 |  |  | 0.01288 |  |  | 0.10478 |  | 1 | CAPACITY
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01288 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01288 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01278 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 69.05 |  |  | 0.01278 |  |  | 0.10478 |  | 1 | CAPACITY
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 11.4 |  |  | 0.01278 |  |  | 0.08446 |  | 1 | CAPACITY
937512 | AD2-210 E | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | 0.01271 |  |  | 0 |  | 1 | MTX | AD2-210
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 175.82 |  |  | 0.01249 |  |  | 0.10478 |  | 1 | CAPACITY
219001 | SEWAREN7GT | 25 | 231 | 58 | 101.5 | 324.6 | 260.61 |  |  | 0.01192 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-089
219002 | SEWAREN7ST | 18 | 231 | 58 | 96.3 | 216.4 | 173.74 |  |  | 0.01192 |  |  | 0 |  | 1 | CAPACITY | Z2-089
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | 0.01192 |  |  | 0 |  | 1 | ENERGY | Z2-089
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | 0.01192 |  |  | 0.04435 |  | 1 | ENERGY | Z2-089
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 66.1 | 98 | 78.68 |  |  | 0.01169 |  |  | 0.08446 |  | 1 | CAPACITY
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 87.02 |  |  | 0.01169 |  |  | 0.08446 |  | 1 | CAPACITY
206327 | 28S RIV G1 | 13.8 | 228 | 57 | 86.9 | 99.9 | 87.02 |  |  | 0.01169 |  |  | 0.08446 |  | 1 | CAPACITY
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | 0.01147 |  |  | 0 |  | 1 | ENERGY
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 43.63 |  |  | 0.01132 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 46.17 |  |  | 0.01132 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
228471 | VALERO1 | 13.8 | 234 | 2 | 19.1 | 22 | 19.16 |  |  | 0.01128 |  |  | 0 |  | 1 | CAPACITY
228473 | VALERO3 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.01128 |  |  | 0 |  | 1 | CAPACITY
228484 | VALERO4 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.01128 |  |  | 0 |  | 1 | CAPACITY
228472 | VALERO2 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.01128 |  |  | 0 |  | 1 | CAPACITY
933332 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | 0.01085 |  |  | 0 |  | 1 | MTX | AC2-145
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 55.49 |  |  | 0.0105 |  |  | 0.08446 |  | 1 | CAPACITY
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0 |  |  | 0.00921 |  |  | 0 |  | 1 | NEWENERGY | W2-056
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 3.36 |  |  | 0.00921 |  |  | 0 |  | 1 | CAPACITY | W2-056
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0 |  |  | 0.00919 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 N
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 0.00919 |  |  | 0 |  | 1 | CAPACITY | AB1-025 N
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | 0.00918 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 141.3 |  |  | 0.00918 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 199.11 |  |  | 0.00811 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | 0.00811 |  |  | 0.04435 |  | 1 | CAPACITY | RED OAK
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | 0.00725 |  |  | 0.05 |  | 1 | MTX | AA2-061
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | 0.00725 |  |  | 0 |  | 1 | NEWENERGY | X1-012
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0 |  |  | 0.00725 |  |  | 0 |  | 1 | NEWENERGY | W3-106
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | 0.00725 |  |  | 0.05 |  | 1 | MTX | AA2-060
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0 |  |  | 0.00725 |  |  | 0 |  | 1 | NEWENERGY | W3-110
206742 | 28SUX_V3-011 | 34.5 | 228 | 64 | 0 | 2 | 0 |  |  | 0.00725 |  |  | 0 |  | 1 | CAPACITY
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | 0.00725 |  |  | 0 |  | 1 | NEWENERGY | W4-064
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 2.99 |  |  | 0.00726 |  |  | 0 |  | 1 | CAPACITY | Y1-020
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 2.97 |  |  | 0.00725 |  |  | 0 |  | 1 | CAPACITY | X1-012
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 2.29 |  |  | 0.00725 |  |  | 0 |  | 1 | CAPACITY | W3-110
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | 0.00725 |  |  | 0 |  | 1 | CAPACITY | W4-064
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 361.29 |  |  | 0.00708 |  |  | 0.10478 |  | 1 | CAPACITY
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 148.77 |  |  | 0.00708 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC1
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0 |  |  | 0.00688 |  |  | 0 |  | 1 | NEWENERGY | AC2-175
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0 |  |  | 0.00688 |  |  | 0 |  | 1 | NEWENERGY | AE1-081
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.77 |  |  | 0.00688 |  |  | 0 |  | 1 | CAPACITY | AE1-081
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0 |  |  | 0.0068 |  |  | 0 |  | 1 | NEWENERGY | W2-052
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | 0.0068 |  |  | 0 |  | 1 | CAPACITY | W2-052
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 369.31 |  |  | 0.00648 |  |  | 0.04435 |  | 1 | CAPACITY | Y1-065
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00648 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00648 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200055 | ROCKSP 4 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00648 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 4
200054 | ROCKSP 3 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00648 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 3
200052 | ROCKSP 1 | 18 | 225 | 57 | 145.7 | 167.5 | 145.91 |  |  | 0.00648 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 1
200053 | ROCKSP 2 | 18 | 225 | 57 | 144.9 | 166.5 | 145.04 |  |  | 0.00648 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 2
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0 |  |  | 0.00626 |  |  | 0 |  | 1 | NEWENERGY | Y1-075
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 0.00626 |  |  | 0 |  | 1 | CAPACITY | Y1-075
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 271.13 |  |  | 0.00554 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.00554 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.00554 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0 |  |  | 0.00535 |  |  | 0 |  | 1 | NEWENERGY | V4-005
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.88 |  |  | 0.00535 |  |  | 0 |  | 1 | CAPACITY | V4-005
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0 |  |  | 0.00473 |  |  | 0 |  | 1 | NEWENERGY | W2-071
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.85 |  |  | 0.00473 |  |  | 0 |  | 1 | CAPACITY | W2-071
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 245.67 |  |  | 0.00377 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | 0.00377 |  |  | 0.04435 |  | 1 | CAPACITY | RARITAN RIVER
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | 0.00377 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
207441 | AD1-113 ST | 18 | 228 | 58 | 0 | 25 | 0 |  |  | 0.00377 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207435 | AD1-113 CT2 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | 0.00377 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207434 | AD1-113 CT1 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | 0.00377 |  |  | 0.04435 |  | 1 | NEW | RARITAN RIVER
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 97.1 | 111.6 | 97.21 |  |  | 0.00377 |  |  | 0.08446 |  | 1 | CAPACITY
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 90.9 | 104.5 | 91.03 |  |  | 0.00377 |  |  | 0.08446 |  | 1 | CAPACITY
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 60.21 |  |  | 0.00372 |  |  | 0.10478 |  | 1 | CAPACITY
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.0023 |  |  | 0.04435 |  | 1 | CAPACITY | PHILLIPS ISLAND
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.0023 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213893 | PHLISST1 | 20 | 230 | 58 | 184 | 267 | 214.36 |  |  | 0.00228 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.00228 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1034.24 |  |  | 0.0014 |  |  | 0.01494 |  | 1 | CAPACITY
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 306.69 |  |  | 0.00137 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00137 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00137 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA2
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 154.95 |  |  | 0.00137 |  |  | 0 |  | 1 | CAPACITY | DELTA
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00137 |  |  | 0 |  | 1 | CAPACITY | DELTA
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00137 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00137 |  |  | 0 |  | 1 | CAPACITY | DELTA
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1049.33 |  |  | 0.00113 |  |  | 0.01494 |  | 1 | CAPACITY
933322 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | 0.00104 |  |  | 0 |  | 1 | MTX | AC2-144
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | 0.00093 |  |  | 0.0316 |  | 1 | CAPACITY
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | 0.00093 |  |  | 0.0316 |  | 1 | CAPACITY
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | 0.00093 |  |  | 0.0316 |  | 1 | CAPACITY
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0 |  |  | -8e-05 |  |  | 0 |  | 1 | NEWENERGY | Y3-087
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 1.84 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY | Y3-087
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | -0.00018 |  |  | 0.0316 |  | 1 | CAPACITY
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | -0.00018 |  |  | 0.0316 |  | 1 | CAPACITY
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | -0.00019 |  |  | 0.0316 |  | 1 | CAPACITY
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | -0.00019 |  |  | 0.0316 |  | 1 | CAPACITY
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | -0.00035 |  |  | 0.07484 |  | 1 | CAPACITY
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | -0.00035 |  |  | 0.07484 |  | 1 | CAPACITY
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 77.07 |  |  | -0.00034 |  |  | 0.07484 |  | 1 | CAPACITY
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | -0.00034 |  |  | 0.07484 |  | 1 | CAPACITY
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | -0.00034 |  |  | 0.07484 |  | 1 | CAPACITY
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 38.54 |  |  | -0.00034 |  |  | 0.07484 |  | 1 | CAPACITY
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 134 | 107.58 |  |  | -0.00074 |  |  | 0.08446 |  | 1 | CAPACITY
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEWENERGY | X1-095
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00114 |  |  | 0 |  | 1 | CAPACITY | X1-095
206747 | 28DSM_X3-029 | 34.5 | 228 | 29 | 0 | 11.15 | 0 |  |  | -0.00156 |  |  | 0.10478 |  | 1 | ENERGY
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | -0.00156 |  |  | 0.08446 |  | 1 | ENERGY
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0 |  |  | -0.00167 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 S
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00167 |  |  | 0 |  | 1 | CAPACITY | AB1-025 S
204651 | 27PORT CT | 13.8 | 227 | 56 | 4 | 35 | 28.1 |  |  | -0.00181 |  |  | 0.08446 |  | 1 | CAPACITY
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00206 |  |  | 0 |  | 1 | NEWENERGY | Y2-018
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00207 |  |  | 0 |  | 1 | NEWENERGY | Y2-081
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.00207 |  |  | 0 |  | 1 | CAPACITY | Y2-081
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 256.27 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | -0.00222 |  |  | 0.04435 |  | 1 | CAPACITY | HUNTERSTOWN
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 134.08 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0 |  |  | -0.00222 |  |  | 0 |  | 1 | NEWENERGY | X3-075
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -0.00235 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 33.72 |  |  | -0.00237 |  |  | 0.04435 |  | 1 | CAPACITY | EAGLE POINT
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 24.08 |  |  | -0.00237 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 20 | 16.06 |  |  | -0.00238 |  |  | 0.08446 |  | 1 | CAPACITY
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -0.00238 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0 |  |  | -0.00245 |  |  | 0 |  | 1 | NEWENERGY | AA2-072
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | -0.00247 |  |  | 0 |  | 1 | ENERGY
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 140.6 | 112.88 |  |  | -0.00248 |  |  | 0.08446 |  | 1 | CAPACITY
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 91.2 |  |  | -0.00248 |  |  | 0.08446 |  | 1 | CAPACITY
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 83.5 |  |  | -0.00248 |  |  | 0.08446 |  | 1 | CAPACITY
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 41.75 |  |  | -0.00248 |  |  | 0.08446 |  | 1 | CAPACITY
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.21 |  |  | -0.00248 |  |  | 0 |  | 1 | CAPACITY
220904 | CRANE G2 | 20 | 232 | 12 | 60 | 195 | 0 |  |  | -0.00253 |  |  | 0.10478 |  | 1 | NEW
220905 | CRANE GT | 4.16 | 232 | 55 | 0 | 14 | 0 |  |  | -0.00253 |  |  | 0.08446 |  | 1 | NEW
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 45.76 |  |  | -0.00254 |  |  | 0.10478 |  | 1 | CAPACITY
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.5 | 24.49 |  |  | -0.00254 |  |  | 0.08446 |  | 1 | CAPACITY
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 30 | 24.08 |  |  | -0.00254 |  |  | 0.08446 |  | 1 | CAPACITY
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 246 |  |  | -0.00256 |  |  | 0.10478 |  | 1 | CAPACITY
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 102.85 |  |  | -0.00256 |  |  | 0.10478 |  | 1 | CAPACITY
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | -0.00256 |  |  | 0.08446 |  | 1 | ENERGY
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 10.68 |  |  | -0.00256 |  |  | 0.08446 |  | 1 | CAPACITY
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 516 |  |  | -0.00259 |  |  | 0.10478 |  | 1 | CAPACITY
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 512.95 |  |  | -0.00259 |  |  | 0.10478 |  | 1 | CAPACITY
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 318.73 |  |  | -0.00259 |  |  | 0.10478 |  | 1 | CAPACITY
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 120 |  |  |  | -0.0026
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.49 |  |  | -0.00269 |  |  | 0 |  | 1 | CAPACITY
226895 | WOAKV2-037 E | 69 | 233 | 65 | 0 | 4.5 | 0 |  |  | -0.00275 |  |  | 0 |  | 1 | ENERGY
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 695.27 |  |  | -0.00281 |  |  | 0.01494 |  | 1 | CAPACITY
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 675.85 |  |  | -0.00281 |  |  | 0.01494 |  | 1 | CAPACITY
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.76 |  |  | -0.00283 |  |  | 0 |  | 1 | CAPACITY
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | -0.00284 |  |  | 0.08446 |  | 1 | ENERGY
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0 |  |  | -0.00286 |  |  | 0 |  | 1 | NEWENERGY | AB2-157
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.69 |  |  | -0.00286 |  |  | 0 |  | 1 | CAPACITY
925011 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00286 |  |  | 0 |  | 1 | CAPACITY | AB2-157
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 477.7 |  |  | -0.00287 |  |  | 0.10478 |  | 1 | CAPACITY
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 469.91 |  |  | -0.00287 |  |  | 0.10478 |  | 1 | CAPACITY
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
227024 | SMECOCT | 13.8 | 238 | 57 | 30 | 80.2 | 64.39 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 19.59 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 14.45 |  |  | -0.00287 |  |  | 0.08446 |  | 1 | CAPACITY
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 497.29 |  |  | -0.00288 |  |  | 0.10478 |  | 1 | CAPACITY
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 492.39 |  |  | -0.00288 |  |  | 0.10478 |  | 1 | CAPACITY
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 272.01 |  |  | -0.00289 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | -0.00289 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | -0.00289 |  |  | 0.04435 |  | 1 | CAPACITY | WALDORF
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 0 |  |  | -0.00288 |  |  | 0 |  | 1 | NEWENERGY | AC2-101
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 0 |  |  | -0.00288 |  |  | 0 |  | 1 | NEWENERGY | AC2-120
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00288 |  |  | 0.08446 |  | 1 | CAPACITY
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00288 |  |  | 0.08446 |  | 1 | CAPACITY
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00288 |  |  | 0.08446 |  | 1 | CAPACITY
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00288 |  |  | 0.08446 |  | 1 | CAPACITY
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | -0.00288 |  |  | 0.08446 |  | 1 | CAPACITY
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | -0.00288 |  |  | 0.08446 |  | 1 | CAPACITY
226915 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 9.92 |  |  | -0.00288 |  |  | 0 |  | 1 | CAPACITY | AC2-101
226912 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 8.39 |  |  | -0.00288 |  |  | 0 |  | 1 | CAPACITY | AC2-120
910861 | X3-087 C | 230 | 233 | 58 | 0 | 744 | 597.33 |  |  | -0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
917371 | Z2-060 | 230 | 233 | 58 | 0 | 116 | 93.13 |  |  | -0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
920642 | AA2-170 E | 230 | 233 | 58 | 0 | 19.1 | 0 |  |  | -0.00294 |  |  | 0.04435 |  | 1 | NEW | AA2-170
920641 | AA2-170 C | 230 | 233 | 58 | 0 | 92 | 73.86 |  |  | -0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-170
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 64.23 |  |  | -0.00294 |  |  | 0 |  | 1 | CAPACITY | PANDA
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | -0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | PANDA
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | -0.00294 |  |  | 0 |  | 1 | CAPACITY | PANDA
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 330 | 264.94 |  |  | -0.00296 |  |  | 0 |  | 1 | CAPACITY | X4-035
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | -0.00296 |  |  | 0.04435 |  | 1 | CAPACITY | X4-035
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | -0.00296 |  |  | 0 |  | 1 | CAPACITY | X4-035
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | -0.00298 |  |  | 0.10478 |  | 1 | ENERGY
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 4 | 3.21 |  |  | -0.00298 |  |  | 0 |  | 1 | CAPACITY
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00299 |  |  | 0 |  | 1 | NEWENERGY | W4-046
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 1.93 |  |  | -0.00299 |  |  | 0 |  | 1 | CAPACITY | W4-046
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | -0.00304 |  |  | 0 |  | 1 | ENERGY
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | -0.00312 |  |  | 0.08446 |  | 1 | CAPACITY
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | -0.00312 |  |  | 0.08446 |  | 1 | CAPACITY
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 41.75 |  |  | -0.00312 |  |  | 0.10478 |  | 1 | CAPACITY
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 14.45 |  |  | -0.00312 |  |  | 0.08446 |  | 1 | CAPACITY
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 0 |  |  | -0.00322 |  |  | 0 |  | 1 | NEWENERGY | AB2-129
924771 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 0 |  |  | -0.00322 |  |  | 0 |  | 1 | NEW | AB2-129
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 245.67 |  |  | -0.00329 |  |  | 0 |  | 1 | CAPACITY | X4-039
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.00329 |  |  | 0 |  | 1 | CAPACITY | X4-039
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.00329 |  |  | 0.04435 |  | 1 | CAPACITY | X4-039
313821 | 6PACIFIC | 230 | 345 | 75 | 0 | 0.09 | 0 |  |  | -0.00331 |  |  | 0 |  | 1 | NEWENERGY
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 31.31 |  |  | -0.00334 |  |  | 0.08446 |  | 1 | CAPACITY
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 201.52 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00334 |  |  | 0.04435 |  | 1 | CAPACITY | POSSUM POINT
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00335 |  |  | 0.10478 |  | 1 | CAPACITY
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00335 |  |  | 0.10478 |  | 1 | CAPACITY
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 28.74 |  |  | -0.00334 |  |  | 0.10478 |  | 1 | CAPACITY
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 28.66 |  |  | -0.00334 |  |  | 0.10478 |  | 1 | CAPACITY
314088 | 6VANDORN | 230 | 345 | 2 | 7 | 21 | 16.86 |  |  | -0.00335 |  |  | 0 |  | 1 | CAPACITY
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00339 |  |  | 0 |  | 1 | NEWENERGY | AC2-072
932521 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00339 |  |  | 0 |  | 1 | CAPACITY | AC2-072
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 0.68 | 0 |  |  | -0.00341 |  |  | 0 |  | 1 | NEWENERGY
235002 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEW | AC1-039
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEWENERGY | AC1-039
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEWENERGY | AA1-109
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 3.61 |  |  | -0.00343 |  |  | 0 |  | 1 | CAPACITY | AA1-109
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00344 |  |  | 0.08446 |  | 1 | CAPACITY
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00344 |  |  | 0.08446 |  | 1 | CAPACITY
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 1.61 |  |  | -0.00344 |  |  | 0 |  | 1 | CAPACITY
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.00345 |  |  | 0 |  | 1 | NEWENERGY | W1-116
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 4.27 |  |  | -0.00345 |  |  | 0 |  | 1 | CAPACITY | W1-116
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00347 |  |  | 0.08446 |  | 1 | CAPACITY
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00347 |  |  | 0.08446 |  | 1 | CAPACITY
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 128.86 |  |  | -0.00347 |  |  | 0.08446 |  | 1 | CAPACITY
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 152.3 | 122.28 |  |  | -0.00347 |  |  | 0.10478 |  | 1 | CAPACITY
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00347 |  |  | 0.10478 |  | 1 | CAPACITY
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00347 |  |  | 0.10478 |  | 1 | CAPACITY
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 120.19 |  |  | -0.00347 |  |  | 0.10478 |  | 1 | CAPACITY
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 0 |  |  | -0.00348 |  |  | 0 |  | 1 | NEWENERGY | AB2-029
314078 | 3REMNGTN | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00348 |  |  | 0 |  | 1 | CAPACITY | AB2-029
315033 | 1BIRCHWDA | 18 | 345 | 13 | 85 | 238 | 191.08 |  |  | -0.00349 |  |  | 0.10478 |  | 1 | CAPACITY
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
923213 | AB1-125 E OP | 34.5 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
923202 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AB1-096
923212 | AB1-125 C OP | 34.5 | 201 | 75 | 0 | 5.7 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 6.98 |  |  | -0.0035 |  |  | 0 |  | 1 | CAPACITY
930521 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 2.49 |  |  | -0.0035 |  |  | 0 |  | 1 | CAPACITY | AB1-096
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 2
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 1
926737 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.0035 |  |  | 0 |  | 1 | CAPACITY | AC1-158 1
926738 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.0035 |  |  | 0 |  | 1 | CAPACITY | AC1-158 2
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00351 |  |  | 0.08446 |  | 1 | CAPACITY
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00351 |  |  | 0.08446 |  | 1 | CAPACITY
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 128.94 |  |  | -0.00351 |  |  | 0.08446 |  | 1 | CAPACITY
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 128.54 |  |  | -0.00351 |  |  | 0.08446 |  | 1 | CAPACITY
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 128.3 |  |  | -0.00351 |  |  | 0.08446 |  | 1 | CAPACITY
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0 |  |  | -0.00351 |  |  | 0 |  | 1 | NEWENERGY | AC2-136
933251 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 4.41 |  |  | -0.00351 |  |  | 0 |  | 1 | CAPACITY | AC2-136
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 761.83 |  |  | -0.00352 |  |  | 0.01494 |  | 1 | CAPACITY
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 761.51 |  |  | -0.00352 |  |  | 0.01494 |  | 1 | CAPACITY
923872 | AB2-027 E | 34.5 | 201 | 75 | 0 | 5.5 | 0 |  |  | -0.00353 |  |  | 0 |  | 1 | NEWENERGY | AB2-027
235006 | AB2-027 C | 34.5 | 201 | 75 | 0 | 3.3 | 0 |  |  | -0.00353 |  |  | 0 |  | 1 | NEW | AB2-027
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00353 |  |  | 0 |  | 1 | CAPACITY
316149 | AD1-046 E | 230 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00355 |  |  | 0 |  | 1 | NEWENERGY | AD1-044
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00356 |  |  | 0 |  | 1 | NEWENERGY | W4-102
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0 |  |  | -0.00356 |  |  | 0 |  | 1 | NEWENERGY | AB2-097
237799 | 01AA2-159 C | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.00356 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
920562 | AA2-159 E | 34.5 | 201 | 75 | 0 | 7.3 | 0 |  |  | -0.00356 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00355 |  |  | 0 |  | 1 | NEWENERGY | AE1-124
316148 | AD1-046 C | 230 | 345 | 75 | 0 | 30.7 | 24.65 |  |  | -0.00355 |  |  | 0 |  | 1 | CAPACITY | AD1-044
938961 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00355 |  |  | 0 |  | 1 | CAPACITY | AE1-124
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00356 |  |  | 0 |  | 1 | CAPACITY | W4-102
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 0 |  |  | -0.00357 |  |  | 0 |  | 1 | NEWENERGY | AB2-158
925021 | AB2-158 C | 230 | 345 | 75 | 0 | 61 | 48.97 |  |  | -0.00357 |  |  | 0 |  | 1 | CAPACITY | AB2-158
314766 | 6LOUISA | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00357 |  |  | 0 |  | 1 | NEWENERGY
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 2.09 |  |  | -0.00356 |  |  | 0 |  | 1 | CAPACITY
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.88 |  |  | -0.00356 |  |  | 0 |  | 1 | CAPACITY
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0 |  |  | -0.00358 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
923192 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0 |  |  | -0.00358 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 0 |  |  | -0.00357 |  |  | 0 |  | 1 | NEWENERGY | AC1-118
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0 |  |  | -0.00358 |  |  | 0 |  | 1 | NEWENERGY | AA1-095
314190 | 6WESTMOR | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00357 |  |  | 0 |  | 1 | CAPACITY | AC1-118
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 2.33 |  |  | -0.00358 |  |  | 0 |  | 1 | CAPACITY | AA1-095
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 136.49 |  |  | -0.00359 |  |  | 0.08446 |  | 1 | CAPACITY
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.0036 |  |  | 0.08446 |  | 1 | CAPACITY
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.0036 |  |  | 0.08446 |  | 1 | CAPACITY
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 126.85 |  |  | -0.00359 |  |  | 0.08446 |  | 1 | CAPACITY
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.0036 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 5
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.0036 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 6
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00359 |  |  | 0.08446 |  | 1 | CAPACITY
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00359 |  |  | 0.08446 |  | 1 | CAPACITY
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00359 |  |  | 0.08446 |  | 1 | CAPACITY
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 61.9 |  |  | -0.00359 |  |  | 0.08446 |  | 1 | CAPACITY
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00359 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00359 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 2
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.0036 |  |  | 0 |  | 1 | NEWENERGY | AC2-138
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 19.99 |  |  | -0.0036 |  |  | 0.10478 |  | 1 | CAPACITY
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00359 |  |  | 0 |  | 1 | CAPACITY | South Anna 2
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00359 |  |  | 0 |  | 1 | CAPACITY | South Anna 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 19.27 |  |  | -0.0036 |  |  | 0.10478 |  | 1 | CAPACITY
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 6.3 | 5.06 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | AC2-138
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0 |  |  | -0.0036 |  |  | 0 |  | 1 | NEWENERGY | AA1-092
314172 | 6DUNNSVL | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0036 |  |  | 0 |  | 1 | NEWENERGY
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 6.42 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | AA1-092
314734 | 6CASHSCORNER | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00361 |  |  | 0 |  | 1 | NEWENERGY
314222 | 6HANOVER | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00362 |  |  | 0 |  | 1 | NEWENERGY
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY | AC1-112
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY | AB1-027
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY | AC2-070
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 8.83 |  |  | -0.00364 |  |  | 0.12623 |  | 1 | CAPACITY
314241 | 6OLDCHRC | 230 | 345 | 75 | 0 | 1.82 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | CAPACITY | AB1-027
932501 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 7.39 |  |  | -0.00364 |  |  | 0 |  | 1 | CAPACITY | AC2-070
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 3.21 |  |  | -0.00363 |  |  | 0 |  | 1 | CAPACITY
314213 | 3CARVER | 115 | 345 | 75 | 0 | 0 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEW | AC1-107
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00365 |  |  | 0.04435 |  | 1 | NEW | AC1-107
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEW | AC1-107
926785 | AC1-164 E | 0.44 | 345 | 75 | 0 | 99.2 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEWENERGY | AC1-164
316114 | AB2-068 ST | 22 | 345 | 58 | 0 | 492 | 395.01 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316113 | AB2-068 CT2 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316112 | AB2-068 CT1 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00365 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-068
926784 | AC1-164 C | 0.44 | 345 | 75 | 0 | 220.8 | 177.27 |  |  | -0.00365 |  |  | 0 |  | 1 | NEW | AC1-164
314189 | 6PAPERMILL | 230 | 345 | 1 | 12 | 37 | 0 |  |  | -0.00365 |  |  | 0.10478 |  | 1 | ENERGY
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY | AC1-065
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 69.05 |  |  | -0.00364 |  |  | 0.10478 |  | 1 | CAPACITY
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 68.97 |  |  | -0.00364 |  |  | 0.10478 |  | 1 | CAPACITY
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 68.72 |  |  | -0.00364 |  |  | 0.10478 |  | 1 | CAPACITY
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 68.64 |  |  | -0.00364 |  |  | 0.10478 |  | 1 | CAPACITY
925863 | AC1-065 C | 0.39 | 345 | 75 | 0 | 41.8 | 33.56 |  |  | -0.00364 |  |  | 0 |  | 1 | CAPACITY | AC1-065
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEWENERGY | AC2-137
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY | AD2-030
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEWENERGY | AE1-074
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEWENERGY | AB2-024
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY | AD1-063
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 16.06 |  |  | -0.00364 |  |  | 0.12623 |  | 1 | CAPACITY
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.3 | 13.09 |  |  | -0.00365 |  |  | 0.12623 |  | 1 | CAPACITY
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 11.96 |  |  | -0.00365 |  |  | 0.12623 |  | 1 | CAPACITY
938551 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | AE1-074
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00364 |  |  | 0 |  | 1 | CAPACITY | AD2-030
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 11.4 | 9.15 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | AC2-137
314375 | 6CORRCTN | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | AB2-024
314187 | 3WAN 176 | 115 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY
934391 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.00364 |  |  | 0 |  | 1 | CAPACITY | AD1-063
314176 | 6HARMONY | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00364 |  |  | 0 |  | 1 | NEWENERGY
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 4.98 |  |  | -0.00364 |  |  | 0 |  | 1 | CAPACITY
315085 | 1SPRUNCC | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00365 |  |  | 0.10478 |  | 1 | NEW
315086 | 1SPRUNCD | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00365 |  |  | 0.10478 |  | 1 | NEW
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 104.93 |  |  | -0.00365 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 7
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 103.25 |  |  | -0.00365 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 8
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 53.15 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 48.17 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7
314294 | 6ENON | 230 | 345 | 75 | 0 | 0.23 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEWENERGY
313828 | 3WHITEMARSH | 115 | 345 | 75 | 0 | 0.05 | 0 |  |  | -0.00366 |  |  | 0 |  | 1 | NEWENERGY
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | -0.00367 |  |  | 0.10478 |  | 1 | ENERGY
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 101.16 |  |  | -0.00367 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00367 |  |  | 0.04435 |  | 1 | CAPACITY | HOPEWELL HCF
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00367 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00367 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00367 |  |  | 0.10478 |  | 1 | CAPACITY
314177 | 3HAYES89 | 115 | 345 | 75 | 0 | 0.31 | 0 |  |  | -0.00367 |  |  | 0 |  | 1 | NEWENERGY
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 788.9 | 633.38 |  |  | -0.00368 |  |  | 0.10478 |  | 1 | CAPACITY
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 422.86 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 0 |  |  | -0.00368 |  |  | 0 |  | 1 | NEWENERGY | AB2-134
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00368 |  |  | 0.04435 |  | 1 | CAPACITY | WARREN COUNTY CC
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00368 |  |  | 0 |  | 1 | NEWENERGY | AB2-160
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 0 |  |  | -0.00367 |  |  | 0 |  | 1 | NEWENERGY | AB2-190
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 89.92 |  |  | -0.00367 |  |  | 0 |  | 1 | CAPACITY | AB2-190
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 57.65 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | AB2-134
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 24.41 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | AB2-160
316158 | AD2-164 | 230 | 345 | 57 | 0 | 26.7 | 21.44 |  |  | -0.00368 |  |  | 0.08446 |  | 1 | CAPACITY
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 12.04 |  |  | -0.00368 |  |  | 0.12623 |  | 1 | CAPACITY
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 8.03 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY
313812 | 6ROCKLANDING | 230 | 345 | 75 | 0 | 0.11 | 0 |  |  | -0.00368 |  |  | 0 |  | 1 | NEWENERGY
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 678.09 |  |  | -0.00369 |  |  | 0.01494 |  | 1 | CAPACITY
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 677.21 |  |  | -0.00368 |  |  | 0.01494 |  | 1 | CAPACITY
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 69.77 |  |  | -0.00369 |  |  | 0.10478 |  | 1 | CAPACITY
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 69.69 |  |  | -0.00369 |  |  | 0.10478 |  | 1 | CAPACITY
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00369 |  |  | 0.10478 |  | 1 | CAPACITY
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00369 |  |  | 0.10478 |  | 1 | CAPACITY
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 23.76 |  |  | -0.00369 |  |  | 0.10478 |  | 1 | CAPACITY
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY | AB2-161
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 88.96 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 87.83 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 86.31 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
314331 | 6POE | 230 | 345 | 75 | 0 | 12.27 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY | AD1-060
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY | AE1-162
935212 | AD1-156 E | 230 | 345 | 75 | 0 | 7.92 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY | AD1-156
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AC1-147
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.00369 |  |  | 0 |  | 1 | CAPACITY | AB2-161
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 12.2 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 11.96 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 10.36 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
926661 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 10.12 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AC1-147
316258 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00369 |  |  | 0 |  | 1 | CAPACITY | AE1-162
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 9.55 |  |  | -0.0037 |  |  | 0.10478 |  | 1 | CAPACITY
935211 | AD1-156 C | 230 | 345 | 75 | 0 | 11.82 | 9.49 |  |  | -0.00369 |  |  | 0 |  | 1 | CAPACITY | AD1-156
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 9.05 |  |  | -0.0037 |  |  | 0.12623 |  | 1 | CAPACITY
314533 | 6SMITFLD | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY
934362 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 4.58 |  |  | -0.00369 |  |  | 0 |  | 1 | CAPACITY | AD1-060
314453 | 6CHRHLND | 230 | 345 | 75 | 0 | 0.08 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY
314487 | 3MCLAUGH | 115 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY | AA1-139
314525 | 6KINGFORK | 230 | 345 | 75 | 0 | 24.3 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY
314550 | 6HICKORY | 230 | 345 | 75 | 0 | 22.93 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 63.18 |  |  | -0.00371 |  |  | 0 |  | 1 | CAPACITY | AA1-139
314466 | 6FENTRES | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY
313717 | 6SLIGO L2192 | 230 | 345 | 75 | 0 | 12.34 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | Z1-068
316145 | AE1-027 E | 230 | 345 | 75 | 0 | 6.9 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AE1-027
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AC2-196
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AC1-027
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AB2-026
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AE1-075
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AD1-144
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AD2-215
316147 | AE1-028 E | 230 | 345 | 75 | 0 | 4.4 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | NEWENERGY | AE1-028
314333 | 6POWHATN | 230 | 345 | 75 | 0 | 3.97 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AB2-026
314645 | 6SLIGO L269 | 230 | 345 | 75 | 0 | 3.22 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY
316144 | AE1-027 C | 230 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AE1-027
938561 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AE1-075
933731 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 8.03 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AC2-196
316150 | AD2-215 C | 230 | 345 | 76 | 0 | 9.8 | 7.87 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AD2-215
935111 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 7.79 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AD1-144
314491 | 3PENDLTN | 115 | 345 | 75 | 0 | 1.89 | 0 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AC1-027
316146 | AE1-028 C | 230 | 345 | 75 | 0 | 7.6 | 6.1 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | AE1-028
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.2 |  |  | -0.0037 |  |  | 0 |  | 1 | CAPACITY | Z1-068
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | NEWENERGY | Y1-086
314632 | 6AYDLETOLD | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | NEWENERGY | AB2-022
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY | Z2-030
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY | AC2-174
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | NEWENERGY | Z2-027
933571 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEW | AC2-174
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 12.04 |  |  | -0.00371 |  |  | 0.12623 |  | 1 | CAPACITY
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 10.44 |  |  | -0.00372 |  |  | 0 |  | 1 | CAPACITY | AB2-022
314648 | 6SUNBURY | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | NEWENERGY
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | MTX | Z1-082
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 3.93 |  |  | -0.00371 |  |  | 0 |  | 1 | CAPACITY
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00371 |  |  | 0 |  | 1 | CAPACITY | Z2-030
314638 | 6ELIZ CT | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | CAPACITY | Y1-086
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 1.61 |  |  | -0.00371 |  |  | 0 |  | 1 | CAPACITY
314639 | 6TANGLEW | 230 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | CAPACITY | Z2-027
314640 | 6KITTY HAWK | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00371 |  |  | 0 |  | 1 | NEWENERGY
901082 | W1-029 E | 230 | 345 | 74 | 0 | 261 | 0 |  |  | -0.00372 |  |  | 0 |  | 1 | NEWENERGY | W1-029
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00372 |  |  | 0 |  | 1 | CAPACITY | W1-029
314651 | 6WINFALL | 230 | 345 | 75 | 0 | 3.35 | 0 |  |  | -0.00373 |  |  | 0 |  | 1 | NEWENERGY
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.56 |  |  | -0.00372 |  |  | 0 |  | 1 | CAPACITY
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 0 |  |  | -0.00374 |  |  | 0 |  | 1 | NEWENERGY | Z1-036
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00374 |  |  | 0 |  | 1 | CAPACITY | Z1-036
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00373 |  |  | 0 |  | 1 | NEWENERGY | AB2-025
314435 | 6SAPONY | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00373 |  |  | 0 |  | 1 | CAPACITY | AB2-025
942852 | AE2-304 E | 230 | 345 | 75 | 0 | 1.4 | 0 |  |  | -0.00373 |  |  | 0 |  | 1 | NEWENERGY | AE2-304
942851 | AE2-304 C | 230 | 345 | 75 | 0 | 3.3 | 2.65 |  |  | -0.00373 |  |  | 0 |  | 1 | CAPACITY | AE2-304
314662 | 6S HERTFORD | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00373 |  |  | 0 |  | 1 | NEWENERGY
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | -0.00375 |  |  | 0.10478 |  | 1 | ENERGY
314637 | 6EDENTON | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00375 |  |  | 0 |  | 1 | NEWENERGY | AA2-059
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 480.11 |  |  | -0.00375 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 452.01 |  |  | -0.00376 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00375 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-086
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00375 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00375 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00376 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00376 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00376 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 0 |  |  | -0.00375 |  |  | 0 |  | 1 | NEW | AB2-015
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 0 |  |  | -0.00375 |  |  | 0 |  | 1 | NEWENERGY | AB2-015
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00376 |  |  | 0.10478 |  | 1 | CAPACITY
314541 | 3WATKINS | 115 | 345 | 1 | 0 | 4 | 0 |  |  | -0.00376 |  |  | 0 |  | 1 | ENERGY
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00377 |  |  | 0.10478 |  | 1 | CAPACITY
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00376 |  |  | 0 |  | 1 | NEWENERGY | AA2-178
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00376 |  |  | 0 |  | 1 | CAPACITY | AA2-178
314566 | 3CRESWEL | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00376 |  |  | 0 |  | 1 | NEWENERGY
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  |  |  | -0.0038
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 322.35 |  |  | -0.00377 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 0 |  |  | -0.00377 |  |  | 0 |  | 1 | NEWENERGY | AA2-088
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 198.31 |  |  | -0.00377 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00377 |  |  | 0.04435 |  | 1 | CAPACITY | BEAR GARDEN
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00377 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00377 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00377 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00377 |  |  | 0.04435 |  | 1 | CAPACITY | FLUVANNA
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 2
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | AC1-116
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 30.51 |  |  | -0.00377 |  |  | 0 |  | 1 | CAPACITY | AA2-088
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | AB2-100 1
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | AB2-100 2
926451 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 3.77 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | AC1-116
314594 | 6PLYMOTH | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00377 |  |  | 0 |  | 1 | NEWENERGY
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY | AB1-128
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY | AB1-127
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | AC2-071
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | AB2-045
314589 | 3MURPHYS | 115 | 345 | 75 | 0 | 4.66 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | V4-068
932511 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | AC2-071
314617 | 3TUNIS | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY
314677 | 6BUCKING | 230 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | AB2-045
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | V4-068
235041 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00379 |  |  | 0 |  | 1 | CAPACITY | AB1-128
235040 | 01AB1-127 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00379 |  |  | 0 |  | 1 | CAPACITY | AB1-127
314620 | 6CASHIE | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY
313826 | 6HYDRAULIC | 230 | 345 | 75 | 0 | 0.04 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 538.72 |  |  | -0.0038 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-116
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AB2-174
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY | AA1-065
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AA1-063A
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 53.6 | 43.03 |  |  | -0.00379 |  |  | 0 |  | 1 | CAPACITY | AA1-065
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 40.87 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY | AA1-063A
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 40.14 |  |  | -0.00379 |  |  | 0.19858 |  | 1 | CAPACITY
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 33.72 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY | AB2-174
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 27.3 |  |  | -0.00379 |  |  | 0.08446 |  | 1 | CAPACITY
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AB1-139
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEW
314568 | 3EARLEYS | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY | AB2-099
314551 | 3AHOSKIE | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AE1-041
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00379 |  |  | 0 |  | 1 | CAPACITY | AB2-099
314604 | 3SEABORD | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY
930901 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 2.01 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY | AB1-139
938281 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY | AE1-041
923262 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
923991 | AB2-040 C O1 | 115 | 345 | 75 | 0 | 44 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEW | AB2-040
923992 | AB2-040 E O1 | 115 | 345 | 75 | 0 | 36 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AB2-040
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY | AA2-053
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.0038 |  |  | 0.07484 |  | 1 | CAPACITY
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.0038 |  |  | 0.07484 |  | 1 | CAPACITY
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 44 |  |  | -0.00381 |  |  | 0 |  | 1 | CAPACITY | AA2-053
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 32.44 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY | AB1-173
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | AB1-173
314266 | 6NORTHAMPTON | 230 | 345 | 75 | 0 | 2.47 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY
314626 | 3WOODLND | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY
314596 | 3POPLR C | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY
314762 | 3JAMES R | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.5 | 354.46 |  |  | -0.00381 |  |  | 0.10478 |  | 1 | CAPACITY
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 350.93 |  |  | -0.00381 |  |  | 0.10478 |  | 1 | CAPACITY
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00382 |  |  | 0.10478 |  | 1 | CAPACITY
925122 | AB2-169 E | 115 | 345 | 75 | 0 | 35 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY | AB2-169
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 76.6 | 61.5 |  |  | -0.00381 |  |  | 0.04435 |  | 1 | CAPACITY | ROSEMARY
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 40.38 |  |  | -0.00381 |  |  | 0.07484 |  | 1 | CAPACITY
314807 | 3MT JACK | 115 | 345 | 75 | 0 | 9.7 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 38.54 |  |  | -0.00381 |  |  | 0.07484 |  | 1 | CAPACITY
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 47.5 | 38.13 |  |  | -0.00381 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
925121 | AB2-169 C | 115 | 345 | 75 | 0 | 39 | 31.31 |  |  | -0.00381 |  |  | 0 |  | 1 | CAPACITY | AB2-169
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 35.9 | 28.82 |  |  | -0.00381 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY | AC2-074
314578 | 3HORNRTN | 115 | 345 | 75 | 0 | 5.15 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY
314579 | 6HORNRTN | 230 | 345 | 75 | 0 | 3.91 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 8.83 |  |  | -0.00381 |  |  | 0.12623 |  | 1 | CAPACITY
932541 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY | AC2-074
314559 | 3CAROLNA | 115 | 345 | 75 | 0 | 1.21 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY
314582 | 3KELFORD | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | CAPACITY | Z2-043
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY | AD1-085
314713 | 3PAMPLIN | 115 | 345 | 75 | 0 | 9.73 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY
316143 | AD1-160 E | 115 | 345 | 75 | 0 | 9.1 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY | AD1-160
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY | AD1-157
313853 | 3PONTONDP | 115 | 345 | 2 | 0 | 4 | 0 |  |  | -0.00383 |  |  | 0 |  | 1 | ENERGY
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 16 | 12.85 |  |  | -0.00383 |  |  | 0.12623 |  | 1 | CAPACITY
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 9.88 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY | AD1-085
314603 | 3SCOT NK | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY
935221 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY | AD1-157
316142 | AD1-160 C | 115 | 345 | 75 | 0 | 6.6 | 5.3 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY | AD1-160
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 1.04 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.64 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY
314593 | 3PARMELE | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY
314629 | 3MARTNCO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY | AC1-054
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY | AC1-036
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 35.73 |  |  | -0.00384 |  |  | 0 |  | 1 | CAPACITY | AC1-054
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY | AE1-099
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY | AE1-098
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00384 |  |  | 0 |  | 1 | CAPACITY | AE1-098
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00384 |  |  | 0 |  | 1 | CAPACITY | AE1-099
925611 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 6.9 |  |  | -0.00384 |  |  | 0 |  | 1 | CAPACITY | AC1-036
314798 | 3MERCK5 | 115 | 345 | 75 | 0 | 0.16 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AB2-043
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AB2-060
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 43.67 |  |  | -0.00386 |  |  | 0 |  | 1 | CAPACITY | AB2-060
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00385 |  |  | 0.08446 |  | 1 | CAPACITY
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00385 |  |  | 0.08446 |  | 1 | CAPACITY
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AB2-077
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AB2-078
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AB2-079
314574 | 6EVERETS | 230 | 345 | 75 | 0 | 5.89 | 0 |  |  | -0.00385 |  |  | 0 |  | 1 | NEWENERGY
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0 |  |  | -0.00385 |  |  | 0 |  | 1 | NEWENERGY | AA1-067
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 15.17 |  |  | -0.00386 |  |  | 0 |  | 1 | CAPACITY | AB2-043
924311 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00386 |  |  | 0 |  | 1 | NEW | AB2-078
924321 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00386 |  |  | 0 |  | 1 | NEW | AB2-079
924301 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00386 |  |  | 0 |  | 1 | NEW | AB2-077
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY | Z2-088
919702 | AA2-057 E OP | 115 | 345 | 75 | 0 | 21.1 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AA2-057
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 53 | 42.55 |  |  | -0.00387 |  |  | 0 |  | 1 | CAPACITY | Z2-088
313719 | 3CHESTNUT | 115 | 345 | 75 | 0 | 44.7 | 35.89 |  |  | -0.00386 |  |  | 0 |  | 1 | CAPACITY | AA2-057
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
314608 | 3TARBORO | 115 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY | Z2-044
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 12.04 |  |  | -0.00387 |  |  | 0.07484 |  | 1 | CAPACITY
314623 | 3WITAKRS | 115 | 345 | 75 | 0 | 2.51 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | CAPACITY | Z2-044
314549 | 3TOT1 | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY
314557 | 3BETHELC | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY
314607 | 3TAR RVR | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY
314545 | 3TOT5 | 115 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY
314560 | 3CNETO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00387 |  |  | 0 |  | 1 | NEWENERGY
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00389 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 0 |  |  | -0.00388 |  |  | 0 |  | 1 | NEWENERGY | AB2-059
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00388 |  |  | 0 |  | 1 | NEWENERGY | AB1-081
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 52.99 |  |  | -0.00388 |  |  | 0 |  | 1 | CAPACITY | AB2-059
922922 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00388 |  |  | 0 |  | 1 | CAPACITY | AB1-081
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00388 |  |  | 0.08446 |  | 1 | CAPACITY
314554 | 3BTLEBRO | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00388 |  |  | 0 |  | 1 | NEWENERGY
314205 | 3HEARTS | 115 | 345 | 75 | 0 | 0.41 | 0 |  |  | -0.00388 |  |  | 0 |  | 1 | NEWENERGY
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 0 |  |  | -0.0039 |  |  | 0 |  | 1 | NEWENERGY | T157
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 238 | 191.08 |  |  | -0.0039 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00389 |  |  | 0.04435 |  | 1 | CAPACITY | LIBERTY EDDY
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 0 |  |  | -0.00389 |  |  | 0 |  | 1 | NEWENERGY | AC1-105
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 36.61 |  |  | -0.0039 |  |  | 0.10478 |  | 1 | CAPACITY
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 27.7 |  |  | -0.00389 |  |  | 0 |  | 1 | CAPACITY | AC1-105
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 16.46 |  |  | -0.0039 |  |  | 0 |  | 1 | CAPACITY | T157
315616 | AA1-038 C | 230 | 345 | 74 | 0 | 76.6 | 0 |  |  | -0.00392 |  |  | 0 |  | 1 | NEW | AA1-038
918232 | AA1-038 E | 230 | 345 | 74 | 0 | 66.7 | 0 |  |  | -0.00392 |  |  | 0 |  | 1 | NEWENERGY | AA1-038
314860 | 4E MILL | 138 | 345 | 2 | 0 | 50 | 0 |  |  | -0.00392 |  |  | 0.10478 |  | 1 | ENERGY
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 20.23 |  |  | -0.00392 |  |  | 0.10478 |  | 1 | CAPACITY
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 20.15 |  |  | -0.00392 |  |  | 0.10478 |  | 1 | CAPACITY
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00392 |  |  | 0 |  | 1 | CAPACITY
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 404.48 |  |  | -0.00393 |  |  | 0.0316 |  | 1 | CAPACITY
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 403.68 |  |  | -0.00393 |  |  | 0.0316 |  | 1 | CAPACITY
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 403.27 |  |  | -0.00393 |  |  | 0.0316 |  | 1 | CAPACITY
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 403.2 |  |  | -0.00393 |  |  | 0.0316 |  | 1 | CAPACITY
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00393 |  |  | 0.0316 |  | 1 | CAPACITY
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00393 |  |  | 0.0316 |  | 1 | CAPACITY
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 0 |  |  | -0.00394 |  |  | 0 |  | 1 | NEWENERGY | K11
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 30.67 |  |  | -0.00394 |  |  | 0 |  | 1 | CAPACITY | K11
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 443.98 |  |  | -0.00395 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM2
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 440.13 |  |  | -0.00395 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 419.81 |  |  | -0.00395 |  |  | 0.10478 |  | 1 | CAPACITY
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 9.55 |  |  | -0.00395 |  |  | 0.08446 |  | 1 | CAPACITY
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | AC1-075
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 30.75 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | AC1-075
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | AC1-080
926023 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 10.28 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | AC1-080
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 68.3 |  |  |  | -0.004
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 23.68 |  |  | -0.00401 |  |  | 0.12623 |  | 1 | CAPACITY
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 106.94 |  |  | -0.00405 |  |  | 0.07484 |  | 1 | CAPACITY
208904 | HOLT 696 | 13.2 | 229 | 60 | 23 | 58.4 | 46.89 |  |  | -0.00405 |  |  | 0.07484 |  | 1 | CAPACITY
208903 | HOLT 695 | 13.2 | 229 | 60 | 26 | 53.2 | 42.71 |  |  | -0.00405 |  |  | 0.07484 |  | 1 | CAPACITY
919535 | V4-027 E | 0 | 229 | 75 | 0 | 3.1 | 0 |  |  | -0.00405 |  |  | 0 |  | 1 | NEWENERGY | V4-027
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 3.93 |  |  | -0.00405 |  |  | 0 |  | 1 | CAPACITY | V4-027
208474 | KINZ 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00405 |  |  | 0 |  | 1 | CAPACITY
244012 | 05PINNACLE | 4 | 205 | 1 | 0 | 11 | 0 |  |  | -0.00408 |  |  | 0.10478 |  | 1 | ENERGY
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 42.07 |  |  | -0.00408 |  |  | 0.10478 |  | 1 | CAPACITY
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00409 |  |  | 0 |  | 1 | NEWENERGY | AC1-145
926645 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.00409 |  |  | 0 |  | 1 | CAPACITY | AC1-145
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.9 | 40.06 |  |  | -0.0041 |  |  | 0.07484 |  | 1 | CAPACITY
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 1044 |  |  |  | -0.0041
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 154.95 |  |  | -0.00412 |  |  | 0.0316 |  | 1 | CAPACITY
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 152.54 |  |  | -0.00412 |  |  | 0.0316 |  | 1 | CAPACITY
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 97.14 |  |  | -0.00412 |  |  | 0.0316 |  | 1 | CAPACITY
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 59.41 |  |  | -0.00412 |  |  | 0.0316 |  | 1 | CAPACITY
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 57 |  |  | -0.00412 |  |  | 0.0316 |  | 1 | CAPACITY
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 3.21 |  |  | -0.00413 |  |  | 0 |  | 1 | CAPACITY
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00418 |  |  | 0 |  | 1 | NEWENERGY | AC1-117
926461 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00418 |  |  | 0 |  | 1 | NEW | AC1-117
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 144.51 |  |  | -0.00418 |  |  | 0.10478 |  | 1 | CAPACITY
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | -0.00418 |  |  | 0.05 |  | 1 | MTX | AA1-100
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 6.42 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00423 |  |  | 0 |  | 1 | NEWENERGY | AD1-018
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.00423 |  |  | 0 |  | 1 | NEW | AD1-018
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00424 |  |  | 0.07484 |  | 1 | CAPACITY
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00424 |  |  | 0.07484 |  | 1 | CAPACITY
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00424 |  |  | 0 |  | 1 | CAPACITY | N47
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 0 |  |  | -0.00425 |  |  | 0 |  | 1 | NEWENERGY | U2-073 A
235520 | 01WVACO_S38 | 13.8 | 201 | 2 | 0 | 60 | 0 |  |  | -0.00424 |  |  | 0 |  | 1 | NEW
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 0 |  |  | -0.00425 |  |  | 0 |  | 1 | NEWENERGY | U2-073 B
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 25.9 | 20.79 |  |  | -0.00425 |  |  | 0 |  | 1 | CAPACITY | U2-073 A
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00425 |  |  | 0 |  | 1 | CAPACITY | U2-073 B
270148 | AE1-018 E | 138 | 205 | 75 | 0 | 2.2 | 0 |  |  | -0.00426 |  |  | 0 |  | 1 | NEWENERGY | AE1-018
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 3.29 |  |  | -0.00425 |  |  | 0 |  | 1 | CAPACITY
270147 | AE1-018 C | 138 | 205 | 75 | 0 | 2.8 | 2.25 |  |  | -0.00426 |  |  | 0 |  | 1 | CAPACITY | AE1-018
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 0 |  |  | -0.00427 |  |  | 0 |  | 1 | NEWENERGY | S14
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 11.24 |  |  | -0.00427 |  |  | 0 |  | 1 | CAPACITY | S14
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00428 |  |  | 0 |  | 1 | MTX | AD2-205
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 14.1 | 11.32 |  |  | -0.00428 |  |  | 0.07484 |  | 1 | CAPACITY
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.7 | 7.79 |  |  | -0.00428 |  |  | 0 |  | 1 | CAPACITY
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 0 |  |  | -0.00428 |  |  | 0 |  | 1 | NEWENERGY | Y1-006
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 0 |  |  | -0.00429 |  |  | 0 |  | 1 | NEWENERGY | U2-030
913034 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 0 |  |  | -0.00428 |  |  | 0 |  | 1 | NEW | Y1-006
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | -0.00428 |  |  | 0.07484 |  | 1 | ENERGY
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 6.26 |  |  | -0.00429 |  |  | 0 |  | 1 | CAPACITY | U2-030
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 0 |  |  | -0.0043 |  |  | 0 |  | 1 | NEWENERGY | AC1-048
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 0 |  |  | -0.0043 |  |  | 0 |  | 1 | NEW | AC1-048
205910 | AC2-053 E | 0.39 | 227 | 74 | 0 | 12.4 | 0 |  |  | -0.0043 |  |  | 0 |  | 1 | NEWENERGY | AC2-053
205909 | AC2-053 C | 0.39 | 227 | 74 | 0 | 7.6 | 0 |  |  | -0.0043 |  |  | 0 |  | 1 | NEW | AC2-053
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00433 |  |  | 0.08446 |  | 1 | CAPACITY
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00433 |  |  | 0.08446 |  | 1 | CAPACITY
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00433 |  |  | 0.08446 |  | 1 | CAPACITY
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00433 |  |  | 0.08446 |  | 1 | CAPACITY
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00433 |  |  | 0.08446 |  | 1 | CAPACITY
242677 | 05INDDRV | 138 | 205 | 64 | 0 | 45 | 36.13 |  |  | -0.00433 |  |  | 0.12623 |  | 1 | CAPACITY
923772 | AB2-011 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00433 |  |  | 0 |  | 1 | NEWENERGY | AB2-011
923771 | AB2-011 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00433 |  |  | 0 |  | 1 | NEW | AB2-011
923762 | AB2-010 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00433 |  |  | 0 |  | 1 | NEWENERGY | AB2-010
923761 | AB2-010 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00433 |  |  | 0 |  | 1 | NEW | AB2-010
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  |  |  | -0.0043
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  |  |  | -0.0043
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 489.98 |  |  | -0.00434 |  |  | 0.10478 |  | 1 | CAPACITY
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 127.4 | 102.28 |  |  | -0.00434 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 101.08 |  |  | -0.00434 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 106.7 | 85.67 |  |  | -0.00434 |  |  | 0 |  | 1 | CAPACITY
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 84.78 |  |  | -0.00434 |  |  | 0 |  | 1 | CAPACITY
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 38 |  |  |  | -0.0044
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 1.3 | 1.04 |  |  | -0.00438 |  |  | 0 |  | 1 | CAPACITY
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 0 |  |  | -0.00438 |  |  | 0 |  | 1 | NEWENERGY | K28
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 0 |  |  | -0.00438 |  |  | 0 |  | 1 | NEWENERGY | K28
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.4 | 13.97 |  |  | -0.00438 |  |  | 0 |  | 1 | CAPACITY | K28
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 896 |  |  |  | -0.0044
342442 | 2W GLASGOW | 69 | 320 | 2 | 0 | 1 | 0.8 |  |  | -0.0044 |  |  | 0 |  | 1 | CAPACITY
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 180.64 |  |  | -0.0044 |  |  | 0.10478 |  | 1 | CAPACITY
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 93.13 |  |  | -0.0044 |  |  | 0.10478 |  | 1 | CAPACITY
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 64.23 |  |  | -0.0044 |  |  | 0.07484 |  | 1 | CAPACITY
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 56.2 |  |  | -0.00441 |  |  | 0.07484 |  | 1 | CAPACITY
342070 | 2PINE GROVE | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00441 |  |  | 0 |  | 1 | CAPACITY
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00441 |  |  | 0.07484 |  | 1 | CAPACITY
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00442 |  |  | 0.07484 |  | 1 | CAPACITY
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00441 |  |  | 0 |  | 1 | CAPACITY
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 0 |  |  | -0.00442 |  |  | 0 |  | 1 | NEWENERGY | M24
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 0 |  |  | -0.00442 |  |  | 0 |  | 1 | NEWENERGY | AB1-150
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | -0.00442 |  |  | 0.05 |  | 1 | MTX | M24 BAT
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 91.93 |  |  | -0.00443 |  |  | 0.07484 |  | 1 | CAPACITY
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 61.42 |  |  | -0.00443 |  |  | 0.07484 |  | 1 | CAPACITY
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00442 |  |  | 0 |  | 1 | CAPACITY | M24
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00443 |  |  | 0 |  | 1 | NEWENERGY | W1-127
931011 | AB1-150 C | 138 | 201 | 74 | 0 | 6.7 | 5.38 |  |  | -0.00442 |  |  | 0 |  | 1 | CAPACITY | AB1-150
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0 |  |  | -0.00443 |  |  | 0 |  | 1 | NEWENERGY | U2-059
925462 | AC1-018 E | 34.5 | 228 | 75 | 0 | 0.9 | 0 |  |  | -0.00443 |  |  | 0 |  | 1 | NEWENERGY | AC1-018
925461 | AC1-018 C | 34.5 | 228 | 75 | 0 | 0.5 | 0 |  |  | -0.00443 |  |  | 0 |  | 1 | NEW | AC1-018
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00443 |  |  | 0 |  | 1 | CAPACITY | W1-127
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00443 |  |  | 0 |  | 1 | CAPACITY | U2-059
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 244.87 |  |  | -0.00444 |  |  | 0.10478 |  | 1 | CAPACITY
247225 | 05FTHLG2 | 18 | 205 | 57 | 120 | 173.8 | 139.54 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247224 | 05FTHLG1 | 18 | 205 | 57 | 120 | 173.7 | 139.46 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247232 | 05RIVRG3 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247230 | 05RIVRG1 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247231 | 05RIVRG2 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.55 |  |  | -0.00443 |  |  | 0 |  | 1 | CAPACITY
918472 | AA1-062 E | 138 | 201 | 74 | 0 | 195 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | NEWENERGY | AA1-062
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 642.29 |  |  | -0.00445 |  |  | 0.10478 |  | 1 | CAPACITY
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00445 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00445 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 2
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
292981 | N-007 E | 138 | 201 | 74 | 0 | 30.4 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | NEWENERGY | N07
235801 | 01WM_AA1_062 | 138 | 201 | 74 | 0 | 29 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | NEW | AA1-062
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 109.5 | 87.91 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
920072 | AA2-103 E | 138 | 201 | 76 | -20 | 20 | 0 |  |  | -0.00445 |  |  | 0.05 |  | 1 | MTX | AA2-103
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 60.94 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 60.78 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 60.7 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 60.53 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 72.9 | 58.53 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 72.6 | 58.29 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00444 |  |  | 0.08446 |  | 1 | CAPACITY
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 11.88 |  |  | -0.00445 |  |  | 0.07484 |  | 1 | CAPACITY
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | MTX | AB1-055
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | K19
235000 | N-007 C | 138 | 201 | 74 | 0 | 7.6 | 6.1 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | N07
341329 | 2COLESBURG | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1067.8 |  |  | -0.00445 |  |  | 0.10478 |  | 1 | CAPACITY | AMG3
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  |  |  | -0.0045
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 642.29 |  |  | -0.00445 |  |  | 0.10478 |  | 1 | CAPACITY
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | NEWENERGY | P59
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 0 |  |  | -0.00446 |  |  | 0 |  | 1 | NEWENERGY | U2-061
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 152 | 122.03 |  |  | -0.00446 |  |  | 0.08446 |  | 1 | CAPACITY
206341 | 28GIL 8 | 13.8 | 228 | 58 | 69.9 | 90 | 72.26 |  |  | -0.00446 |  |  | 0.04435 |  | 1 | CAPACITY | GILBERT
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00445 |  |  | 0.08446 |  | 1 | CAPACITY
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 87 | 100 | 87.11 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY | GILBERT
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 85.3 | 98 | 85.37 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY | GILBERT
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | -0.0045
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.00446 |  |  | 0 |  | 1 | NEWENERGY | W3-077
925972 | AC1-073 E | 138 | 201 | 74 | 0 | 5.9 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | NEWENERGY | AC1-073
925971 | AC1-073 C | 138 | 201 | 74 | 0 | 5.8 | 0 |  |  | -0.00445 |  |  | 0 |  | 1 | NEW | AC1-073
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 9.39 |  |  | -0.00445 |  |  | 0 |  | 1 | CAPACITY | P59
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 5.22 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY | U2-061
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 5.7 | 4.58 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY | W3-077
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY | W2-091
342031 | 2PACTOLUS | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 62.8 |  |  |  | -0.0045
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 55 | 44.16 |  |  | -0.00446 |  |  | 0.10478 |  | 1 | CAPACITY
341200 | 2BROMLEYEK | 69 | 320 | 2 | 0 | 2 | 1.61 |  |  | -0.00447 |  |  | 0 |  | 1 | CAPACITY
237085 | AD2-192 GEN | 23 | 201 | 57 | 0 | 600 | 0 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | NEW
293798 | W4-005 E | 0.69 | 222 | 74 | 0 | 305.37 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | W4-005
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1396 | 1120.79 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | GVG2
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1371 | 1100.72 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | GVG1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1088.67 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | RKG1
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1043.71 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | RKG2
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | X2-022
274663 | QUAD CITI;2U | 18 | 222 | 48 | 150 | 911.7 | 731.97 |  |  | -0.00448 |  |  | 0.01494 |  | 1 | CAPACITY
274662 | QUAD CITI;1U | 18 | 222 | 48 | 150 | 911.1 | 731.48 |  |  | -0.00448 |  |  | 0.01494 |  | 1 | CAPACITY
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00447 |  |  | 0.10478 |  | 1 | CAPACITY
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00447 |  |  | 0.10478 |  | 1 | CAPACITY
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | W2-048
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 144.51 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00448 |  |  | 0.04435 |  | 1 | CAPACITY | CORDOVA
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 77.88 |  |  | -0.00447 |  |  | 0.07484 |  | 1 | CAPACITY
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 52.91 |  |  | -0.00447 |  |  | 0.07484 |  | 1 | CAPACITY
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 51.78 |  |  | -0.00447 |  |  | 0.07484 |  | 1 | CAPACITY
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 51.38 |  |  | -0.00447 |  |  | 0.07484 |  | 1 | CAPACITY
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 36.61 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | W4-005
341584 | 2GRIFFIN | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1356 | 1088.67 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | MTG1
274656 | BYRON ;1U | 25 | 222 | 45 | 700 | 1168.5 | 938.14 |  |  | -0.00449 |  |  | 0.01494 |  | 1 | CAPACITY
274657 | BYRON ;2U | 25 | 222 | 45 | 700 | 1141.5 | 916.46 |  |  | -0.00449 |  |  | 0.01494 |  | 1 | CAPACITY
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 200 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | Q57
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | Z2-087
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | S28
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | S27
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 124 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | ENERGY | L05_CE22
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 409.46 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | P36 2
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | P36 1
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | AC1-089
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | O29 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | P26
293516 | O-009 E1 | 0.69 | 222 | 74 | 0 | 82.04 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | O09 1
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | P11 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | P11 2
294763 | P-046 E | 12 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | P46
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | O35
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 240.86 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | O29 2
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | NQ71
293518 | O-009 E3 | 0.57 | 222 | 74 | 0 | 45.89 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | O09 3
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 45.5 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | Z1-073
916211 | Z1-072 E | 0.6 | 222 | 74 | 0 | 44.8 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | Z1-072
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | O29 3
293517 | O-009 E2 | 0.6 | 222 | 74 | 0 | 41.67 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | O09 2
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 136.16 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | NELSON
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 135.12 |  |  | -0.00448 |  |  | 0.04435 |  | 1 | CAPACITY | NELSON
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 134.32 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 134.16 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 31.5 |  |  |  | -0.0045
919221 | AA1-146 | 345 | 222 | 58 | 0 | 157 | 126.05 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CLIF1
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CLIF3
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CLIF5
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CLIF4
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF2
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CLIF6
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 99.47 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | NELSON
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 98.59 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | NELSON
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 0 |  |  | -0.00448 |  |  | 0 |  | 1 | NEWENERGY | NQ72
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00449 |  |  | 0.05 |  | 1 | MTX | AA2-123
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 133.1 | 153 | 133.28 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 129.7 | 149.1 | 129.88 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 128.6 | 147.8 | 128.75 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 67.52 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | CLIF2
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF6
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF1
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF3
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF4
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00448 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF5
926103 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 45.76 |  |  | -0.00449 |  |  | 0.05 |  | 1 | NEW | AC1-089
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 36.93 |  |  | -0.00448 |  |  | 0.07484 |  | 1 | CAPACITY
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Q57
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 28.74 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | S28
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 27.94 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | S27
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | L05_CE22
274889 | BRIGHTSTK;1U | 0.7 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Z2-087
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | O29 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 17.58 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | P26
293513 | O-009 C1 | 0.69 | 222 | 74 | 0 | 20.5 | 16.46 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | O09 1
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | P11 2
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | P11 1
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 15.58 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | P46
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | P36 2
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | P36 1
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Z1-073
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 9.64 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | O29 2
293515 | O-009 C3 | 0.57 | 222 | 74 | 0 | 11.5 | 9.23 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | O09 3
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 8.91 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | O29 3
293514 | O-009 C2 | 0.6 | 222 | 74 | 0 | 10.4 | 8.35 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | O09 2
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 10.3 | 8.27 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | O35
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 10 | 8.03 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Z1-072
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.6 | 7.71 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY
295108 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 5.7 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | NQ71
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY
342550 | 4BAVARIAN LF | 138 | 320 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY
295110 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 2.57 |  |  | -0.00448 |  |  | 0 |  | 1 | CAPACITY | NQ72
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 949.78 |  |  | -0.0045 |  |  | 0.01494 |  | 1 | CAPACITY
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 926.5 |  |  | -0.0045 |  |  | 0.01494 |  | 1 | CAPACITY
274661 | LASCO STA;2U | 25 | 222 | 49 | 150 | 1135.9 | 911.97 |  |  | -0.0045 |  |  | 0.01494 |  | 1 | CAPACITY
274660 | LASCO STA;1U | 25 | 222 | 49 | 150 | 1131.2 | 908.19 |  |  | -0.0045 |  |  | 0.01494 |  | 1 | CAPACITY
274658 | DRESDEN ;2U | 18 | 222 | 48 | 150 | 902.5 | 724.58 |  |  | -0.0045 |  |  | 0.01494 |  | 1 | CAPACITY
274659 | DRESDEN ;3U | 18 | 222 | 48 | 150 | 895.5 | 718.96 |  |  | -0.00449 |  |  | 0.01494 |  | 1 | CAPACITY
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | O50
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Q01 3
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | O22 2
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | P10
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 589.3 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | ZIMM
293799 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | S36
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | S37
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 570.03 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | AA1-018
235587 | 01HARRN3 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
235586 | 01HARRN2 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
235585 | 01HARRN1 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Q01 4
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | O51 2
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | O51 1
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | N15
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 470.47 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | ZIMM
927091 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-204
927093 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | AC1-204
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 415.88 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 415.88 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
274687 | WILL CNTY;4U | 20 | 222 | 15 | 0 | 510 | 409.46 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY | WILL4
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Q01 21
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 81.6 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | O22 1
247903 | 05FR-22G E | 0.69 | 205 | 75 | 0 | 78.8 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Q01 22
247900 | 05FR-11G E | 0.6 | 205 | 75 | 0 | 78.3 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Q01 11
930062 | AB1-014 E | 138 | 212 | 75 | 0 | 77.5 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | AB1-014
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 522.66 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Q01 12
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 284.53 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK8
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 263.34 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK7
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.00449 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-169
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 294 | 236.04 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-079
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 225.6 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | AB1-169
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 219 | 175.82 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Z1-079
274708 | KENDALL ;3C | 18 | 222 | 58 | 140 | 184.3 | 147.97 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 3
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 146.36 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 2
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 146.36 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 138 | 182.3 | 146.36 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 4
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00449 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 2
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00449 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 1
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 132.47 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | ENERGY
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 99.72 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | KYG1
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | KYG2
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | KYG5
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | KYG3
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | KYG4
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 97.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Kendall 2
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 97.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Kendall 1
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 97.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Kendall 4
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 97.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Kendall 3
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 96.42 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 115.4 | 92.65 |  |  | -0.00449 |  |  | 0.04435 |  | 1 | CAPACITY | EQUISTAR MORRIS
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 75.6 | 104 | 83.5 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 72.7 | 101.6 | 81.57 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00449 |  |  | 0.05 |  | 1 | MTX | Z1-108
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.0045 |  |  | 0.05 |  | 1 | MTX | Z1-107
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 80.93 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 71.2 | 100.6 | 80.77 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 80.21 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
243415 | 05WWVSTA | 69 | 205 | 61 | 60 | 96 | 77.08 |  |  | -0.0045 |  |  | 0.07484 |  | 1 | CAPACITY
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 65.51 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 81.5 | 65.43 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.8 | 64.87 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 64.31 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 62.14 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
250166 | HLCRST AB114 | 138 | 212 | 75 | 0 | 76 | 61.02 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | AB1-014
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 58.77 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 58.45 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | KYG1
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | KYG3
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | KYG4
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | KYG5
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00449 |  |  | 0.10478 |  | 1 | CAPACITY | KYG2
251953 | 08MADSN2 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251954 | 08MADSN3 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251952 | 08MADSN1 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251957 | 08MADSN6 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251956 | 08MADSN5 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251955 | 08MADSN4 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251959 | 08MADSN8 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251958 | 08MADSN7 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 56.84 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 55.4 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251828 | CLNTESP1 | 34.5 | 212 | 76 | 0 | 12 | 0 |  |  | -0.00449 |  |  | 0.05 |  | 1 | MTX | Z1-080
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 43.03 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00449 |  |  | 0.05 |  | 1 | MTX | Z1-106
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00449 |  |  | 0.05 |  | 1 | MTX | Z1-106
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 40.54 |  |  | -0.0045 |  |  | 0.04435 |  | 1 | CAPACITY | MIDDLETOWN COKE
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | O50
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00449 |  |  | 0.07484 |  | 1 | CAPACITY
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00449 |  |  | 0.07484 |  | 1 | CAPACITY
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00449 |  |  | 0.07484 |  | 1 | CAPACITY
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 28.18 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | O22 2
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | S37
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | S36
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -0.00449 |  |  | 0.05 |  | 1 | MTX | Z1-065
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 24.08 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 23.36 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Q01 4
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 20.3 | 27.6 | 22.16 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 22 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | N15
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 21.68 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 20.63 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Q01 11
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 20.07 |  |  | -0.00449 |  |  | 0.08446 |  | 1 | CAPACITY
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | O51 2
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | O51 1
274891 | OTTER CRK;1U | 0.69 | 222 | 74 | 0 | 19.5 | 15.66 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | AA1-018
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 14.77 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | O22 1
276173 | Z2-081 | 138 | 222 | 2 | 0 | 13.3 | 10.68 |  |  | -0.00449 |  |  | 0.12623 |  | 1 | CAPACITY
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Q01 21
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Q01 22
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 10.36 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Q01 12
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Q01 3
904211 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 9.71 |  |  | -0.00449 |  |  | 0.07484 |  | 1 | CAPACITY
904201 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 8.51 |  |  | -0.0045 |  |  | 0.07484 |  | 1 | CAPACITY
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 8.19 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | P10
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | MTX | Y3-099
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | MTX | Y3-100
276159 | W4-082 | 138 | 222 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.8 | 3.85 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY
930042 | AB1-006 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | AB1-006
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | U3-002 2
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | U2-090
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | V3-007
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 159.7 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | S06
253317 | AC1-085 B_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 B
253314 | AC1-085 A_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 A
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 443.18 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 437.96 |  |  | -0.0045 |  |  | 0.10478 |  | 1 | CAPACITY
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 80 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | T126 3
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 80 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | T127 4
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 80 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | T126 2
247943 | T-127 E | 0.74 | 205 | 74 | 0 | 80 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | T127 5
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 131.75 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 130.06 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
276592 | O-012 C | 138 | 222 | 64 | 0 | 20 | 0 |  |  | -0.0045 |  |  | 0.12623 |  | 1 | ENERGY
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | AC1-085 A
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | AC1-085 B
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEWENERGY | W3-044
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 37.49 |  |  | -0.00451 |  |  | 0.07484 |  | 1 | CAPACITY
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 42.68 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 42.6 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 42.51 |  |  | -0.0045 |  |  | 0.08446 |  | 1 | CAPACITY
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | X3-005
930041 | AB1-006 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | AB1-006
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | U2-090
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | V3-007
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 20.79 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | S06
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 16.22 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | T127 5
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 12.28 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | T126 3
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 12.2 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | T126 2
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 10.6 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | U3-002 1
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 10.28 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | U3-002 2
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 9.47 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | T127 4
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY | W3-044
247968 | Z2-115 E | 12 | 205 | 74 | 0 | 1.25 | 0 |  |  | -0.0045 |  |  | 0 |  | 1 | NEWENERGY | Z2-115
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 2.73 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | X3-005
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 1 |  |  | -0.0045 |  |  | 0 |  | 1 | CAPACITY | Z2-115
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1402 |  |  |  | -0.0045
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1148 | 921.68 |  |  | -0.00452 |  |  | 0.01494 |  | 1 | CAPACITY
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEWENERGY | AC2-176
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEWENERGY | S71
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 268.96 |  |  | -0.00452 |  |  | 0.08446 |  | 1 | CAPACITY
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 201.52 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY | X2-052
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 193.49 |  |  | -0.00452 |  |  | 0.08446 |  | 1 | CAPACITY
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00452 |  |  | 0.04435 |  | 1 | CAPACITY | X2-052
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY | X2-052
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 0 |  |  | -0.00452 |  |  | 0 |  | 1 | NEWENERGY | AC2-067
902531 | W2-040 C | 69 | 209 | 75 | 0 | 20 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEW | W2-040
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 80.69 |  |  | -0.00451 |  |  | 0.08446 |  | 1 | CAPACITY
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 64.23 |  |  | -0.00452 |  |  | 0.10478 |  | 1 | CAPACITY
902532 | W2-040 E | 69 | 209 | 75 | 0 | 12.4 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEWENERGY | W2-040
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 48.09 |  |  | -0.00451 |  |  | 0.08446 |  | 1 | CAPACITY
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 47.93 |  |  | -0.00451 |  |  | 0.08446 |  | 1 | CAPACITY
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 46.65 |  |  | -0.00451 |  |  | 0.08446 |  | 1 | CAPACITY
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 46.41 |  |  | -0.00451 |  |  | 0.08446 |  | 1 | CAPACITY
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 21.28 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY | AC2-067
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 19.27 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY | S71
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 22.91 |  |  | -0.00451 |  |  | 0.08446 |  | 1 | CAPACITY
933594 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 13.57 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY | AC2-176
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00452 |  |  | 0.12623 |  | 1 | CAPACITY
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 8.03 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEWENERGY | V4-073
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.76 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY
904721 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY | V4-073
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 814.5 |  |  | -0.00453 |  |  | 0.01494 |  | 1 | CAPACITY
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | AA2-116
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00453 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-116
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 267.35 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | AA2-116
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 162.9 |  |  | -0.00452 |  |  | 0.08446 |  | 1 | CAPACITY
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00453 |  |  | 0 |  | 1 | NEWENERGY | AC1-166
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00453 |  |  | 0 |  | 1 | NEWENERGY | AC1-165
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00453 |  |  | 0 |  | 1 | NEWENERGY | AC1-069
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00453 |  |  | 0 |  | 1 | NEWENERGY | AC1-068
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | AC1-068
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | AC1-069
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | AC1-166
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | AC1-165
247969 | Z2-116 E | 138 | 205 | 76 | 0 | 1.3 | 0 |  |  | -0.00452 |  |  | 0 |  | 1 | NEWENERGY | Z2-116
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 4.82 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 3.13 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.8 | 2.25 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 2.09 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.5 | 1.2 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY | Z2-116
927184 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -0.00454 |  |  | 0.05 |  | 1 | MTX | AC1-212
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00453 |  |  | 0.08446 |  | 1 | CAPACITY
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00453 |  |  | 0.08446 |  | 1 | CAPACITY
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00453 |  |  | 0.08446 |  | 1 | CAPACITY
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 65.03 |  |  | -0.00453 |  |  | 0.08446 |  | 1 | CAPACITY
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 64.23 |  |  | -0.00453 |  |  | 0.08446 |  | 1 | CAPACITY
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 63.43 |  |  | -0.00453 |  |  | 0.08446 |  | 1 | CAPACITY
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00454 |  |  | 0.12623 |  | 1 | CAPACITY
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0 |  |  | -0.00453 |  |  | 0 |  | 1 | NEWENERGY | Z2-113
AC1-212 | BATTERY_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | -0.0045
247604 | X1-042 | 12 | 205 | 64 | 0 | 3 | 2.41 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 1.85 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | Z2-113
927183 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.53 |  |  | -0.00454 |  |  | 0 |  | 1 | CAPACITY | AC1-212
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 120.8 | 0 |  |  | -0.00455 |  |  | 0 |  | 1 | NEWENERGY | R49
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 0 |  |  | -0.00454 |  |  | 0 |  | 1 | NEWENERGY | T131
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 0 |  |  | -0.00454 |  |  | 0 |  | 1 | NEWENERGY | AC1-173
247530 | 05COVRT3 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00454 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 3
247528 | 05COVRT1 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00454 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 1
247529 | 05COVRT2 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00454 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 2
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00455 |  |  | 0.08446 |  | 1 | CAPACITY
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00455 |  |  | 0.08446 |  | 1 | CAPACITY
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00455 |  |  | 0.08446 |  | 1 | CAPACITY
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00455 |  |  | 0.08446 |  | 1 | CAPACITY
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 120.19 |  |  | -0.00455 |  |  | 0.08446 |  | 1 | CAPACITY
247531 | 05COVRT4 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00454 |  |  | 0 |  | 1 | CAPACITY | Covert 1
247533 | 05COVRT6 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00454 |  |  | 0 |  | 1 | CAPACITY | Covert 3
247532 | 05COVRT5 | 16.5 | 205 | 58 | 90 | 131.2 | 105.33 |  |  | -0.00454 |  |  | 0 |  | 1 | CAPACITY | Covert 2
932312 | AC2-045 E | 69 | 205 | 75 | 0 | 6.2 | 0 |  |  | -0.00454 |  |  | 0 |  | 1 | NEWENERGY | AC2-045
247521 | T131 | 0.69 | 205 | 74 | 22.4 | 30 | 24.08 |  |  | -0.00454 |  |  | 0 |  | 1 | CAPACITY | T131
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 18.39 |  |  | -0.00455 |  |  | 0 |  | 1 | CAPACITY | R49
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00455 |  |  | 0.07484 |  | 1 | CAPACITY
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00455 |  |  | 0.07484 |  | 1 | CAPACITY
932311 | AC2-045 C | 69 | 205 | 75 | 0 | 3.8 | 0 |  |  | -0.00454 |  |  | 0 |  | 1 | NEW | AC2-045
926865 | AC1-173 C | 0.65 | 205 | 75 | 0 | 9.9 | 7.95 |  |  | -0.00454 |  |  | 0 |  | 1 | CAPACITY | AC1-173
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 94.4 | 0 |  |  | -0.00456 |  |  | 0 |  | 1 | NEWENERGY | R60 3
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00456 |  |  | 0 |  | 1 | NEWENERGY | R60 2
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00456 |  |  | 0 |  | 1 | NEWENERGY | R60 1
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00455 |  |  | 0 |  | 1 | NEWENERGY | V1-011
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 13.25 |  |  | -0.00456 |  |  | 0 |  | 1 | CAPACITY | R60 3
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00456 |  |  | 0 |  | 1 | CAPACITY | R60 2
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00456 |  |  | 0 |  | 1 | CAPACITY | R60 1
247607 | V1-011 C | 34.5 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00455 |  |  | 0 |  | 1 | CAPACITY | V1-011
294740 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -0.00455 |  |  | 0 |  | 1 | ENERGY
903052 | W2-094 E | 115 | 227 | 75 | 0 | 1.9 | 0 |  |  | -0.00456 |  |  | 0 |  | 1 | NEWENERGY | W2-094
205911 | 27W2-094 | 115 | 227 | 75 | 0 | 1.1 | 0 |  |  | -0.00456 |  |  | 0 |  | 1 | NEWENERGY | W2-094
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00457 |  |  | 0 |  | 1 | NEWENERGY | U2-072
247919 | U2-041 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00457 |  |  | 0 |  | 1 | NEWENERGY | U2-041
247506 | U2-041 C | 345 | 205 | 74 | 0 | 39 | 0 |  |  | -0.00457 |  |  | 0 |  | 1 | CAPACITY | U2-041
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00457 |  |  | 0 |  | 1 | NEWENERGY | V3-028
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 31.31 |  |  | -0.00457 |  |  | 0 |  | 1 | CAPACITY | U2-072
247549 | V3-028 C | 345 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00457 |  |  | 0 |  | 1 | CAPACITY | V3-028
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00456 |  |  | 0 |  | 1 | MTX
208876 | WLAN | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00457 |  |  | 0 |  | 1 | CAPACITY
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00458 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-067
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00458 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-044
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00458 |  |  | 0 |  | 1 | CAPACITY | AB2-067
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 292.88 |  |  | -0.00458 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00458 |  |  | 0.04435 |  | 1 | CAPACITY | WATERFORD
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00458 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00458 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00458 |  |  | 0 |  | 1 | NEWENERGY | W4-073
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.00458 |  |  | 0 |  | 1 | CAPACITY
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 238.45 |  |  | -0.00459 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00459 |  |  | 0.04435 |  | 1 | CAPACITY | WASHINGTON
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00459 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00459 |  |  | 0 |  | 1 | CAPACITY
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 618.28 |  |  | -0.00459 |  |  | 0.10478 |  | 1 | CAPACITY
893022 | V2-006 E | 138 | 205 | 74 | 0 | 130.5 | 0 |  |  | -0.00459 |  |  | 0 |  | 1 | NEWENERGY | V2-006
893021 | V2-006 C | 138 | 205 | 74 | 0 | 19.5 | 0 |  |  | -0.00459 |  |  | 0 |  | 1 | NEWENERGY | V2-006
208769 | SISO | 12.5 | 229 | 2 | 0 | 2.48 | 0 |  |  | -0.0046 |  |  | 0 |  | 1 | ENERGY
245413 | 05S FULTHA | 69 | 205 | 65 | 0 | 0.85 | 0 |  |  | -0.00459 |  |  | 0 |  | 1 | ENERGY
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 318.8 | 255.95 |  |  | -0.00461 |  |  | 0 |  | 1 | CAPACITY | RONCO
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 225.4 | 180.96 |  |  | -0.0046 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 0 |  |  | -0.0046 |  |  | 0 |  | 1 | NEWENERGY | U1-059
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00461 |  |  | 0 |  | 1 | CAPACITY | RONCO
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00461 |  |  | 0.04435 |  | 1 | CAPACITY | RONCO
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.0046 |  |  | 0.04435 |  | 1 | CAPACITY | DRESDEN
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.0046 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 0 |  |  | -0.0046 |  |  | 0 |  | 1 | NEWENERGY | W1-056
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 0 |  |  | -0.0046 |  |  | 0 |  | 1 | NEWENERGY | U1-059
930262 | AB1-065 E | 34.5 | 201 | 75 | 0 | 6.8 | 0 |  |  | -0.0046 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
235013 | 01AB1-065 C | 34.5 | 201 | 75 | 0 | 4.1 | 0 |  |  | -0.0046 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.93 |  |  | -0.0046 |  |  | 0 |  | 1 | CAPACITY | W1-056
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 533.66 |  |  | -0.00462 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-173
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.00461 |  |  | 0.08446 |  | 1 | CAPACITY
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.00461 |  |  | 0.08446 |  | 1 | CAPACITY
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.66 | 96.07 |  |  | -0.00461 |  |  | 0.08446 |  | 1 | CAPACITY
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 17.66 |  |  | -0.00461 |  |  | 0.08446 |  | 1 | CAPACITY
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 8.83 |  |  | -0.00461 |  |  | 0.10478 |  | 1 | CAPACITY
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 10.19 |  |  | -0.00464 |  |  | 0.10478 |  | 1 | CAPACITY
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00466 |  |  | 0.07484 |  | 1 | CAPACITY
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00466 |  |  | 0.07484 |  | 1 | CAPACITY
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 15.25 |  |  | -0.00466 |  |  | 0.07484 |  | 1 | CAPACITY
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 634.42 |  |  | -0.00467 |  |  | 0.10478 |  | 1 | CAPACITY
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00467 |  |  | 0 |  | 1 | NEWENERGY | U4-029
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00467 |  |  | 0 |  | 1 | NEWENERGY | U4-028
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00467 |  |  | 0.08446 |  | 1 | CAPACITY
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00467 |  |  | 0.10478 |  | 1 | CAPACITY
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00467 |  |  | 0.08446 |  | 1 | CAPACITY
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00467 |  |  | 0.10478 |  | 1 | CAPACITY
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 0 |  |  | -0.00467 |  |  | 0 |  | 1 | NEWENERGY
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00467 |  |  | 0 |  | 1 | NEW | U4-028
247552 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00467 |  |  | 0 |  | 1 | NEW | U4-029
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00467 |  |  | 0 |  | 1 | NEWENERGY | V4-010
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 261.89 |  |  | -0.00467 |  |  | 0 |  | 1 | CAPACITY | OREGON
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 248.73 |  |  | -0.00467 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00467 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00468 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-107
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00467 |  |  | 0 |  | 1 | CAPACITY | OREGON
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00467 |  |  | 0.04435 |  | 1 | CAPACITY | OREGON
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 109.19 |  |  | -0.00468 |  |  | 0.10478 |  | 1 | CAPACITY
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 0 |  |  | -0.00467 |  |  | 0 |  | 1 | NEW | V4-010
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00468 |  |  | 0.08446 |  | 1 | CAPACITY
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00468 |  |  | 0.08446 |  | 1 | CAPACITY
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 10.68 |  |  | -0.00468 |  |  | 0.10478 |  | 1 | CAPACITY
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 19.5 | 15.66 |  |  | -0.00469 |  |  | 0.08446 |  | 1 | CAPACITY
924440 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 389.39 |  |  | -0.0047 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-093
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 364.2 | 292.4 |  |  | -0.0047 |  |  | 0 |  | 1 | CAPACITY | FREMONT
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 170 | 136.49 |  |  | -0.0047 |  |  | 0.04435 |  | 1 | CAPACITY | FREMONT
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 166.4 | 133.6 |  |  | -0.0047 |  |  | 0 |  | 1 | CAPACITY | FREMONT
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 780.51 |  |  | -0.00471 |  |  | 0.01494 |  | 1 | CAPACITY
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00472 |  |  | 0.10478 |  | 1 | CAPACITY
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00472 |  |  | 0.10478 |  | 1 | CAPACITY
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 192.53 |  |  | -0.00472 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 160.57 |  |  | -0.00472 |  |  | 0.04435 |  | 1 | CAPACITY | LOWER MT BETHEL
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 160.57 |  |  | -0.00472 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 4.41 |  |  | -0.00473 |  |  | 0 |  | 1 | CAPACITY | N32
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | -0.00473 |  |  | 0 |  | 1 | NEW | AB1-069
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00473 |  |  | 0 |  | 1 | NEW | AB1-069
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00473 |  |  | 0.04435 |  | 1 | NEW | AB1-069
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 60 | 48.17 |  |  | -0.00474 |  |  | 0.08446 |  | 1 | CAPACITY
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 8.03 |  |  | -0.00473 |  |  | 0 |  | 1 | CAPACITY
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 7.95 |  |  | -0.00473 |  |  | 0 |  | 1 | CAPACITY
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 1.85 |  |  | -0.00477 |  |  | 0 |  | 1 | CAPACITY
936011 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 16.06 |  |  | -0.00478 |  |  | 0.10478 |  | 1 | CAPACITY
209030 | FRFA O01 | 12.5 | 229 | 2 | 0 | 3.2 | 0 |  |  | -0.0048 |  |  | 0 |  | 1 | NEW
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 11.24 |  |  | -0.00481 |  |  | 0.12623 |  | 1 | CAPACITY
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 0.4 | 0.32 |  |  | -0.0048 |  |  | 0 |  | 1 | CAPACITY | V3-051
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00482 |  |  | 0.10478 |  | 1 | CAPACITY
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 272 | 218.38 |  |  | -0.00483 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00483 |  |  | 0.04435 |  | 1 | CAPACITY | Y2-050
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00483 |  |  | 0 |  | 1 | CAPACITY | Y2-050
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 62.22 |  |  | -0.00483 |  |  | 0.08446 |  | 1 | CAPACITY
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00482 |  |  | 0.08446 |  | 1 | CAPACITY
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00483 |  |  | 0.08446 |  | 1 | CAPACITY
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 60.86 |  |  | -0.00483 |  |  | 0.08446 |  | 1 | CAPACITY
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 60.29 |  |  | -0.00483 |  |  | 0.08446 |  | 1 | CAPACITY
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 41.03 |  |  | -0.00482 |  |  | 0.12623 |  | 1 | CAPACITY
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 39.82 |  |  | -0.00482 |  |  | 0.12623 |  | 1 | CAPACITY
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 498.09 |  |  | -0.00483 |  |  | 0.10478 |  | 1 | CAPACITY
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00483 |  |  | 0.10478 |  | 1 | CAPACITY
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 503.47 |  |  | -0.00486 |  |  | 0.04435 |  | 1 | CAPACITY | AVON LAKE
237082 | AA2-121 | 345 | 201 | 58 | 0 | 830 | 666.37 |  |  | -0.00489 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-121
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 21 | 16.86 |  |  | -0.00489 |  |  | 0.12623 |  | 1 | CAPACITY
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0 |  |  | -0.0049 |  |  | 0 |  | 1 | NEWENERGY | W1-045
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.13 | 4.12 |  |  | -0.0049 |  |  | 0 |  | 1 | CAPACITY | W1-045
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 3.21 |  |  | -0.00489 |  |  | 0 |  | 1 | CAPACITY
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 81.57 |  |  | -0.00492 |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND
253970 | 15BI2 | 13.8 | 215 | 58 | 60 | 96.2 | 77.24 |  |  | -0.00492 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.7 | 39.1 |  |  | -0.00492 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0 |  |  | -0.00492 |  |  | 0 |  | 1 | NEWENERGY | AC2-168
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 14.53 |  |  | -0.00492 |  |  | 0.08446 |  | 1 | CAPACITY
933531 | AC2-168 C | 138 | 215 | 75 | 0 | 7.55 | 6.06 |  |  | -0.00492 |  |  | 0 |  | 1 | CAPACITY | AC2-168
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00492 |  |  | 0.10478 |  | 1 | CAPACITY
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00492 |  |  | 0.10478 |  | 1 | CAPACITY
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 455.62 |  |  | -0.00492 |  |  | 0.10478 |  | 1 | CAPACITY
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | AA1-123
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 233.87 |  |  | -0.00492 |  |  | 0.10478 |  | 1 | CAPACITY
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.00493 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-123
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00493 |  |  | 0.04435 |  | 1 | CAPACITY | Y3-103
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY | Y3-103
253900 | 15BVRVL1 | 22 | 215 | 44 | 843.9 | 970 | 844.97 |  |  | -0.00493 |  |  | 0.01494 |  | 1 | CAPACITY
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 783.39 |  |  | -0.00493 |  |  | 0.01494 |  | 1 | CAPACITY
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 300.6 | 241.34 |  |  | -0.00494 |  |  | 0 |  | 1 | CAPACITY | Z2-028
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00494 |  |  | 0 |  | 1 | CAPACITY | Z2-028
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00494 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-028
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.5 |  |  | -0.00493 |  |  | 0 |  | 1 | CAPACITY
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | -0.00494 |  |  | 0.10478 |  | 1 | ENERGY
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 24.6 | 19.75 |  |  | -0.00495 |  |  | 0.12623 |  | 1 | CAPACITY
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 0 |  |  | -0.00496 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 0 |  |  | -0.00496 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 329.17 |  |  | -0.00498 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00498 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00498 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-044
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 3.21 |  |  | -0.00498 |  |  | 0 |  | 1 | CAPACITY
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 16.46 |  |  | -0.005 |  |  | 0.12623 |  | 1 | CAPACITY
239023 | 02NWCAG4 | 14.4 | 202 | 58 | 20 | 92 | 73.86 |  |  | -0.00504 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 2.01 |  |  | -0.00504 |  |  | 0 |  | 1 | CAPACITY
239024 | 02NWCAG5 | 16.5 | 202 | 58 | 23 | 141 | 113.2 |  |  | -0.00504 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 1.37 |  |  | -0.00505 |  |  | 0 |  | 1 | CAPACITY | K20
239022 | 02NWCAG3 | 14.4 | 202 | 58 | 20 | 92.3 | 74.11 |  |  | -0.00505 |  |  | 0.04435 |  | 1 | CAPACITY | NEW CASTLE
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 19.6 | 15.74 |  |  | -0.00507 |  |  | 0.08446 |  | 1 | CAPACITY
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 261.73 |  |  | -0.00509 |  |  | 0 |  | 1 | CAPACITY | T-174
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00509 |  |  | 0 |  | 1 | CAPACITY | T-174
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00509 |  |  | 0.04435 |  | 1 | CAPACITY | T-174
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1086.27 |  |  | -0.0051 |  |  | 0.01494 |  | 1 | CAPACITY
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.82 |  |  | -0.00512 |  |  | 0 |  | 1 | CAPACITY
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 39.5 | 31.71 |  |  | -0.00513 |  |  | 0.08446 |  | 1 | CAPACITY
920571 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 411.86 |  |  | -0.00514 |  |  | 0.04435 |  | 1 | NEW | AA2-161
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 3.05 |  |  | -0.00517 |  |  | 0 |  | 1 | CAPACITY
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00519 |  |  | 0.08446 |  | 1 | CAPACITY
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 64.31 |  |  | -0.0052 |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 52.35 |  |  | -0.0052 |  |  | 0.04435 |  | 1 | CAPACITY | CAMDEN COGEN TECH
925391 | AC1-010 C | 26.4 | 231 | 75 | 0 | 6 | 0 |  |  | -0.0052 |  |  | 0 |  | 1 | NEW | AC1-010
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 19.27 |  |  | -0.0052 |  |  | 0.10478 |  | 1 | CAPACITY
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -0.0052 |  |  | 0 |  | 1 | NEWENERGY | AC1-010
219765 | PARADISE E | 26.4 | 231 | 75 | 0 | 3.2 | 0 |  |  | -0.0052 |  |  | 0 |  | 1 | NEWENERGY | U4-036
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.3 | 9.07 |  |  | -0.0052 |  |  | 0.10478 |  | 1 | CAPACITY
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | -0.0052 |  |  | 0 |  | 1 | MTX | X2-013
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.0052 |  |  | 0 |  | 1 | CAPACITY | U4-036
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 28.1 |  |  | -0.00523 |  |  | 0.10478 |  | 1 | CAPACITY
913142 | Y1-033 E OP1 | 115 | 226 | 74 | 0 | 34.02 | 0 |  |  | -0.00525 |  |  | 0 |  | 1 | NEWENERGY | Y1-033
207402 | 28AA2-082 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.00524 |  |  | 0.05 |  | 1 | MTX | AA2-082
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 4.01 |  |  | -0.00525 |  |  | 0 |  | 1 | CAPACITY | Y1-033
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 38.7 | 31.07 |  |  | -0.00532 |  |  | 0.08446 |  | 1 | CAPACITY
204555 | 27QUEEN ST | 115 | 227 | 74 | 0 | 5 | 0 |  |  | -0.00536 |  |  | 0 |  | 1 | NEWENERGY
204638 | 27CAT TRAC | 13.2 | 227 | 58 | 0 | 32.3 | 25.93 |  |  | -0.00539 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
204706 | 27CAT TRC2 | 13.2 | 227 | 58 | 0 | 13.9 | 11.16 |  |  | -0.00539 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 140 | 182.2 | 146.28 |  |  | -0.00541 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 118.7 | 175.2 | 140.66 |  |  | -0.00541 |  |  | 0.04435 |  | 1 | CAPACITY | AE SPRINGDALE
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 118.7 | 172.2 | 138.25 |  |  | -0.00541 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.00541 |  |  | 0.08446 |  | 1 | CAPACITY
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.00541 |  |  | 0.08446 |  | 1 | CAPACITY
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 353.26 |  |  | -0.00543 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00543 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-076
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00543 |  |  | 0 |  | 1 | CAPACITY | AA1-076
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 24.08 |  |  | -0.00545 |  |  | 0.10478 |  | 1 | CAPACITY
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 5.54 |  |  | -0.00551 |  |  | 0 |  | 1 | CAPACITY
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.33 |  |  | -0.00552 |  |  | 0 |  | 1 | CAPACITY
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00552 |  |  | 0 |  | 1 | NEWENERGY | K23
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 0 |  |  | -0.00552 |  |  | 0 |  | 1 | NEWENERGY | L13
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 0 |  |  | -0.00552 |  |  | 0 |  | 1 | NEWENERGY | O48
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | -0.00552 |  |  | 0.05 |  | 1 | MTX
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | -0.00552 |  |  | 0.05 |  | 1 | MTX
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 0 |  |  | -0.00552 |  |  | 0 |  | 1 | NEWENERGY | R40
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 5.06 |  |  | -0.00552 |  |  | 0 |  | 1 | CAPACITY | O48
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 4.74 |  |  | -0.00552 |  |  | 0 |  | 1 | CAPACITY | L13
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 5.1 | 4.09 |  |  | -0.00552 |  |  | 0 |  | 1 | CAPACITY | K23
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 6.1 |  |  | -0.00561 |  |  | 0 |  | 1 | CAPACITY
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0 |  |  | -0.00569 |  |  | 0 |  | 1 | NEWENERGY | AD2-070
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00569 |  |  | 0 |  | 1 | CAPACITY | AD2-070
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.02 |  |  | -0.0057 |  |  | 0 |  | 1 | CAPACITY
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 5.46 |  |  | -0.00572 |  |  | 0 |  | 1 | CAPACITY
208920 | WLPK | 12.5 | 229 | 60 | 0 | 40.9 | 32.84 |  |  | -0.00574 |  |  | 0.07484 |  | 1 | CAPACITY
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.45 |  |  | -0.00574 |  |  | 0 |  | 1 | CAPACITY
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.72 |  |  | -0.00574 |  |  | 0 |  | 1 | CAPACITY | K22
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 68.24 |  |  | -0.00576 |  |  | 0.10478 |  | 1 | CAPACITY
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 42.95 |  |  | -0.00575 |  |  | 0.08446 |  | 1 | CAPACITY
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 42.95 |  |  | -0.00575 |  |  | 0.08446 |  | 1 | CAPACITY
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00575 |  |  | 0.08446 |  | 1 | CAPACITY
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00575 |  |  | 0.08446 |  | 1 | CAPACITY
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00575 |  |  | 0.08446 |  | 1 | CAPACITY
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00576 |  |  | 0 |  | 1 | CAPACITY
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 16.55 |  |  | -0.00576 |  |  | 0.07484 |  | 1 | CAPACITY
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 682.91 |  |  | -0.00577 |  |  | 0.10478 |  | 1 | CAPACITY | Cone1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 682.43 |  |  | -0.00577 |  |  | 0.10478 |  | 1 | CAPACITY | Cone2
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 400 | 321.14 |  |  | -0.00578 |  |  | 0.04435 |  | 1 | CAPACITY | AD2-114
235622 | 01SBEND4 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00578 |  |  | 0.08446 |  | 1 | CAPACITY
235620 | 01SBEND2 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00578 |  |  | 0.08446 |  | 1 | CAPACITY
235621 | 01SBEND3 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00578 |  |  | 0.08446 |  | 1 | CAPACITY
235619 | 01SBEND1 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00578 |  |  | 0.08446 |  | 1 | CAPACITY
903644 | W3-099 E OP1 | 230 | 226 | 74 | 0 | 87 | 0 |  |  | -0.00578 |  |  | 0 |  | 1 | NEWENERGY | W3-099
201144 | W3-099 C OP1 | 230 | 226 | 74 | 0 | 13 | 0 |  |  | -0.00578 |  |  | 0 |  | 1 | NEW | W3-099
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 853.3 | 685.08 |  |  | -0.0058 |  |  | 0.10478 |  | 1 | CAPACITY | Keys1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 853.1 | 684.92 |  |  | -0.0058 |  |  | 0.10478 |  | 1 | CAPACITY | Keys2
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00583 |  |  | 0 |  | 1 | NEWENERGY | P60
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 6.82 |  |  | -0.00583 |  |  | 0 |  | 1 | CAPACITY | P60
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 24.24 |  |  | -0.00584 |  |  | 0.07484 |  | 1 | CAPACITY
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00589 |  |  | 0 |  | 1 | CAPACITY
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 23.2 | 0 |  |  | -0.0059 |  |  | 0 |  | 1 | NEWENERGY | K13
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.0059 |  |  | 0.12623 |  | 1 | CAPACITY
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 2.57 |  |  | -0.0059 |  |  | 0 |  | 1 | CAPACITY | K13
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 10.44 |  |  | -0.00592 |  |  | 0.12623 |  | 1 | CAPACITY
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00595 |  |  | 0.12623 |  | 1 | CAPACITY
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 422.06 |  |  | -0.00598 |  |  | 0.10478 |  | 1 | CAPACITY
200805 | 26COLVER13 | 13.2 | 226 | 12 | 77 | 110 | 88.31 |  |  | -0.00598 |  |  | 0.10478 |  | 1 | CAPACITY
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 60 | 0 |  |  | -0.006 |  |  | 0 |  | 1 | NEWENERGY | R32
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 52 | 0 |  |  | -0.006 |  |  | 0 |  | 1 | NEWENERGY | O18
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 10.19 |  |  | -0.006 |  |  | 0 |  | 1 | CAPACITY | R32
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 6.5 |  |  | -0.006 |  |  | 0 |  | 1 | CAPACITY | O18
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 497.77 |  |  | -0.00601 |  |  | 0.10478 |  | 1 | CAPACITY
200809 | 26SITHE | 138 | 226 | 15 | 0 | 36 | 28.9 |  |  | -0.00601 |  |  | 0.10478 |  | 1 | CAPACITY
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 521.86 |  |  | -0.00608 |  |  | 0.10478 |  | 1 | CAPACITY
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 492.95 |  |  | -0.00608 |  |  | 0.10478 |  | 1 | CAPACITY
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 0 |  |  | -0.00607 |  |  | 0 |  | 1 | NEWENERGY | V3-030
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 4.25 |  |  | -0.00607 |  |  | 0 |  | 1 | CAPACITY | V3-030
208946 | MACR CT | 12.5 | 229 | 55 | 0 | 72 | 57.81 |  |  | -0.00612 |  |  | 0.08446 |  | 1 | CAPACITY
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 57 | 45.76 |  |  | -0.00613 |  |  | 0.08446 |  | 1 | CAPACITY
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 48 | 0 |  |  | -0.00615 |  |  | 0 |  | 1 | NEWENERGY | Q53
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 5.14 |  |  | -0.00615 |  |  | 0 |  | 1 | CAPACITY | Q53
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00623 |  |  | 0 |  | 1 | NEWENERGY | W4-097
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00623 |  |  | 0 |  | 1 | CAPACITY | W4-097
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 0 |  |  | -0.00626 |  |  | 0 |  | 1 | NEWENERGY | N39
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00626 |  |  | 0 |  | 1 | NEWENERGY | O38
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00626 |  |  | 0 |  | 1 | CAPACITY | N39
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.4 | 7.55 |  |  | -0.00626 |  |  | 0 |  | 1 | CAPACITY | O38
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 187.87 |  |  | -0.00628 |  |  | 0.0316 |  | 1 | CAPACITY
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 177.43 |  |  | -0.00628 |  |  | 0.0316 |  | 1 | CAPACITY
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 26.13 |  |  | -0.00628 |  |  | 0.07484 |  | 1 | CAPACITY
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 601.34 |  |  | -0.0064 |  |  | 0.10478 |  | 1 | CAPACITY
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 293.93 |  |  | -0.0064 |  |  | 0.10478 |  | 1 | CAPACITY | Bris2
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 248.4 |  |  | -0.0064 |  |  | 0.10478 |  | 1 | CAPACITY | Bris1
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 40 | 0 |  |  | -0.00639 |  |  | 0 |  | 1 | NEWENERGY | Q36
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 6.66 |  |  | -0.00639 |  |  | 0 |  | 1 | CAPACITY | Q36
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 33.96 |  |  | -0.00654 |  |  | 0.10478 |  | 1 | CAPACITY
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | -0.00655 |  |  | 0 |  | 1 | ENERGY
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4.82 |  |  | -0.00659 |  |  | 0 |  | 1 | CAPACITY
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 16.86 |  |  | -0.00665 |  |  | 0.07484 |  | 1 | CAPACITY
200722 | 26SHAWVL 2 | 18 | 226 | 12 | 62 | 124.7 | 100.12 |  |  | -0.00667 |  |  | 0.10478 |  | 1 | CAPACITY
200715 | 26SHAWVL 1 | 18 | 226 | 12 | 62 | 122 | 97.95 |  |  | -0.00667 |  |  | 0.10478 |  | 1 | CAPACITY
200665 | 26SHAWVL 3 | 22 | 226 | 12 | 120 | 174.2 | 139.86 |  |  | -0.00675 |  |  | 0.10478 |  | 1 | CAPACITY
200666 | 26SHAWVL 4 | 22 | 226 | 12 | 120 | 171 | 137.29 |  |  | -0.00675 |  |  | 0.10478 |  | 1 | CAPACITY
922932 | AB1-082 OP | 46 | 201 | 55 | 0 | 19.9 | 0 |  |  | -0.0068 |  |  | 0.08446 |  | 1 | NEW
208947 | WSHO CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00682 |  |  | 0.08446 |  | 1 | CAPACITY
236828 | 01GRAYMONT | 46 | 201 | 2 | 0 | 4 | 0 |  |  | -0.0069 |  |  | 0 |  | 1 | ENERGY
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | -0.00691 |  |  | 0 |  | 1 | MTX | AC1-025
208348 | EELI | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00695 |  |  | 0 |  | 1 | CAPACITY
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 24.08 |  |  | -0.00701 |  |  | 0.10478 |  | 1 | CAPACITY
208942 | HARR CT | 12.5 | 229 | 55 | 0 | 42 | 33.72 |  |  | -0.00702 |  |  | 0.08446 |  | 1 | CAPACITY
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 9.64 |  |  | -0.00702 |  |  | 0.12623 |  | 1 | CAPACITY
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 8.19 |  |  | -0.00702 |  |  | 0.10478 |  | 1 | CAPACITY
210022 | LING 2 | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00701 |  |  | 0 |  | 1 | CAPACITY
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 0 |  |  | -0.00705 |  |  | 0 |  | 1 | NEWENERGY | Z1-069
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00705 |  |  | 0 |  | 1 | CAPACITY | Z1-069
219647 | COOPERSOLA E | 13.2 | 231 | 75 | 0 | 0.4 | 0 |  |  | -0.00711 |  |  | 0 |  | 1 | NEWENERGY | AB1-063
210319 | WCAR 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00732 |  |  | 0 |  | 1 | CAPACITY
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | -0.00748 |  |  | 0.12623 |  | 1 | ENERGY
208697 | PRIN B34 | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00748 |  |  | 0 |  | 1 | CAPACITY
208885 | WNHO | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00748 |  |  | 0 |  | 1 | CAPACITY
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | -0.00759 |  |  | 0 |  | 1 | ENERGY
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.61 |  |  | -0.00759 |  |  | 0 |  | 1 | CAPACITY
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 19 | 15.25 |  |  | -0.00763 |  |  | 0.08446 |  | 1 | CAPACITY
211065 | PSPA IPP | 13.8 | 229 | 75 | 0 | 18.4 | 6.74 |  |  | -0.00765 |  |  | 0 |  | 1 | NEWENERGY | U4-014
204663 | 27AES GEN2 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00767 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204664 | 27AES GEN3 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00767 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204662 | 27AES GEN1 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00767 |  |  | 0.04435 |  | 1 | CAPACITY | IRONWOOD
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 130.87 |  |  | -0.00768 |  |  | 0.04435 |  | 1 | CAPACITY | GRAYS FERRY
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 0 |  |  | -0.00772 |  |  | 0 |  | 1 | NEWENERGY | P47
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.8 | 12.69 |  |  | -0.00772 |  |  | 0 |  | 1 | CAPACITY | P47
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 0 |  |  | -0.0078 |  |  | 0 |  | 1 | NEWENERGY | K02
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 16.86 |  |  | -0.00788 |  |  | 0.12623 |  | 1 | CAPACITY
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 17.18 |  |  | -0.0079 |  |  | 0.12623 |  | 1 | CAPACITY
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 16.86 |  |  | -0.0079 |  |  | 0.12623 |  | 1 | CAPACITY
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.00799 |  |  | 0.08446 |  | 1 | CAPACITY
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 0 |  |  | -0.00813 |  |  | 0 |  | 1 | NEWENERGY | AA2-017
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 0 |  |  | -0.00813 |  |  | 0 |  | 1 | NEW | AA2-017
920341 | AA2-132 | 34.5 | 226 | 55 | 0 | 19.9 | 0 |  |  | -0.00815 |  |  | 0.08446 |  | 1 | NEW
919201 | AA1-144 OP | 230 | 226 | 58 | 0 | 163 | 130.87 |  |  | -0.00832 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-144
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00836 |  |  | 0 |  | 1 | CAPACITY | X1-109
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00836 |  |  | 0.04435 |  | 1 | CAPACITY | X1-109
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.04 |  |  | -0.00837 |  |  | 0 |  | 1 | CAPACITY
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | -0.00839 |  |  | 0 |  | 1 | ENERGY
208580 | MGTN 2 | 12.5 | 229 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00839 |  |  | 0 |  | 1 | CAPACITY
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.0084 |  |  | 0.08446 |  | 1 | CAPACITY
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.0084 |  |  | 0.08446 |  | 1 | CAPACITY
203932 | AA2-133 GEN | 13.8 | 226 | 55 | 0 | 19.89 | 0 |  |  | -0.00865 |  |  | 0.08446 |  | 1 | NEW
219913 | PENNSAU2 E | 26.4 | 231 | 75 | 0 | 8.2 | 0 |  |  | -0.0088 |  |  | 0 |  | 1 | NEWENERGY | AD2-042
219915 | CINNAMSOL E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.0088 |  |  | 0 |  | 1 | NEWENERGY | AD2-027
219912 | PENNSAU2 C | 26.4 | 231 | 75 | 0 | 5 | 0 |  |  | -0.0088 |  |  | 0 |  | 1 | NEW | AD2-042
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.63 | 3.72 |  |  | -0.0088 |  |  | 0 |  | 1 | CAPACITY
219914 | CINNAMSOL C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.0088 |  |  | 0 |  | 1 | CAPACITY | AD2-027
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.4 |  |  | -0.0088 |  |  | 0 |  | 1 | CAPACITY
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 389.39 |  |  | -0.00884 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-115
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 30.1 | 24.17 |  |  | -0.00898 |  |  | 0.08446 |  | 1 | CAPACITY
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 0 |  |  | -0.00899 |  |  | 0 |  | 1 | NEWENERGY | P28
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | -0.00899 |  |  | 0.10478 |  | 1 | NEW
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 47.37 |  |  | -0.00899 |  |  | 0.10478 |  | 1 | CAPACITY
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00899 |  |  | 0 |  | 1 | CAPACITY | P28
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 17.18 |  |  | -0.00899 |  |  | 0.12623 |  | 1 | CAPACITY
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 4.82 |  |  | -0.00902 |  |  | 0 |  | 1 | CAPACITY
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 6 | 4.82 |  |  | -0.00906 |  |  | 0 |  | 1 | CAPACITY
209007 | NOEN IPP | 13.8 | 229 | 12 | 80 | 111.4 | 89.44 |  |  | -0.00919 |  |  | 0.10478 |  | 1 | CAPACITY
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 152.86 |  |  | -0.00931 |  |  | 0.04435 |  | 1 | CAPACITY | ONTELAUNEE
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 152.86 |  |  | -0.00931 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 139.94 |  |  | -0.00931 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 64.23 |  |  | -0.00939 |  |  | 0.10478 |  | 1 | CAPACITY
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 69.05 |  |  | -0.00952 |  |  | 0.10478 |  | 1 | CAPACITY
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 65.83 |  |  | -0.00952 |  |  | 0.10478 |  | 1 | CAPACITY
208941 | FISH CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00952 |  |  | 0.08446 |  | 1 | CAPACITY
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.4 | 9.15 |  |  | -0.00952 |  |  | 0 |  | 1 | CAPACITY | Q27
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.81 |  |  | -0.00952 |  |  | 0 |  | 1 | CAPACITY | N14
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 18.3 | 14.69 |  |  | -0.00954 |  |  | 0.12623 |  | 1 | CAPACITY
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00964 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
211375 | BEAC | 69 | 229 | 2 | 0 | 20 | 0 |  |  | -0.00969 |  |  | 0.10478 |  | 1 | ENERGY
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 47.77 |  |  | -0.00969 |  |  | 0.08446 |  | 1 | CAPACITY
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 47.21 |  |  | -0.00969 |  |  | 0.08446 |  | 1 | CAPACITY
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 23.76 |  |  | -0.00969 |  |  | 0.08446 |  | 1 | CAPACITY
208943 | HARW CT | 12.5 | 229 | 55 | 0 | 27.2 | 21.84 |  |  | -0.00969 |  |  | 0.08446 |  | 1 | CAPACITY
211591 | HARW | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00969 |  |  | 0 |  | 1 | CAPACITY
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 34.28 |  |  | -0.00977 |  |  | 0.10478 |  | 1 | CAPACITY
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 26.09 |  |  | -0.00977 |  |  | 0.10478 |  | 1 | CAPACITY
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 6.42 |  |  | -0.00977 |  |  | 0 |  | 1 | CAPACITY
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 4.9 |  |  | -0.00977 |  |  | 0 |  | 1 | CAPACITY
208940 | ALLE CT | 12.5 | 229 | 55 | 0 | 56 | 44.96 |  |  | -0.00984 |  |  | 0.08446 |  | 1 | CAPACITY
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 608.97 |  |  | -0.01019 |  |  | 0.10478 |  | 1 | CAPACITY
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 608.49 |  |  | -0.01019 |  |  | 0.10478 |  | 1 | CAPACITY
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.01021 |  |  | 0.04435 |  | 1 | CAPACITY | MOXIE PATRIOT
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.01021 |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT
208948 | WILL CT | 12.5 | 229 | 55 | 0 | 27.4 | 22 |  |  | -0.01023 |  |  | 0.08446 |  | 1 | CAPACITY
212005 | ALWD | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.01023 |  |  | 0 |  | 1 | CAPACITY
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 11.24 |  |  | -0.01024 |  |  | 0.08446 |  | 1 | CAPACITY
212435 | SMIL | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.01025 |  |  | 0 |  | 1 | CAPACITY
209018 | SUNBIPCT | 12.5 | 229 | 55 | 0 | 36 | 28.9 |  |  | -0.01029 |  |  | 0.08446 |  | 1 | CAPACITY
212345 | PENS | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.01029 |  |  | 0 |  | 1 | CAPACITY
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.01036 |  |  | 0.05 |  | 1 | MTX | AB1-182
208944 | JENK CT | 12.5 | 229 | 55 | 0 | 28 | 22.48 |  |  | -0.01036 |  |  | 0.08446 |  | 1 | CAPACITY
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.65 |  |  | -0.01036 |  |  | 0 |  | 1 | CAPACITY | L18
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1091.76 |  |  | -0.01037 |  |  | 0.01494 |  | 1 | CAPACITY
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 35.57 |  |  | -0.01041 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 23.44 |  |  | -0.01041 |  |  | 0.04435 |  | 1 | CAPACITY | HUNLOCK
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 39.1 |  |  | -0.01041 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 38.86 |  |  | -0.01041 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 317.93 |  |  | -0.01049 |  |  | 0 |  | 1 | CAPACITY | Hummel
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 194.29 |  |  | -0.01049 |  |  | 0 |  | 1 | CAPACITY | Hummel
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.01049 |  |  | 0 |  | 1 | CAPACITY | Hummel
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.01049 |  |  | 0.04435 |  | 1 | CAPACITY | Hummel
211374 | AVOC | 12.5 | 229 | 2 | 0 | 17.4 | 13.97 |  |  | -0.01048 |  |  | 0 |  | 1 | CAPACITY
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 0 |  |  | -0.01055 |  |  | 0 |  | 1 | NEWENERGY | AC1-071
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 7.02 |  |  | -0.01055 |  |  | 0 |  | 1 | NEW | AC1-071
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.01062 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G2
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.01062 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G1
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.01062 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G3
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | -0.01062 |  |  | 0.05 |  | 1 | MTX | Z2-107
209009 | PEIP 2 | 13.8 | 229 | 56 | 0 | 43.7 | 35.08 |  |  | -0.01062 |  |  | 0.08446 |  | 1 | CAPACITY
209010 | PEIP 1 | 13.8 | 229 | 29 | 0 | 26.7 | 21.43 |  |  | -0.01062 |  |  | 0.10478 |  | 1 | CAPACITY
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 7.23 |  |  | -0.01062 |  |  | 0 |  | 1 | CAPACITY | K21
209003 | KSTN IPP | 13.8 | 229 | 65 | 0 | 4.9 | 3.93 |  |  | -0.01062 |  |  | 0 |  | 1 | CAPACITY
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.01203 |  |  | 0.08446 |  | 1 | CAPACITY
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.01203 |  |  | 0.08446 |  | 1 | CAPACITY
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 22.48 |  |  | -0.01207 |  |  | 0.10478 |  | 1 | CAPACITY
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.01227 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-046
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.01227 |  |  | 0 |  | 1 | CAPACITY | Z2-046
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.01228 |  |  | 0 |  | 1 | NEWENERGY | V4-001
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.61 |  |  | -0.01228 |  |  | 0 |  | 1 | CAPACITY | V4-001
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1090.36 |  |  | -0.01229 |  |  | 0.01494 |  | 1 | CAPACITY
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.01249 |  |  | 0.08446 |  | 1 | CAPACITY
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.01249 |  |  | 0.08446 |  | 1 | CAPACITY
214030 | WAYNEJCT | 13.8 | 230 | 2 | 0 | 8.8 | 7.07 |  |  | -0.01264 |  |  | 0 |  | 1 | CAPACITY
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 900.89 |  |  | -0.01425 |  |  | 0.01494 |  | 1 | CAPACITY
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 898.96 |  |  | -0.01483 |  |  | 0.01494 |  | 1 | CAPACITY
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.01518 |  |  | 0.08446 |  | 1 | CAPACITY
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.01573 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.01573 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.01573 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.01573 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.01573 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200044 | BETH CT1 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.01573 |  |  | 0.04435 |  | 1 | CAPACITY | BETH1234
200048 | BETH CT5 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.01573 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
219650 | TRENT_COLLEG | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.01694 |  |  | 0 |  | 1 | CAPACITY
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0 |  |  | -0.01694 |  |  | 0 |  | 1 | NEWENERGY | W4-058
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.22 |  |  | -0.01694 |  |  | 0 |  | 1 | CAPACITY | W4-058
213798 | MERCK 3 | 13.8 | 230 | 2 | 13 | 35 | 28.1 |  |  | -0.01714 |  |  | 0 |  | 1 | CAPACITY
213797 | MERCK 2 | 13.8 | 230 | 2 | 4 | 25 | 20.07 |  |  | -0.01714 |  |  | 0 |  | 1 | CAPACITY
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 3.29 |  |  | -0.01714 |  |  | 0 |  | 1 | CAPACITY
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.01898 |  |  | 0 |  | 1 | NEWENERGY | AC1-030
925561 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.01898 |  |  | 0 |  | 1 | CAPACITY | AC1-030
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0 |  |  | -0.01909 |  |  | 0 |  | 1 | NEWENERGY | X1-071
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.28 |  |  | -0.01909 |  |  | 0 |  | 1 | CAPACITY | X1-071
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.0209 |  |  | 0 |  | 1 | NEWENERGY | W2-016
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.0209 |  |  | 0 |  | 1 | CAPACITY | W2-016
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0 |  |  | -0.03025 |  |  | 0 |  | 1 | NEWENERGY | AC1-017
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0 |  |  | -0.03025 |  |  | 0 |  | 1 | NEWENERGY | X1-070
925451 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 1.12 |  |  | -0.03025 |  |  | 0 |  | 1 | CAPACITY | AC1-017
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.96 |  |  | -0.03025 |  |  | 0 |  | 1 | CAPACITY | X1-070
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  |  |  | -0.0336
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 38.54 |  |  | -0.03751 |  |  | 0.08446 |  | 1 | CAPACITY
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 260.3 | 208.98 |  |  | -0.03836 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | -0.03836 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | -0.03836 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill B
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 205.69 |  |  | -0.03839 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | -0.03839 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | -0.03839 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill A
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 0 |  |  | -0.03845 |  |  | 0 |  | 1 | NEWENERGY | W3-080
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.03845 |  |  | 0.08446 |  | 1 | CAPACITY
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.03845 |  |  | 0.08446 |  | 1 | CAPACITY
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.03845 |  |  | 0.08446 |  | 1 | CAPACITY
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.03845 |  |  | 0.08446 |  | 1 | CAPACITY
925442 | AC1-016 E | 26.4 | 231 | 75 | 0 | 5.45 | 0 |  |  | -0.03845 |  |  | 0 |  | 1 | NEWENERGY | AC1-016
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | -0.03845 |  |  | 0 |  | 1 | NEWENERGY | W4-103
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | -0.03845 |  |  | 0 |  | 1 | NEWENERGY | W2-102
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -0.03845 |  |  | 0 |  | 1 | NEWENERGY | Y3-026
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.03845 |  |  | 0 |  | 1 | CAPACITY | Y3-026
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 2.97 |  |  | -0.03845 |  |  | 0 |  | 1 | CAPACITY | W3-080
925441 | AC1-016 C | 26.4 | 231 | 75 | 0 | 3.34 | 2.68 |  |  | -0.03845 |  |  | 0 |  | 1 | CAPACITY | AC1-016
219685 | NATIONAL_GYP | 26 | 231 | 2 | 0 | 2.8 | 2.25 |  |  | -0.03845 |  |  | 0 |  | 1 | CAPACITY
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.03845 |  |  | 0 |  | 1 | CAPACITY | W4-103
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.03845 |  |  | 0 |  | 1 | CAPACITY | W2-102
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0 |  |  | -0.04128 |  |  | 0 |  | 1 | NEWENERGY | W2-080
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.04128 |  |  | 0 |  | 1 | CAPACITY | W2-080
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0 |  |  | -0.04651 |  |  | 0 |  | 1 | NEWENERGY | W2-050
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0 |  |  | -0.04858 |  |  | 0 |  | 1 | NEWENERGY | V3-070
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.04858 |  |  | 0 |  | 1 | CAPACITY | V3-070
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0 |  |  | -0.0491 |  |  | 0 |  | 1 | NEWENERGY | X2-075
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 1.83 |  |  | -0.0491 |  |  | 0 |  | 1 | CAPACITY | X2-075
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | W3-029
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | W3-003
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEW | AE1-156
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | AE1-156
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | W1-132
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | V4-070
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | W2-061
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | V4-069
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.05064 |  |  | 0 |  | 1 | CAPACITY | W3-029
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.05064 |  |  | 0 |  | 1 | CAPACITY | V4-069
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.05064 |  |  | 0 |  | 1 | CAPACITY | V4-070
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.05064 |  |  | 0 |  | 1 | CAPACITY | W2-061
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.05507 |  |  | 0.08446 |  | 1 | CAPACITY
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 1.04 |  |  | -0.05507 |  |  | 0 |  | 1 | CAPACITY | T20
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0 |  |  | -0.05648 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0 |  |  | -0.05648 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
932032 | AC2-009 E | 13.2 | 231 | 75 | -0.5 | 0.49 | 0 |  |  | -0.05648 |  |  | 0 |  | 1 | NEWENERGY | AC2-009
932031 | AC2-009 C | 13.2 | 231 | 75 | -0.1 | 0.1 | 0 |  |  | -0.05648 |  |  | 0 |  | 1 | NEW | AC2-009
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.05648 |  |  | 0 |  | 1 | CAPACITY | AA2-058
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0 |  |  | -0.07377 |  |  | 0 |  | 1 | NEWENERGY | W2-036
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.07377 |  |  | 0 |  | 1 | CAPACITY | W2-036
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0 |  |  | -0.10269 |  |  | 0 |  | 1 | NEWENERGY | W1-121 Z
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.10269 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.10269 |  |  | 0 |  | 1 | CAPACITY | W1-121 Z
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.46 |  |  | -0.10269 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 35.24 |  |  | -0.11211 |  |  | 0.10478 |  | 1 | CAPACITY
218780 | PRINCENTON_U | 26 | 231 | 2 | 0 | 31.56 | 25.34 |  |  | -0.13126 |  |  | 0 |  | 1 | CAPACITY
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0 |  |  | -0.13126 |  |  | 0 |  | 1 | NEWENERGY | Z1-096
219622 | TRENT_BIOGAS | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.13126 |  |  | 0 |  | 1 | CAPACITY
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 2.39 |  |  | -0.13126 |  |  | 0 |  | 1 | CAPACITY | Z1-096
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0 |  |  | -0.2107 |  |  | 0 |  | 1 | NEWENERGY | V2-009 3
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0 |  |  | -0.2107 |  |  | 0 |  | 1 | NEWENERGY | V2-009 4
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 1.92 |  |  | -0.2107 |  |  | 0 |  | 1 | CAPACITY | V2-009 3
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 1.15 |  |  | -0.2107 |  |  | 0 |  | 1 | CAPACITY | V2-009 4
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0 |  |  | -0.23582 |  |  | 0 |  | 1 | NEWENERGY | W3-124
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0 |  |  | -0.23582 |  |  | 0 |  | 1 | NEWENERGY | V2-009 1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.87 |  |  | -0.23582 |  |  | 0 |  | 1 | CAPACITY | W3-124
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.23582 |  |  | 0 |  | 1 | CAPACITY | V2-009 1
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.23653 |  |  | 0 |  | 1 | NEWENERGY | V3-024
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0 |  |  | -0.23653 |  |  | 0 |  | 1 | NEWENERGY | V2-009 2
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0 |  |  | -0.23653 |  |  | 0 |  | 1 | NEWENERGY | X2-088
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.23653 |  |  | 0 |  | 1 | CAPACITY | V3-024
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 1.52 |  |  | -0.23653 |  |  | 0 |  | 1 | CAPACITY | V2-009 2
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.72 |  |  | -0.23653 |  |  | 0 |  | 1 | CAPACITY | X2-088
218455 | CINNBAY_CGEN | 26.4 | 231 | 75 | 0 | 9 | 0 |  |  | -0.28851 |  |  | 0 |  | 1 | NEWENERGY
924132 | NEWROADSO E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.28851 |  |  | 0 |  | 1 | NEWENERGY | AB2-057
217199 | EDGEBORO_2E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.28851 |  |  | 0 |  | 1 | NEWENERGY | V3-059
217198 | EDGEBORO_1E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.28851 |  |  | 0 |  | 1 | NEWENERGY | V3-058
924131 | NEWROADSO C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.28851 |  |  | 0 |  | 1 | CAPACITY | AB2-057
218781 | BRIS_MYERS | 26 | 231 | 2 | 0 | 3 | 2.41 |  |  | -0.28851 |  |  | 0 |  | 1 | CAPACITY

## FG 28-GD-S2-S134
****** PJM Generator Deliverability Detailed Report ****** POWER-GEM [TARA Ver 2001.1a PJMGD RC3 64-bit - Wed Aug 18 16:44:04 2021]
FG Index | 134 | Monitored Facility:227934 CARDIFF2 138 227945 LEWIS #2 138 1 / Contingency:AE_P7-1 AE3TOWER[Tower]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
400 | 115.67 | 113.1 | AC | 274.73 | 188.01 | -2.8 | 1.93 | 0.83 | 462.69 | 452.4 | 0.000257 | 0 | 12850.4 | 0 | 11615.4 | 0.05 | 1246.31 | 1235 | 11.31 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited?
900000 | CARDIFF E | 230 | 234 | 74 | 0 | 1235 | 0 | 1235 | FiftyFifty | 0.15223 | 188.0053 |  | 0 | 1 | 1 | NEWENERGY | OSW_CARDIF
227900 | CARDIFF C | 230 | 234 | 74 | 0 | 275 | 275 | 275 | FiftyFifty | 0.15223 |  |  | 0 | 1 | 1 | CAPACITY | OSW_CARDIF
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  | 105 | LTF/CMTX NF | 0.00248 | 0.2605 | -0.027
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  | 673 | LTF/CMTX NF | 0.00083 | 0.5598 | -0.1733
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  | 55.3 | CLTF | 0.00043 | 0.024 | -0.0142
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 1044 |  | 1044 | LTF/CBM | 0.00028 | 0.2961 | 0.2688
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 68.3 |  | 68.3 | CLTF | 0.00029 | 0.0197 | 0.0176
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  | 175 | CLTF | 0.00027 | 0.0473 | 0.0451
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  | 140 | CLTF | 0.00027 | 0.038 | 0.036
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1402 |  | 1402 | LTF/CBM | 0.00026 | 0.366 | 0.361
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 896 |  | 896 | LTF/CBM | 0.00027 | 0.2401 | 0.2307
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  | 158.9 | CLTF | 0.00026 | 0.042 | 0.0409
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 62.8 |  | 62.8 | CLTF | 0.00026 | 0.0166 | 0.0162
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 38 |  | 38 | LTF/CBM | 0.00027 | 0.0103 | 0.0098
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 31.5 |  | 31.5 | CLTF | 0.00026 | 0.0083 | 0.0081
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  | 10.5 | CLTF | 0.00026 | 0.0028 | 0.0027
AC1-212 | BATTERY_AC1-212->PJM |  |  | LTF |  | 1.9 |  | 1.9 | LTF/CMTX | 0.00026 | 0.0005 | 0.0005
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 | 4.67 | Adder/OL | -0.24728 | -1.156 | 0.0012 | 0.10478 |  | 1 | ENERGY
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 | 6.63 | Adder/OL | -0.24858 | -1.6481 | 0.0017 | 0.12623 |  | 1 | ENERGY
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 998.11 |  |  | 0.0029 |  |  | 0.01494 |  | 1 | CAPACITY
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 992.1 |  |  | 0.0029 |  |  | 0.01494 |  | 1 | CAPACITY
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | 0.0029 |  |  | 0.08446 |  | 1 | ENERGY
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1026.43 |  |  | 0.00288 |  |  | 0.01494 |  | 1 | CAPACITY
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | 0.0019 |  |  | 0.04435 |  | 1 | NEW | AA2-069
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 154.95 |  |  | 0.0019 |  |  | 0.04435 |  | 1 | CAPACITY | Garrison
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 93.29 |  |  | 0.0019 |  |  | 0 |  | 1 | CAPACITY | Garrison
232901 | NORTHST | 69 | 235 | 56 | 5 | 46 | 36.93 |  |  | 0.0019 |  |  | 0.08446 |  | 1 | CAPACITY
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 12.2 |  |  | 0.0019 |  |  | 0.10478 |  | 1 | CAPACITY
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 39.34 |  |  | 0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 38.54 |  |  | 0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 152.54 |  |  | 0.00182 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00182 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00182 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC2
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00182 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 0 |  |  | 0.00178 |  |  | 0 |  | 1 | NEWENERGY | AB1-056
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 330.7 |  |  | 0.00178 |  |  | 0.10478 |  | 1 | CAPACITY
930201 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 51.71 |  |  | 0.00178 |  |  | 0 |  | 1 | CAPACITY | AB1-056
232920 | IR10 | 13.2 | 235 | 55 | 12.6 | 16.1 | 12.93 |  |  | 0.00178 |  |  | 0.08446 |  | 1 | CAPACITY
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | 0.00177 |  |  | 0.10478 |  | 1 | ENERGY
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.00177 |  |  | 0 |  | 1 | NEWENERGY | Z2-077
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.00177 |  |  | 0 |  | 1 | NEWENERGY | Z2-076
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0 |  |  | 0.00178 |  |  | 0 |  | 1 | NEWENERGY | AB1-137
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 3.37 |  |  | 0.00178 |  |  | 0 |  | 1 | CAPACITY | AB1-137
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.00177 |  |  | 0 |  | 1 | CAPACITY | Z2-077
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.00177 |  |  | 0 |  | 1 | CAPACITY | Z2-076
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.41 |  |  | 0.00177 |  |  | 0 |  | 1 | CAPACITY
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.00176 |  |  | 0.08446 |  | 1 | CAPACITY
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.00176 |  |  | 0.08446 |  | 1 | CAPACITY
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.05 |  |  | 0.00176 |  |  | 0 |  | 1 | CAPACITY
917082 | CHERRYDALE E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00175 |  |  | 0 |  | 1 | NEWENERGY | Z2-012
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00175 |  |  | 0 |  | 1 | NEWENERGY | W1-005
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00175 |  |  | 0 |  | 1 | NEWENERGY | W1-004
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00175 |  |  | 0 |  | 1 | NEWENERGY | W1-006
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00175 |  |  | 0 |  | 1 | NEWENERGY | W1-003
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.00175 |  |  | 0.08446 |  | 1 | CAPACITY
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.00175 |  |  | 0.08446 |  | 1 | CAPACITY
232915 | OH NUG4 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.00175 |  |  | 0.08446 |  | 1 | CAPACITY
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.00175 |  |  | 0.08446 |  | 1 | CAPACITY
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 39.03 |  |  | 0.00175 |  |  | 0.08446 |  | 1 | CAPACITY
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 38.94 |  |  | 0.00175 |  |  | 0.08446 |  | 1 | CAPACITY
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 38.68 |  |  | 0.00175 |  |  | 0.08446 |  | 1 | CAPACITY
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 26.05 |  |  | 0.00175 |  |  | 0.08446 |  | 1 | CAPACITY
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.00175 |  |  | 0 |  | 1 | CAPACITY | W1-003
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.00175 |  |  | 0 |  | 1 | CAPACITY | W1-006
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.00175 |  |  | 0 |  | 1 | CAPACITY | W1-005
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.00175 |  |  | 0 |  | 1 | CAPACITY | W1-004
232905 | BAYVIEW1 | 24.9 | 235 | 65 | 0 | 12.5 | 10.04 |  |  | 0.00175 |  |  | 0.12623 |  | 1 | CAPACITY
917081 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.00175 |  |  | 0 |  | 1 | CAPACITY | Z2-012
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 0 |  |  | 0.00174 |  |  | 0 |  | 1 | NEWENERGY | AA1-102
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 45.76 |  |  | 0.00174 |  |  | 0 |  | 1 | CAPACITY | AA1-102
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0 |  |  | 0.00175 |  |  | 0 |  | 1 | NEWENERGY | X1-032
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 8.03 |  |  | 0.00174 |  |  | 0 |  | 1 | CAPACITY
293670 | O-025 C | 25 | 235 | 64 | 0 | 6 | 4.82 |  |  | 0.00175 |  |  | 0 |  | 1 | CAPACITY
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0 |  |  | 0.00174 |  |  | 0 |  | 1 | NEWENERGY | Y3-058
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 5.7 | 4.58 |  |  | 0.00174 |  |  | 0 |  | 1 | CAPACITY | Y3-058
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 122.84 |  |  | 0.00171 |  |  | 0.10478 |  | 1 | CAPACITY
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0 |  |  | 0.00171 |  |  | 0 |  | 1 | NEWENERGY | Y1-080
232919 | VN10 | 13.2 | 235 | 55 | 12.4 | 14.3 | 12.46 |  |  | 0.00172 |  |  | 0 |  | 1 | CAPACITY
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 1.03 |  |  | 0.00171 |  |  | 0 |  | 1 | CAPACITY | Y1-080
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00169 |  |  | 0 |  | 1 | NEWENERGY | X3-008
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.00169 |  |  | 0 |  | 1 | CAPACITY | X3-008
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 55.4 |  |  | 0.00163 |  |  | 0.12623 |  | 1 | CAPACITY
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0 |  |  | 0.00159 |  |  | 0 |  | 1 | NEWENERGY | Y1-079
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.00159 |  |  | 0 |  | 1 | CAPACITY | Y1-079
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0 |  |  | 0.00156 |  |  | 0 |  | 1 | NEWENERGY | X3-066
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 2.28 | 1.83 |  |  | 0.00156 |  |  | 0 |  | 1 | CAPACITY | X3-066
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 57.24 |  |  | 0.00154 |  |  | 0.10478 |  | 1 | CAPACITY
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 45.76 |  |  | 0.00154 |  |  | 0.08446 |  | 1 | CAPACITY
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 44.16 |  |  | 0.00154 |  |  | 0.04435 |  | 1 | CAPACITY | DELAWARE CITY
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.00153 |  |  | 0 |  | 1 | NEWENERGY | AB1-141
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.00153 |  |  | 0 |  | 1 | NEWENERGY | AB1-142
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 14.29 |  |  | 0.00154 |  |  | 0.08446 |  | 1 | CAPACITY
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.00153 |  |  | 0 |  | 1 | CAPACITY | AB1-141
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.00153 |  |  | 0 |  | 1 | CAPACITY | AB1-142
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 19.11 |  |  | 0.00151 |  |  | 0.12623 |  | 1 | CAPACITY
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0 |  |  | 0.00139 |  |  | 0 |  | 1 | NEWENERGY | W2-071
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.85 |  |  | 0.00139 |  |  | 0 |  | 1 | CAPACITY | W2-071
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00138 |  |  | 0 |  | 1 | NEWENERGY | AB2-179
233931 | AB2-179 C | 0.38 | 235 | 75 | 0 | 38 | 30.51 |  |  | 0.00138 |  |  | 0 |  | 1 | CAPACITY | AB2-179
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0 |  |  | 0.00131 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 S
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 0.00131 |  |  | 0 |  | 1 | CAPACITY | AB1-025 S
925112 | AB2-168 E | 34.5 | 235 | 75 | 0 | 5.2 | 0 |  |  | 0.00113 |  |  | 0 |  | 1 | NEWENERGY | AB2-168
925111 | AB2-168 C | 34.5 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.00113 |  |  | 0 |  | 1 | CAPACITY | AB2-168
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0 |  |  | 0.00112 |  |  | 0 |  | 1 | NEWENERGY | W2-056
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0 |  |  | 0.00112 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 N
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 3.36 |  |  | 0.00112 |  |  | 0 |  | 1 | CAPACITY | W2-056
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.09 |  |  | 0.00113 |  |  | 0 |  | 1 | CAPACITY
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 0.00112 |  |  | 0 |  | 1 | CAPACITY | AB1-025 N
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 13.81 |  |  | 0.00092 |  |  | 0.08446 |  | 1 | CAPACITY
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 18.47 |  |  | 0.00089 |  |  | 0.08446 |  | 1 | CAPACITY
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 18.39 |  |  | 0.00089 |  |  | 0.08446 |  | 1 | CAPACITY
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 369.31 |  |  | 0.00088 |  |  | 0.04435 |  | 1 | CAPACITY | Y1-065
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00088 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00088 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200054 | ROCKSP 3 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00088 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 3
200055 | ROCKSP 4 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00088 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 4
200052 | ROCKSP 1 | 18 | 225 | 57 | 145.7 | 167.5 | 145.91 |  |  | 0.00088 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 1
200053 | ROCKSP 2 | 18 | 225 | 57 | 144.9 | 166.5 | 145.04 |  |  | 0.00088 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 2
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 139.7 |  |  | 0.00077 |  |  | 0.10478 |  | 1 | CAPACITY
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00077 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00077 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00076 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 69.05 |  |  | 0.00076 |  |  | 0.10478 |  | 1 | CAPACITY
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 11.4 |  |  | 0.00076 |  |  | 0.08446 |  | 1 | CAPACITY
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1034.24 |  |  | 0.00061 |  |  | 0.01494 |  | 1 | CAPACITY
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 306.69 |  |  | 0.0006 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.0006 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA2
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.0006 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 154.95 |  |  | 0.0006 |  |  | 0 |  | 1 | CAPACITY | DELTA
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.0006 |  |  | 0 |  | 1 | CAPACITY | DELTA
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.0006 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.0006 |  |  | 0 |  | 1 | CAPACITY | DELTA
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1049.33 |  |  | 0.00059 |  |  | 0.01494 |  | 1 | CAPACITY
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | 0.00044 |  |  | 0.0316 |  | 1 | CAPACITY
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | 0.00044 |  |  | 0.0316 |  | 1 | CAPACITY
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | 0.00044 |  |  | 0.0316 |  | 1 | CAPACITY
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | 0.00044 |  |  | 0.0316 |  | 1 | CAPACITY
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 256.27 |  |  | 0.0004 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 134.08 |  |  | 0.0004 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | 0.0004 |  |  | 0.04435 |  | 1 | CAPACITY | HUNTERSTOWN
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | 0.0004 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | 0.00037 |  |  | 0 |  | 1 | ENERGY
220904 | CRANE G2 | 20 | 232 | 12 | 60 | 195 | 0 |  |  | 0.00036 |  |  | 0.10478 |  | 1 | NEW
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 516 |  |  | 0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 512.95 |  |  | 0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 318.73 |  |  | 0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 246 |  |  | 0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 140.6 | 112.88 |  |  | 0.00036 |  |  | 0.08446 |  | 1 | CAPACITY
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 102.85 |  |  | 0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 91.2 |  |  | 0.00036 |  |  | 0.08446 |  | 1 | CAPACITY
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 83.5 |  |  | 0.00036 |  |  | 0.08446 |  | 1 | CAPACITY
220905 | CRANE GT | 4.16 | 232 | 55 | 0 | 14 | 0 |  |  | 0.00036 |  |  | 0.08446 |  | 1 | NEW
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 45.76 |  |  | 0.00037 |  |  | 0.10478 |  | 1 | CAPACITY
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 41.75 |  |  | 0.00036 |  |  | 0.08446 |  | 1 | CAPACITY
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | 0.00036 |  |  | 0.08446 |  | 1 | ENERGY
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.5 | 24.49 |  |  | 0.00036 |  |  | 0.08446 |  | 1 | CAPACITY
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 30 | 24.08 |  |  | 0.00036 |  |  | 0.08446 |  | 1 | CAPACITY
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 10.68 |  |  | 0.00036 |  |  | 0.08446 |  | 1 | CAPACITY
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0 |  |  | 0.00036 |  |  | 0 |  | 1 | NEWENERGY | V4-005
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0 |  |  | 0.00036 |  |  | 0 |  | 1 | NEWENERGY | AA2-072
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.21 |  |  | 0.00036 |  |  | 0 |  | 1 | CAPACITY
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.49 |  |  | 0.00036 |  |  | 0 |  | 1 | CAPACITY
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.88 |  |  | 0.00036 |  |  | 0 |  | 1 | CAPACITY | V4-005
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 695.27 |  |  | 0.00036 |  |  | 0.01494 |  | 1 | CAPACITY
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 675.85 |  |  | 0.00036 |  |  | 0.01494 |  | 1 | CAPACITY
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 497.29 |  |  | 0.00035 |  |  | 0.10478 |  | 1 | CAPACITY
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 492.39 |  |  | 0.00035 |  |  | 0.10478 |  | 1 | CAPACITY
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 477.7 |  |  | 0.00035 |  |  | 0.10478 |  | 1 | CAPACITY
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 469.91 |  |  | 0.00035 |  |  | 0.10478 |  | 1 | CAPACITY
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 272.01 |  |  | 0.00035 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | 0.00035 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | 0.00035 |  |  | 0.04435 |  | 1 | CAPACITY | WALDORF
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 0 |  |  | 0.00035 |  |  | 0 |  | 1 | NEWENERGY | AC2-101
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 0 |  |  | 0.00035 |  |  | 0 |  | 1 | NEWENERGY | AC2-120
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
227024 | SMECOCT | 13.8 | 238 | 57 | 30 | 80.2 | 64.39 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | ENERGY
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 19.59 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
226895 | WOAKV2-037 E | 69 | 233 | 65 | 0 | 4.5 | 0 |  |  | 0.00036 |  |  | 0 |  | 1 | ENERGY
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 14.45 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | 0.00035 |  |  | 0.08446 |  | 1 | CAPACITY
226915 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 9.92 |  |  | 0.00035 |  |  | 0 |  | 1 | CAPACITY | AC2-101
226912 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 8.39 |  |  | 0.00035 |  |  | 0 |  | 1 | CAPACITY | AC2-120
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0 |  |  | 0.00035 |  |  | 0 |  | 1 | NEWENERGY | AB2-157
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.69 |  |  | 0.00035 |  |  | 0 |  | 1 | CAPACITY
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.76 |  |  | 0.00035 |  |  | 0 |  | 1 | CAPACITY
925011 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.64 |  |  | 0.00035 |  |  | 0 |  | 1 | CAPACITY | AB2-157
910861 | X3-087 C | 230 | 233 | 58 | 0 | 744 | 597.33 |  |  | 0.00035 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 330 | 264.94 |  |  | 0.00035 |  |  | 0 |  | 1 | CAPACITY | X4-035
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | 0.00035 |  |  | 0 |  | 1 | CAPACITY | X4-035
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | 0.00035 |  |  | 0.04435 |  | 1 | CAPACITY | X4-035
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | 0.00035 |  |  | 0.10478 |  | 1 | ENERGY
917371 | Z2-060 | 230 | 233 | 58 | 0 | 116 | 93.13 |  |  | 0.00035 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
920642 | AA2-170 E | 230 | 233 | 58 | 0 | 19.1 | 0 |  |  | 0.00035 |  |  | 0.04435 |  | 1 | NEW | AA2-170
920641 | AA2-170 C | 230 | 233 | 58 | 0 | 92 | 73.86 |  |  | 0.00035 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-170
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 64.23 |  |  | 0.00035 |  |  | 0 |  | 1 | CAPACITY | PANDA
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | 0.00035 |  |  | 0.04435 |  | 1 | CAPACITY | PANDA
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | 0.00035 |  |  | 0 |  | 1 | CAPACITY | PANDA
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 245.67 |  |  | 0.00033 |  |  | 0 |  | 1 | CAPACITY | X4-039
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 0 |  |  | 0.00033 |  |  | 0 |  | 1 | NEWENERGY | AB2-129
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | 0.00033 |  |  | 0.04435 |  | 1 | CAPACITY | X4-039
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | 0.00033 |  |  | 0 |  | 1 | CAPACITY | X4-039
924771 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 0 |  |  | 0.00033 |  |  | 0 |  | 1 | NEW | AB2-129
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | 0.00034 |  |  | 0.08446 |  | 1 | CAPACITY
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | 0.00034 |  |  | 0.08446 |  | 1 | CAPACITY
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 41.75 |  |  | 0.00034 |  |  | 0.10478 |  | 1 | CAPACITY
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 14.45 |  |  | 0.00034 |  |  | 0.08446 |  | 1 | CAPACITY
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 201.52 |  |  | 0.00033 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | 0.00033 |  |  | 0.04435 |  | 1 | CAPACITY | POSSUM POINT
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | 0.00033 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 128.86 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 152.3 | 122.28 |  |  | 0.00032 |  |  | 0.10478 |  | 1 | CAPACITY
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | 0.00032 |  |  | 0.10478 |  | 1 | CAPACITY
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | 0.00032 |  |  | 0.10478 |  | 1 | CAPACITY
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 120.19 |  |  | 0.00032 |  |  | 0.10478 |  | 1 | CAPACITY
235002 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEW | AC1-039
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AC1-039
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | W1-116
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | 0.00033 |  |  | 0.10478 |  | 1 | CAPACITY
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | 0.00033 |  |  | 0.10478 |  | 1 | CAPACITY
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 28.74 |  |  | 0.00033 |  |  | 0.10478 |  | 1 | CAPACITY
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 28.66 |  |  | 0.00033 |  |  | 0.10478 |  | 1 | CAPACITY
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AC2-072
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AA1-109
314088 | 6VANDORN | 230 | 345 | 2 | 7 | 21 | 16.86 |  |  | 0.00033 |  |  | 0 |  | 1 | CAPACITY
932521 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | AC2-072
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 4.27 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | W1-116
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 3.61 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | AA1-109
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 0.68 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 1.61 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY
313821 | 6PACIFIC | 230 | 345 | 75 | 0 | 0.09 | 0 |  |  | 0.00033 |  |  | 0 |  | 1 | NEWENERGY
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEW | AC1-107
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEW | AC1-107
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | 0.00031 |  |  | 0.04435 |  | 1 | NEW | AC1-107
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 761.83 |  |  | 0.00032 |  |  | 0.01494 |  | 1 | CAPACITY
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 761.51 |  |  | 0.00032 |  |  | 0.01494 |  | 1 | CAPACITY
316114 | AB2-068 ST | 22 | 345 | 58 | 0 | 492 | 395.01 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AB2-068
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 1
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 2
316112 | AB2-068 CT1 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | 0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-068
316113 | AB2-068 CT2 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AB2-068
315033 | 1BIRCHWDA | 18 | 345 | 13 | 85 | 238 | 191.08 |  |  | 0.00032 |  |  | 0.10478 |  | 1 | CAPACITY
314189 | 6PAPERMILL | 230 | 345 | 1 | 12 | 37 | 0 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | ENERGY
926737 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | AC1-158 1
926738 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | AC1-158 2
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 136.49 |  |  | 0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | 0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | 0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 128.94 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 128.54 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 128.3 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 126.85 |  |  | 0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC1-065
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB2-158
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | 0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 5
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | 0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 6
316149 | AD1-046 E | 230 | 345 | 75 | 0 | 20.5 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AD1-044
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 69.05 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 68.97 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 68.72 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 68.64 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | 0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | 0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | 0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 61.9 |  |  | 0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | W4-102
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AB2-029
925021 | AB2-158 C | 230 | 345 | 75 | 0 | 61 | 48.97 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AB2-158
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AB2-097
923213 | AB1-125 E OP | 34.5 | 201 | 75 | 0 | 9.3 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | 0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 2
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | 0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 1
237799 | 01AA2-159 C | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
925863 | AC1-065 C | 0.39 | 345 | 75 | 0 | 41.8 | 33.56 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AC1-065
923202 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC2-137
920562 | AA2-159 E | 34.5 | 201 | 75 | 0 | 7.3 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
923192 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC1-118
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AE1-124
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AD2-030
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AC2-136
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB2-024
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AB1-096
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC1-112
316148 | AD1-046 C | 230 | 345 | 75 | 0 | 30.7 | 24.65 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | AD1-044
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC2-138
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB1-027
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AD1-063
923212 | AB1-125 C OP | 34.5 | 201 | 75 | 0 | 5.7 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
923872 | AB2-027 E | 34.5 | 201 | 75 | 0 | 5.5 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AB2-027
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 19.99 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | South Anna 2
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | South Anna 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 19.27 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AA1-092
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 16.06 |  |  | 0.00031 |  |  | 0.12623 |  | 1 | CAPACITY
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC2-070
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AA1-095
235006 | AB2-027 C | 34.5 | 201 | 75 | 0 | 3.3 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEW | AB2-027
938961 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | AE1-124
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AD2-030
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 11.4 | 9.15 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AC2-137
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 8.83 |  |  | 0.00031 |  |  | 0.12623 |  | 1 | CAPACITY
314078 | 3REMNGTN | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | AB2-029
314766 | 6LOUISA | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314190 | 6WESTMOR | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AC1-118
314172 | 6DUNNSVL | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314375 | 6CORRCTN | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AB2-024
314187 | 3WAN 176 | 115 | 345 | 75 | 0 | 2.12 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314241 | 6OLDCHRC | 230 | 345 | 75 | 0 | 1.82 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AB1-027
932501 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 7.39 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AC2-070
934391 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 7.23 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AD1-063
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 6.98 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY
314176 | 6HARMONY | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 6.42 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AA1-092
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | W4-102
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 6.3 | 5.06 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AC2-138
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 4.98 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY
933251 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 4.41 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | AC2-136
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 3.21 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY
930521 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 2.49 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | AB1-096
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 2.33 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | AA1-095
314734 | 6CASHSCORNER | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 2.09 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.88 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY
314222 | 6HANOVER | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314213 | 3CARVER | 115 | 345 | 75 | 0 | 0 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | Z1-036
901082 | W1-029 E | 230 | 345 | 74 | 0 | 261 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | W1-029
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 678.09 |  |  | 0.00031 |  |  | 0.01494 |  | 1 | CAPACITY
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 677.21 |  |  | 0.00031 |  |  | 0.01494 |  | 1 | CAPACITY
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 788.9 | 633.38 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 480.11 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 452.01 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 422.86 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
926785 | AC1-164 E | 0.44 | 345 | 75 | 0 | 99.2 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC1-164
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.5 | 354.46 |  |  | 0.0003 |  |  | 0.10478 |  | 1 | CAPACITY
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 350.93 |  |  | 0.0003 |  |  | 0.10478 |  | 1 | CAPACITY
923262 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 322.35 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB2-134
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | 0.0003 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-086
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Z1-086
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AA2-088
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | 0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | WARREN COUNTY CC
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | 0.0003 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEW | AB2-015
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB2-160
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 198.31 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB2-190
923991 | AB2-040 C O1 | 115 | 345 | 75 | 0 | 44 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEW | AB2-040
926784 | AC1-164 C | 0.44 | 345 | 75 | 0 | 220.8 | 177.27 |  |  | 0.00031 |  |  | 0 |  | 1 | NEW | AC1-164
315086 | 1SPRUNCD | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | NEW
315085 | 1SPRUNCC | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | NEW
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-015
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | ENERGY
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-174
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | 0.0003 |  |  | 0.04435 |  | 1 | CAPACITY | BEAR GARDEN
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AA1-139
923992 | AB2-040 E O1 | 115 | 345 | 75 | 0 | 36 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-040
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | 0.0003 |  |  | 0.04435 |  | 1 | CAPACITY | FLUVANNA
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | 0.0003 |  |  | 0.10478 |  | 1 | ENERGY
925122 | AB2-169 E | 115 | 345 | 75 | 0 | 35 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-169
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB2-161
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 104.93 |  |  | 0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 7
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 103.25 |  |  | 0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 8
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 101.16 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
314525 | 6KINGFORK | 230 | 345 | 75 | 0 | 24.3 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AA2-178
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AA1-065
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AA1-063A
314550 | 6HICKORY | 230 | 345 | 75 | 0 | 22.93 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AA2-053
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 89.92 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AB2-190
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 88.96 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | 0.0003 |  |  | 0.07484 |  | 1 | CAPACITY
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | 0.0003 |  |  | 0.07484 |  | 1 | CAPACITY
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 87.83 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 86.31 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AD1-085
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 69.77 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 69.69 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 2
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | 0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | HOPEWELL HCF
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 63.18 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AA1-139
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 76.6 | 61.5 |  |  | 0.0003 |  |  | 0.04435 |  | 1 | CAPACITY | ROSEMARY
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 57.65 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AB2-134
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 53.15 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | Y1-086
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB1-127
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB1-128
314466 | 6FENTRES | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314632 | 6AYDLETOLD | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
313717 | 6SLIGO L2192 | 230 | 345 | 75 | 0 | 12.34 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314331 | 6POE | 230 | 345 | 75 | 0 | 12.27 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 48.17 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 44.96 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AA2-178
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 44 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AA2-053
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 53.6 | 43.03 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AA1-065
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | Z1-068
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | 0.0003 |  |  | 0.10478 |  | 1 | CAPACITY
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 40.87 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AA1-063A
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 40.38 |  |  | 0.0003 |  |  | 0.07484 |  | 1 | CAPACITY
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 40.14 |  |  | 0.0003 |  |  | 0.19858 |  | 1 | CAPACITY
314713 | 3PAMPLIN | 115 | 345 | 75 | 0 | 9.73 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314807 | 3MT JACK | 115 | 345 | 75 | 0 | 9.7 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 38.54 |  |  | 0.0003 |  |  | 0.07484 |  | 1 | CAPACITY
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 47.5 | 38.13 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AD1-060
316143 | AD1-160 E | 115 | 345 | 75 | 0 | 9.1 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AD1-160
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 33.72 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB2-174
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AE1-162
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 32.44 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB1-173
935212 | AD1-156 E | 230 | 345 | 75 | 0 | 7.92 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AD1-156
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AC1-116
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | W1-029
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Z1-036
925121 | AB2-169 C | 115 | 345 | 75 | 0 | 39 | 31.31 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB2-169
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 30.51 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AA2-088
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC1-147
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 35.9 | 28.82 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB2-022
316145 | AE1-027 E | 230 | 345 | 75 | 0 | 6.9 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AE1-027
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AE1-074
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AC2-071
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC2-196
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB2-100 1
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB2-100 2
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC1-027
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-045
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB1-173
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB2-026
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | Z2-030
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC2-174
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB2-025
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | Z2-027
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AD1-157
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 24.41 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AB2-160
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AE1-075
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 23.76 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AD1-144
316158 | AD2-164 | 230 | 345 | 57 | 0 | 26.7 | 21.44 |  |  | 0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AC2-074
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AD2-215
314578 | 3HORNRTN | 115 | 345 | 75 | 0 | 5.15 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314589 | 3MURPHYS | 115 | 345 | 75 | 0 | 4.66 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | V4-068
316147 | AE1-028 E | 230 | 345 | 75 | 0 | 4.4 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AE1-028
314541 | 3WATKINS | 115 | 345 | 1 | 0 | 4 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | ENERGY
314333 | 6POWHATN | 230 | 345 | 75 | 0 | 3.97 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AB2-026
314579 | 6HORNRTN | 230 | 345 | 75 | 0 | 3.91 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
933571 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEW | AC2-174
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 15.25 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AB2-161
314651 | 6WINFALL | 230 | 345 | 75 | 0 | 3.35 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314645 | 6SLIGO L269 | 230 | 345 | 75 | 0 | 3.22 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.3 | 13.09 |  |  | 0.00031 |  |  | 0.12623 |  | 1 | CAPACITY
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 12.2 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 12.04 |  |  | 0.00031 |  |  | 0.12623 |  | 1 | CAPACITY
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 12.04 |  |  | 0.00031 |  |  | 0.12623 |  | 1 | CAPACITY
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 11.96 |  |  | 0.00031 |  |  | 0.12623 |  | 1 | CAPACITY
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 11.96 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
938551 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AE1-074
932511 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AC2-071
316144 | AE1-027 C | 230 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AE1-027
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 10.44 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AB2-022
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 10.36 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEW
926661 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 10.12 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AC1-147
314266 | 6NORTHAMPTON | 230 | 345 | 75 | 0 | 2.47 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 9.88 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AD1-085
316258 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AE1-162
938561 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AE1-075
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 9.55 |  |  | 0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
935211 | AD1-156 C | 230 | 345 | 75 | 0 | 11.82 | 9.49 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AD1-156
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 9.05 |  |  | 0.00031 |  |  | 0.12623 |  | 1 | CAPACITY
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 8.83 |  |  | 0.0003 |  |  | 0.12623 |  | 1 | CAPACITY
314533 | 6SMITFLD | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314435 | 6SAPONY | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AB2-025
314603 | 3SCOT NK | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314617 | 3TUNIS | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314677 | 6BUCKING | 230 | 345 | 75 | 0 | 2.12 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB2-045
932541 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AC2-074
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 8.03 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY
933731 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 8.03 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AC2-196
316150 | AD2-215 C | 230 | 345 | 76 | 0 | 9.8 | 7.87 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AD2-215
935111 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 7.79 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AD1-144
314491 | 3PENDLTN | 115 | 345 | 75 | 0 | 1.89 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AC1-027
935221 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 7.23 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AD1-157
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | V4-068
314637 | 6EDENTON | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AA2-059
314568 | 3EARLEYS | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314566 | 3CRESWEL | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-099
316146 | AE1-028 C | 230 | 345 | 75 | 0 | 7.6 | 6.1 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AE1-028
235040 | 01AB1-127 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB1-127
235041 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB1-128
942852 | AE2-304 E | 230 | 345 | 75 | 0 | 1.4 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY | AE2-304
316142 | AD1-160 C | 115 | 345 | 75 | 0 | 6.6 | 5.3 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AD1-160
314559 | 3CAROLNA | 115 | 345 | 75 | 0 | 1.21 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
934362 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 4.58 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AD1-060
314648 | 6SUNBURY | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314620 | 6CASHIE | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314551 | 3AHOSKIE | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314626 | 3WOODLND | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314596 | 3POPLR C | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314582 | 3KELFORD | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Z2-043
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 3.93 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY
926451 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 3.77 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AC1-116
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 3.61 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 3.05 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | Z2-030
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 2.81 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB2-099
942851 | AE2-304 C | 230 | 345 | 75 | 0 | 3.3 | 2.65 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | AE2-304
314638 | 6ELIZ CT | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | Y1-086
314662 | 6S HERTFORD | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314594 | 6PLYMOTH | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314604 | 3SEABORD | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314762 | 3JAMES R | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 1.61 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY
314639 | 6TANGLEW | 230 | 345 | 75 | 0 | 0.32 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | Z2-027
314177 | 3HAYES89 | 115 | 345 | 75 | 0 | 0.31 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.2 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | Z1-068
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 1.04 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY
314294 | 6ENON | 230 | 345 | 75 | 0 | 0.23 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.64 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.56 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY
313812 | 6ROCKLANDING | 230 | 345 | 75 | 0 | 0.11 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314453 | 6CHRHLND | 230 | 345 | 75 | 0 | 0.08 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
313828 | 3WHITEMARSH | 115 | 345 | 75 | 0 | 0.05 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
313826 | 6HYDRAULIC | 230 | 345 | 75 | 0 | 0.04 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314640 | 6KITTY HAWK | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
314487 | 3MCLAUGH | 115 | 345 | 75 | 0 | 0.01 | 0 |  |  | 0.00031 |  |  | 0 |  | 1 | NEWENERGY
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 0 |  |  | 0.00029 |  |  | 0 |  | 1 | NEWENERGY | K11
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 443.98 |  |  | 0.00029 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM2
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 440.13 |  |  | 0.00029 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 419.81 |  |  | 0.00029 |  |  | 0.10478 |  | 1 | CAPACITY
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 404.48 |  |  | 0.00029 |  |  | 0.0316 |  | 1 | CAPACITY
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 403.68 |  |  | 0.00029 |  |  | 0.0316 |  | 1 | CAPACITY
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 403.27 |  |  | 0.00029 |  |  | 0.0316 |  | 1 | CAPACITY
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 403.2 |  |  | 0.00029 |  |  | 0.0316 |  | 1 | CAPACITY
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | 0.00029 |  |  | 0.0316 |  | 1 | CAPACITY
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | 0.00029 |  |  | 0.0316 |  | 1 | CAPACITY
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | T157
315616 | AA1-038 C | 230 | 345 | 74 | 0 | 76.6 | 0 |  |  | 0.00029 |  |  | 0 |  | 1 | NEW | AA1-038
918232 | AA1-038 E | 230 | 345 | 74 | 0 | 66.7 | 0 |  |  | 0.00029 |  |  | 0 |  | 1 | NEWENERGY | AA1-038
314860 | 4E MILL | 138 | 345 | 2 | 0 | 50 | 0 |  |  | 0.00029 |  |  | 0.10478 |  | 1 | ENERGY
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | Z2-088
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-059
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-043
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-060
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB1-081
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 0 |  |  | 0.00029 |  |  | 0 |  | 1 | NEWENERGY | AC1-075
919702 | AA2-057 E OP | 115 | 345 | 75 | 0 | 21.1 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AA2-057
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AC1-054
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AC1-105
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 52.99 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB2-059
922922 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 44.96 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB1-081
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 43.67 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB2-060
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 53 | 42.55 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Z2-088
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AC1-036
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 36.61 |  |  | 0.0003 |  |  | 0.10478 |  | 1 | CAPACITY
313719 | 3CHESTNUT | 115 | 345 | 75 | 0 | 44.7 | 35.89 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AA2-057
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 35.73 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AC1-054
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | 0.0003 |  |  | 0.08446 |  | 1 | CAPACITY
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | 0.0003 |  |  | 0.08446 |  | 1 | CAPACITY
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | 0.0003 |  |  | 0.07484 |  | 1 | CAPACITY
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | 0.0003 |  |  | 0.07484 |  | 1 | CAPACITY
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | 0.0003 |  |  | 0.07484 |  | 1 | CAPACITY
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | 0.0003 |  |  | 0.07484 |  | 1 | CAPACITY
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | 0.0003 |  |  | 0.07484 |  | 1 | CAPACITY
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | 0.0003 |  |  | 0.07484 |  | 1 | CAPACITY
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-077
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-079
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-078
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 30.75 |  |  | 0.00029 |  |  | 0 |  | 1 | CAPACITY | AC1-075
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 30.67 |  |  | 0.00029 |  |  | 0 |  | 1 | CAPACITY | K11
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 0 |  |  | 0.00029 |  |  | 0 |  | 1 | NEWENERGY | AC1-080
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 27.7 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AC1-105
314608 | 3TARBORO | 115 | 345 | 75 | 0 | 6.2 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314574 | 6EVERETS | 230 | 345 | 75 | 0 | 5.89 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 23.68 |  |  | 0.00029 |  |  | 0.12623 |  | 1 | CAPACITY
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AE1-098
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AE1-099
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 20.23 |  |  | 0.00029 |  |  | 0.10478 |  | 1 | CAPACITY
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 20.15 |  |  | 0.00029 |  |  | 0.10478 |  | 1 | CAPACITY
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | AA1-067
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 16.46 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | T157
313853 | 3PONTONDP | 115 | 345 | 2 | 0 | 4 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | ENERGY
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 15.17 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AB2-043
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY | Z2-044
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 16 | 12.85 |  |  | 0.0003 |  |  | 0.12623 |  | 1 | CAPACITY
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 12.04 |  |  | 0.0003 |  |  | 0.07484 |  | 1 | CAPACITY
926023 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 10.28 |  |  | 0.00029 |  |  | 0 |  | 1 | CAPACITY | AC1-080
314623 | 3WITAKRS | 115 | 345 | 75 | 0 | 2.51 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Z2-044
924321 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | 0.0003 |  |  | 0 |  | 1 | NEW | AB2-079
924311 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | 0.0003 |  |  | 0 |  | 1 | NEW | AB2-078
924301 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | 0.0003 |  |  | 0 |  | 1 | NEW | AB2-077
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 9.55 |  |  | 0.00029 |  |  | 0.08446 |  | 1 | CAPACITY
314593 | 3PARMELE | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AE1-098
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AE1-099
925611 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 6.9 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | AC1-036
314554 | 3BTLEBRO | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 4.41 |  |  | 0.00029 |  |  | 0 |  | 1 | CAPACITY
314557 | 3BETHELC | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314549 | 3TOT1 | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314607 | 3TAR RVR | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314205 | 3HEARTS | 115 | 345 | 75 | 0 | 0.41 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314545 | 3TOT5 | 115 | 345 | 75 | 0 | 0.32 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314629 | 3MARTNCO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314560 | 3CNETO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
314798 | 3MERCK5 | 115 | 345 | 75 | 0 | 0.16 | 0 |  |  | 0.0003 |  |  | 0 |  | 1 | NEWENERGY
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 154.95 |  |  | 0.00028 |  |  | 0.0316 |  | 1 | CAPACITY
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 152.54 |  |  | 0.00028 |  |  | 0.0316 |  | 1 | CAPACITY
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 144.51 |  |  | 0.00028 |  |  | 0.10478 |  | 1 | CAPACITY
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 0 |  |  | 0.00029 |  |  | 0 |  | 1 | NEWENERGY | AC1-145
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 97.14 |  |  | 0.00028 |  |  | 0.0316 |  | 1 | CAPACITY
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 59.41 |  |  | 0.00028 |  |  | 0.0316 |  | 1 | CAPACITY
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 57 |  |  | 0.00028 |  |  | 0.0316 |  | 1 | CAPACITY
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0 |  |  | 0.00028 |  |  | 0 |  | 1 | NEWENERGY | AC1-117
244012 | 05PINNACLE | 4 | 205 | 1 | 0 | 11 | 0 |  |  | 0.00029 |  |  | 0.10478 |  | 1 | ENERGY
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | 0.00028 |  |  | 0.05 |  | 1 | MTX | AA1-100
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 42.07 |  |  | 0.00029 |  |  | 0.10478 |  | 1 | CAPACITY
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.9 | 40.06 |  |  | 0.00028 |  |  | 0.07484 |  | 1 | CAPACITY
926461 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0 |  |  | 0.00028 |  |  | 0 |  | 1 | NEW | AC1-117
926645 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 15.25 |  |  | 0.00029 |  |  | 0 |  | 1 | CAPACITY | AC1-145
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 3.21 |  |  | 0.00028 |  |  | 0 |  | 1 | CAPACITY
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 489.98 |  |  | 0.00027 |  |  | 0.10478 |  | 1 | CAPACITY
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 0 |  |  | 0.00028 |  |  | 0 |  | 1 | NEWENERGY | U2-073 A
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | Y1-006
235520 | 01WVACO_S38 | 13.8 | 201 | 2 | 0 | 60 | 0 |  |  | 0.00028 |  |  | 0 |  | 1 | NEW
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 0 |  |  | 0.00028 |  |  | 0 |  | 1 | NEWENERGY | S14
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | U2-030
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 0 |  |  | 0.00028 |  |  | 0 |  | 1 | NEWENERGY | U2-073 B
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 106.94 |  |  | 0.00028 |  |  | 0.07484 |  | 1 | CAPACITY
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 127.4 | 102.28 |  |  | 0.00027 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 101.08 |  |  | 0.00027 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | AC1-048
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 106.7 | 85.67 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 84.78 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEW | AC1-048
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0 |  |  | 0.00028 |  |  | 0 |  | 1 | NEWENERGY | AD1-018
205910 | AC2-053 E | 0.39 | 227 | 74 | 0 | 12.4 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | AC2-053
208904 | HOLT 696 | 13.2 | 229 | 60 | 23 | 58.4 | 46.89 |  |  | 0.00028 |  |  | 0.07484 |  | 1 | CAPACITY
208903 | HOLT 695 | 13.2 | 229 | 60 | 26 | 53.2 | 42.71 |  |  | 0.00028 |  |  | 0.07484 |  | 1 | CAPACITY
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
913034 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEW | Y1-006
242677 | 05INDDRV | 138 | 205 | 64 | 0 | 45 | 36.13 |  |  | 0.00027 |  |  | 0.12623 |  | 1 | CAPACITY
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0 |  |  | 0.00028 |  |  | 0 |  | 1 | NEW | AD1-018
205909 | AC2-053 C | 0.39 | 227 | 74 | 0 | 7.6 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEW | AC2-053
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | 0.00028 |  |  | 0.07484 |  | 1 | CAPACITY
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | 0.00028 |  |  | 0.07484 |  | 1 | CAPACITY
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | 0.00027 |  |  | 0.07484 |  | 1 | ENERGY
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 25.9 | 20.79 |  |  | 0.00028 |  |  | 0 |  | 1 | CAPACITY | U2-073 A
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | MTX | AD2-205
919535 | V4-027 E | 0 | 229 | 75 | 0 | 3.1 | 0 |  |  | 0.00028 |  |  | 0 |  | 1 | NEWENERGY | V4-027
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 15 | 12.04 |  |  | 0.00028 |  |  | 0 |  | 1 | CAPACITY | U2-073 B
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 14.1 | 11.32 |  |  | 0.00027 |  |  | 0.07484 |  | 1 | CAPACITY
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 11.24 |  |  | 0.00028 |  |  | 0 |  | 1 | CAPACITY | S14
923761 | AB2-010 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEW | AB2-010
923762 | AB2-010 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | AB2-010
923771 | AB2-011 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEW | AB2-011
923772 | AB2-011 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | AB2-011
270148 | AE1-018 E | 138 | 205 | 75 | 0 | 2.2 | 0 |  |  | 0.00028 |  |  | 0 |  | 1 | NEWENERGY | AE1-018
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 8.59 |  |  | 0.00028 |  |  | 0 |  | 1 | CAPACITY | N47
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.7 | 7.79 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 6.42 |  |  | 0.00028 |  |  | 0 |  | 1 | CAPACITY
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 6.26 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY | U2-030
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 3.93 |  |  | 0.00028 |  |  | 0 |  | 1 | CAPACITY | V4-027
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 3.29 |  |  | 0.00028 |  |  | 0 |  | 1 | CAPACITY
208474 | KINZ 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | 0.00028 |  |  | 0 |  | 1 | CAPACITY
270147 | AE1-018 C | 138 | 205 | 75 | 0 | 2.8 | 2.25 |  |  | 0.00028 |  |  | 0 |  | 1 | CAPACITY | AE1-018
237085 | AD2-192 GEN | 23 | 201 | 57 | 0 | 600 | 0 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | NEW
293798 | W4-005 E | 0.69 | 222 | 74 | 0 | 305.37 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | W4-005
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1396 | 1120.79 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | GVG2
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1371 | 1100.72 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | GVG1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1088.67 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | RKG1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1356 | 1088.67 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | MTG1
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1067.8 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | AMG3
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1043.71 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | RKG2
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 949.78 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
274656 | BYRON ;1U | 25 | 222 | 45 | 700 | 1168.5 | 938.14 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 926.5 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1148 | 921.68 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
274657 | BYRON ;2U | 25 | 222 | 45 | 700 | 1141.5 | 916.46 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
274661 | LASCO STA;2U | 25 | 222 | 49 | 150 | 1135.9 | 911.97 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
274660 | LASCO STA;1U | 25 | 222 | 49 | 150 | 1131.2 | 908.19 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 814.5 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 200 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Q57
918472 | AA1-062 E | 138 | 201 | 74 | 0 | 195 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | AA1-062
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | X2-022
274663 | QUAD CITI;2U | 18 | 222 | 48 | 150 | 911.7 | 731.97 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
274662 | QUAD CITI;1U | 18 | 222 | 48 | 150 | 911.1 | 731.48 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
274658 | DRESDEN ;2U | 18 | 222 | 48 | 150 | 902.5 | 724.58 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
274659 | DRESDEN ;3U | 18 | 222 | 48 | 150 | 895.5 | 718.96 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Z2-087
930042 | AB1-006 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AB1-006
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | U3-002 2
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | V3-007
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | U2-090
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | O50
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 159.7 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | S06
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Q01 3
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | S27
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | S28
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | O22 2
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 642.29 |  |  | 0.00027 |  |  | 0.10478 |  | 1 | CAPACITY
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 642.29 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | P10
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 589.3 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | ZIMM
293799 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | S36
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | S37
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 570.03 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AA1-018
235586 | 01HARRN2 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
235585 | 01HARRN1 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
235587 | 01HARRN3 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Q01 4
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 124 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | ENERGY | L05_CE22
253314 | AC1-085 A_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 A
253317 | AC1-085 B_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 B
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | O51 2
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | O51 1
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | N15
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 470.47 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | ZIMM
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC2-176
927091 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-204
927093 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AC1-204
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 443.18 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 437.96 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 415.88 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 415.88 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 409.46 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
274687 | WILL CNTY;4U | 20 | 222 | 15 | 0 | 510 | 409.46 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | WILL4
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | P36 1
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | P36 2
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | S71
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC1-089
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | O29 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | P26
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | P59
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | M24
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Q01 21
293516 | O-009 E1 | 0.69 | 222 | 74 | 0 | 82.04 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | O09 1
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 81.6 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | O22 1
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | P11 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | P11 2
294763 | P-046 E | 12 | 222 | 74 | 0 | 80 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | P46
247943 | T-127 E | 0.74 | 205 | 74 | 0 | 80 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | T127 5
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 80 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | T127 4
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 80 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | T126 2
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 80 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | T126 3
247903 | 05FR-22G E | 0.69 | 205 | 75 | 0 | 78.8 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Q01 22
247900 | 05FR-11G E | 0.6 | 205 | 75 | 0 | 78.3 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Q01 11
930062 | AB1-014 E | 138 | 212 | 75 | 0 | 77.5 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AB1-014
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 522.66 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Q01 12
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-116
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AA2-116
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 284.53 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK8
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 268.96 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 267.35 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AA2-116
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | W2-048
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 263.34 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK7
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-169
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AB1-169
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 244.87 |  |  | 0.00027 |  |  | 0.10478 |  | 1 | CAPACITY
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | O35
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 240.86 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | K28
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 294 | 236.04 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-079
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 225.6 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 201.52 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | X2-052
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | O29 2
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 193.49 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | NQ71
293518 | O-009 E3 | 0.57 | 222 | 74 | 0 | 45.89 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | O09 3
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | X2-052
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | X2-052
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 45.5 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Z1-073
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AB1-169
916211 | Z1-072 E | 0.6 | 222 | 74 | 0 | 44.8 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Z1-072
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 180.64 |  |  | 0.00027 |  |  | 0.10478 |  | 1 | CAPACITY
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | O29 3
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | AB1-150
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | U2-061
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 219 | 175.82 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Z1-079
293517 | O-009 E2 | 0.6 | 222 | 74 | 0 | 41.67 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | O09 2
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 162.9 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 2
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
274708 | KENDALL ;3C | 18 | 222 | 58 | 140 | 184.3 | 147.97 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 3
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 146.36 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 2
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 146.36 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 138 | 182.3 | 146.36 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 4
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 144.51 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
247225 | 05FTHLG2 | 18 | 205 | 57 | 120 | 173.8 | 139.54 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247224 | 05FTHLG1 | 18 | 205 | 57 | 120 | 173.7 | 139.46 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 2
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 1
247230 | 05RIVRG1 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247232 | 05RIVRG3 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247231 | 05RIVRG2 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 136.16 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | NELSON
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 135.12 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | NELSON
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 134.32 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 134.16 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 132.47 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 131.75 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | 0.00027 |  |  | 0.05 |  | 1 | MTX | M24 BAT
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 130.06 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | CORDOVA
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC2-067
919221 | AA1-146 | 345 | 222 | 58 | 0 | 157 | 126.05 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
292981 | N-007 E | 138 | 201 | 74 | 0 | 30.4 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | N07
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
235801 | 01WM_AA1_062 | 138 | 201 | 74 | 0 | 29 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEW | AA1-062
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | ENERGY
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | CLIF5
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | CLIF1
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF2
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | CLIF6
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | CLIF4
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | CLIF3
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 99.72 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | KYG1
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 99.47 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | NELSON
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | KYG4
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | KYG2
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | KYG5
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | KYG3
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 98.59 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | NELSON
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 97.87 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Kendall 1
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 97.87 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Kendall 2
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 97.87 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Kendall 4
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 97.87 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Kendall 3
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | K28
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 96.42 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 93.13 |  |  | 0.00027 |  |  | 0.10478 |  | 1 | CAPACITY
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | NQ72
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 115.4 | 92.65 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | EQUISTAR MORRIS
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 109.5 | 87.91 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 75.6 | 104 | 83.5 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 72.7 | 101.6 | 81.57 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
920072 | AA2-103 E | 138 | 201 | 76 | -20 | 20 | 0 |  |  | 0.00027 |  |  | 0.05 |  | 1 | MTX | AA2-103
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.00026 |  |  | 0.05 |  | 1 | MTX | AA2-123
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.00026 |  |  | 0.05 |  | 1 | MTX | Z1-108
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | 0.00026 |  |  | 0.05 |  | 1 | MTX | Z1-107
276592 | O-012 C | 138 | 222 | 64 | 0 | 20 | 0 |  |  | 0.00026 |  |  | 0.12623 |  | 1 | ENERGY
902531 | W2-040 C | 69 | 209 | 75 | 0 | 20 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEW | W2-040
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 80.93 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 71.2 | 100.6 | 80.77 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 80.69 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 133.1 | 153 | 133.28 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 80.21 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 129.7 | 149.1 | 129.88 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 128.6 | 147.8 | 128.75 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
243415 | 05WWVSTA | 69 | 205 | 61 | 60 | 96 | 77.08 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 67.52 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC1-165
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC1-166
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 65.51 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 81.5 | 65.43 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 65.03 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.8 | 64.87 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC1-069
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC1-068
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 64.31 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 64.23 |  |  | 0.00027 |  |  | 0.07484 |  | 1 | CAPACITY
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 64.23 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 64.23 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 63.43 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 62.14 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
250166 | HLCRST AB114 | 138 | 212 | 75 | 0 | 76 | 61.02 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AB1-014
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AC1-085 B
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AC1-085 A
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 60.94 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 60.78 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 60.7 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 60.53 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | CLIF2
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF4
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF6
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF5
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF1
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF3
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 58.77 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 72.9 | 58.53 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 58.45 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | KYG1
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 72.6 | 58.29 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | KYG2
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | KYG5
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY | KYG4
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | KYG3
251958 | 08MADSN7 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251957 | 08MADSN6 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251952 | 08MADSN1 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251954 | 08MADSN3 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251955 | 08MADSN4 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251953 | 08MADSN2 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251956 | 08MADSN5 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251959 | 08MADSN8 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 56.84 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 56.2 |  |  | 0.00027 |  |  | 0.07484 |  | 1 | CAPACITY
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 55.4 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 52.91 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
902532 | W2-040 E | 69 | 209 | 75 | 0 | 12.4 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | W2-040
251828 | CLNTESP1 | 34.5 | 212 | 76 | 0 | 12 | 0 |  |  | 0.00026 |  |  | 0.05 |  | 1 | MTX | Z1-080
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 48.09 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 47.93 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 46.65 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 46.41 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
926103 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 45.76 |  |  | 0.00026 |  |  | 0.05 |  | 1 | NEW | AC1-089
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 55 | 44.16 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 43.03 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | 0.00026 |  |  | 0.05 |  | 1 | MTX | Z1-106
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | 0.00026 |  |  | 0.05 |  | 1 | MTX | Z1-106
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 40.54 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | MIDDLETOWN COKE
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | 0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 37.49 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 36.93 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 36.61 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | W4-005
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Q57
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | O50
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 28.74 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | S28
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 28.18 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | O22 2
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | S37
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | S36
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 27.94 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | S27
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AC1-069
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AC1-068
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AC1-166
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AC1-165
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 42.68 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 42.6 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 42.51 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | 0.00026 |  |  | 0.05 |  | 1 | MTX | Z1-065
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 24.08 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
925972 | AC1-073 E | 138 | 201 | 74 | 0 | 5.9 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEWENERGY | AC1-073
925971 | AC1-073 C | 138 | 201 | 74 | 0 | 5.8 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | NEW | AC1-073
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 23.36 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Q01 4
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | X3-005
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 20.3 | 27.6 | 22.16 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 22 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | N15
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 21.68 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 21.28 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AC2-067
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 26 | 20.87 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | L05_CE22
274889 | BRIGHTSTK;1U | 0.7 | 222 | 74 | 0 | 26 | 20.87 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Z2-087
930041 | AB1-006 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AB1-006
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | V3-007
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 20.87 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | U2-090
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 20.79 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | S06
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 20.63 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Q01 11
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 20.07 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 19.27 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | S71
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | O51 2
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | O51 1
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 17.58 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | O29 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 17.58 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | P26
293513 | O-009 C1 | 0.69 | 222 | 74 | 0 | 20.5 | 16.46 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | O09 1
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 16.22 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | T127 5
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | P11 2
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | P11 1
274891 | OTTER CRK;1U | 0.69 | 222 | 74 | 0 | 19.5 | 15.66 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AA1-018
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 15.58 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | P46
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 14.77 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | O22 1
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.4 | 13.97 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY | K28
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 22.91 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
933594 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 13.57 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AC2-176
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 12.28 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | T126 3
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | P36 1
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | P36 2
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 12.2 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | T126 2
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 12.04 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY | M24
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 11.88 |  |  | 0.00027 |  |  | 0.07484 |  | 1 | CAPACITY
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | 0.00027 |  |  | 0.07484 |  | 1 | CAPACITY
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | 0.00027 |  |  | 0.07484 |  | 1 | CAPACITY
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 13.3 | 10.68 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Z1-073
276173 | Z2-081 | 138 | 222 | 2 | 0 | 13.3 | 10.68 |  |  | 0.00026 |  |  | 0.12623 |  | 1 | CAPACITY
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 10.6 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | U3-002 1
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 10.44 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Q01 21
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 10.44 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Q01 22
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 10.36 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 10.28 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | U3-002 2
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Q01 12
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Q01 3
904211 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 9.71 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 9.64 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | O29 2
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | 0.00026 |  |  | 0.12623 |  | 1 | CAPACITY
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 9.47 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | T127 4
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 9.39 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY | P59
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Z2-113
293515 | O-009 C3 | 0.57 | 222 | 74 | 0 | 11.5 | 9.23 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | O09 3
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 8.91 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | O29 3
904201 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 8.51 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
293514 | O-009 C2 | 0.6 | 222 | 74 | 0 | 10.4 | 8.35 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | O09 2
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 10.3 | 8.27 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | O35
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 8.19 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | P10
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | 0.00027 |  |  | 0 |  | 1 | MTX | AB1-055
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | MTX | Y3-100
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | MTX | Y3-099
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 10 | 8.03 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Z1-072
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 8.03 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.6 | 7.71 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 6.5 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY | K19
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | V4-073
235000 | N-007 C | 138 | 201 | 74 | 0 | 7.6 | 6.1 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY | N07
295108 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 5.7 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | NQ71
931011 | AB1-150 C | 138 | 201 | 74 | 0 | 6.7 | 5.38 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY | AB1-150
247969 | Z2-116 E | 138 | 205 | 76 | 0 | 1.3 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Z2-116
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 5.22 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY | U2-061
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 5.14 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
247968 | Z2-115 E | 12 | 205 | 74 | 0 | 1.25 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | Z2-115
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 4.82 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
276159 | W4-082 | 138 | 222 | 64 | 0 | 5.8 | 4.66 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 4.66 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 4.41 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY
342550 | 4BAVARIAN LF | 138 | 320 | 2 | 0 | 4.8 | 3.85 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.8 | 3.85 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.61 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 3.13 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 2.73 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | X3-005
342070 | 2PINE GROVE | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY
341584 | 2GRIFFIN | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
295110 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 2.57 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | NQ72
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.55 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY
247604 | X1-042 | 12 | 205 | 64 | 0 | 3 | 2.41 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.8 | 2.25 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 2.09 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
341329 | 2COLESBURG | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY
342031 | 2PACTOLUS | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 1.85 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Z2-113
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.76 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
341200 | 2BROMLEYEK | 69 | 320 | 2 | 0 | 2 | 1.61 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.5 | 1.2 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 1.3 | 1.04 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 1.04 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Z2-116
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 1 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Z2-115
342442 | 2W GLASGOW | 69 | 320 | 2 | 0 | 1 | 0.8 |  |  | 0.00027 |  |  | 0 |  | 1 | CAPACITY
904721 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.76 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | V4-073
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | U2-072
247919 | U2-041 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | U2-041
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 0 |  |  | 0.00025 |  |  | 0 |  | 1 | NEWENERGY | V4-010
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 634.42 |  |  | 0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 618.28 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 533.66 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-173
893022 | V2-006 E | 138 | 205 | 74 | 0 | 130.5 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | V2-006
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 120.8 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | R49
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-067
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AB2-067
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-044
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | T131
924440 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 389.39 |  |  | 0.00025 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-093
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 94.4 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | R60 3
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | R60 1
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | R60 2
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | V1-011
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | 0.00025 |  |  | 0 |  | 1 | NEWENERGY | U4-028
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | 0.00025 |  |  | 0 |  | 1 | NEWENERGY | U4-029
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 292.88 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC1-173
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 261.89 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY | OREGON
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 318.8 | 255.95 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | RONCO
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 248.73 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY | AB1-107
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 238.45 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | 0.00025 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-107
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | 0.00025 |  |  | 0.04435 |  | 1 | CAPACITY | OREGON
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY | OREGON
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 225.4 | 180.96 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | U1-059
247529 | 05COVRT2 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 2
247530 | 05COVRT3 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 3
247528 | 05COVRT1 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 1
247506 | U2-041 C | 345 | 205 | 74 | 0 | 39 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | U2-041
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | WASHINGTON
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | RONCO
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | RONCO
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | DRESDEN
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | 0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | WATERFORD
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | 0.00025 |  |  | 0.08446 |  | 1 | CAPACITY
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | 0.00025 |  |  | 0.08446 |  | 1 | CAPACITY
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | 0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | 0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 120.19 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 109.19 |  |  | 0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
247531 | 05COVRT4 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Covert 1
247533 | 05COVRT6 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Covert 3
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 0 |  |  | 0.00025 |  |  | 0 |  | 1 | NEW | V4-010
247532 | 05COVRT5 | 16.5 | 205 | 58 | 90 | 131.2 | 105.33 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | Covert 2
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.66 | 96.07 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 91.93 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 0 |  |  | 0.00025 |  |  | 0 |  | 1 | NEWENERGY
893021 | V2-006 C | 138 | 205 | 74 | 0 | 19.5 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | V2-006
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 77.88 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
927184 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | 0.00026 |  |  | 0.05 |  | 1 | MTX | AC1-212
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | W1-056
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 61.42 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 51.78 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 51.38 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | V3-028
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | U1-059
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | 0.00025 |  |  | 0.08446 |  | 1 | CAPACITY
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | 0.00025 |  |  | 0.08446 |  | 1 | CAPACITY
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 31.31 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | U2-072
247549 | V3-028 C | 345 | 205 | 75 | 0 | 7.6 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | V3-028
930262 | AB1-065 E | 34.5 | 201 | 75 | 0 | 6.8 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
932312 | AC2-045 E | 69 | 205 | 75 | 0 | 6.2 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC2-045
247521 | T131 | 0.69 | 205 | 74 | 22.4 | 30 | 24.08 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | T131
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | 0.00025 |  |  | 0.07484 |  | 1 | CAPACITY
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | 0.00025 |  |  | 0.07484 |  | 1 | CAPACITY
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 18.39 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | R49
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 17.66 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | 0.00026 |  |  | 0.07484 |  | 1 | CAPACITY
235013 | 01AB1-065 C | 34.5 | 201 | 75 | 0 | 4.1 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | MTX
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 19.5 | 15.66 |  |  | 0.00025 |  |  | 0.08446 |  | 1 | CAPACITY
932311 | AC2-045 C | 69 | 205 | 75 | 0 | 3.8 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEW | AC2-045
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 15.25 |  |  | 0.00025 |  |  | 0.07484 |  | 1 | CAPACITY
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 13.25 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | R60 3
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | R60 2
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | R60 1
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 10.68 |  |  | 0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
247607 | V1-011 C | 34.5 | 205 | 74 | 0 | 13 | 10.44 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | V1-011
247552 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | 0.00025 |  |  | 0 |  | 1 | NEW | U4-029
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | 0.00025 |  |  | 0 |  | 1 | NEW | U4-028
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 10.19 |  |  | 0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | 0.00026 |  |  | 0.12623 |  | 1 | CAPACITY
294740 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | ENERGY
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 8.83 |  |  | 0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
926865 | AC1-173 C | 0.65 | 205 | 75 | 0 | 9.9 | 7.95 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AC1-173
903052 | W2-094 E | 115 | 227 | 75 | 0 | 1.9 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | W2-094
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 5.14 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY
205911 | 27W2-094 | 115 | 227 | 75 | 0 | 1.1 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | W2-094
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 4.41 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY | N32
245413 | 05S FULTHA | 69 | 205 | 65 | 0 | 0.85 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | ENERGY
208876 | WLAN | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.93 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | W1-056
927183 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.53 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AC1-212
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | 0.00025 |  |  | 0 |  | 1 | NEW | AB1-069
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | 0.00025 |  |  | 0.04435 |  | 1 | NEW | AB1-069
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | 0.00025 |  |  | 0 |  | 1 | NEW | AB1-069
237082 | AA2-121 | 345 | 201 | 58 | 0 | 830 | 666.37 |  |  | 0.00024 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-121
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 503.47 |  |  | 0.00024 |  |  | 0.04435 |  | 1 | CAPACITY | AVON LAKE
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 498.09 |  |  | 0.00024 |  |  | 0.10478 |  | 1 | CAPACITY
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 780.51 |  |  | 0.00025 |  |  | 0.01494 |  | 1 | CAPACITY
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | 0.00024 |  |  | 0.10478 |  | 1 | CAPACITY
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | 0.00024 |  |  | 0.10478 |  | 1 | CAPACITY
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 364.2 | 292.4 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY | FREMONT
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 272 | 218.38 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | 0.00024 |  |  | 0.04435 |  | 1 | CAPACITY | Y2-050
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 170 | 136.49 |  |  | 0.00025 |  |  | 0.04435 |  | 1 | CAPACITY | FREMONT
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 166.4 | 133.6 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY | FREMONT
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | 0.00024 |  |  | 0.07484 |  | 1 | CAPACITY
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | 0.00024 |  |  | 0.07484 |  | 1 | CAPACITY
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 77.07 |  |  | 0.00024 |  |  | 0.07484 |  | 1 | CAPACITY
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | 0.00024 |  |  | 0.07484 |  | 1 | CAPACITY
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | 0.00024 |  |  | 0.07484 |  | 1 | CAPACITY
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 62.22 |  |  | 0.00024 |  |  | 0.08446 |  | 1 | CAPACITY
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | 0.00024 |  |  | 0.08446 |  | 1 | CAPACITY
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | 0.00024 |  |  | 0.08446 |  | 1 | CAPACITY
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 60.86 |  |  | 0.00024 |  |  | 0.08446 |  | 1 | CAPACITY
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 60.29 |  |  | 0.00024 |  |  | 0.08446 |  | 1 | CAPACITY
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 60 | 48.17 |  |  | 0.00025 |  |  | 0.08446 |  | 1 | CAPACITY
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 41.03 |  |  | 0.00024 |  |  | 0.12623 |  | 1 | CAPACITY
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 39.82 |  |  | 0.00024 |  |  | 0.12623 |  | 1 | CAPACITY
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 38.54 |  |  | 0.00024 |  |  | 0.07484 |  | 1 | CAPACITY
936011 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 16.06 |  |  | 0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 11.24 |  |  | 0.00024 |  |  | 0.12623 |  | 1 | CAPACITY
208769 | SISO | 12.5 | 229 | 2 | 0 | 2.48 | 0 |  |  | 0.00025 |  |  | 0 |  | 1 | ENERGY
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 8.03 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 7.95 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 3.21 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 1.85 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY
253900 | 15BVRVL1 | 22 | 215 | 44 | 843.9 | 970 | 844.97 |  |  | 0.00024 |  |  | 0.01494 |  | 1 | CAPACITY
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | 0.00024 |  |  | 0.10478 |  | 1 | CAPACITY
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | 0.00024 |  |  | 0.10478 |  | 1 | CAPACITY
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 783.39 |  |  | 0.00024 |  |  | 0.01494 |  | 1 | CAPACITY
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 455.62 |  |  | 0.00024 |  |  | 0.10478 |  | 1 | CAPACITY
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 329.17 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | AA1-044
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 261.73 |  |  | 0.00023 |  |  | 0 |  | 1 | CAPACITY | T-174
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | AA1-123
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | 0.00023 |  |  | 0 |  | 1 | CAPACITY | T-174
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | 0.00023 |  |  | 0.04435 |  | 1 | CAPACITY | T-174
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 300.6 | 241.34 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | Z2-028
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | 0.00024 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-044
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 233.87 |  |  | 0.00024 |  |  | 0.10478 |  | 1 | CAPACITY
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | 0.00024 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-028
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | Z2-028
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | 0.00024 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-123
239024 | 02NWCAG5 | 16.5 | 202 | 58 | 23 | 141 | 113.2 |  |  | 0.00023 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 81.57 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND
253970 | 15BI2 | 13.8 | 215 | 58 | 60 | 96.2 | 77.24 |  |  | 0.00024 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
239022 | 02NWCAG3 | 14.4 | 202 | 58 | 20 | 92.3 | 74.11 |  |  | 0.00023 |  |  | 0.04435 |  | 1 | CAPACITY | NEW CASTLE
239023 | 02NWCAG4 | 14.4 | 202 | 58 | 20 | 92 | 73.86 |  |  | 0.00023 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | 0.00024 |  |  | 0.10478 |  | 1 | ENERGY
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 0 |  |  | 0.00023 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | Y3-103
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.7 | 39.1 |  |  | 0.00024 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0 |  |  | 0.00024 |  |  | 0 |  | 1 | NEWENERGY | W1-045
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0 |  |  | 0.00024 |  |  | 0 |  | 1 | NEWENERGY | AC2-168
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | 0.00024 |  |  | 0.04435 |  | 1 | CAPACITY | Y3-103
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 24.6 | 19.75 |  |  | 0.00024 |  |  | 0.12623 |  | 1 | CAPACITY
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 21 | 16.86 |  |  | 0.00024 |  |  | 0.12623 |  | 1 | CAPACITY
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 16.46 |  |  | 0.00023 |  |  | 0.12623 |  | 1 | CAPACITY
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 19.6 | 15.74 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 14.53 |  |  | 0.00024 |  |  | 0.08446 |  | 1 | CAPACITY
209030 | FRFA O01 | 12.5 | 229 | 2 | 0 | 3.2 | 0 |  |  | 0.00024 |  |  | 0 |  | 1 | NEW
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 0 |  |  | 0.00023 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
933531 | AC2-168 C | 138 | 215 | 75 | 0 | 7.55 | 6.06 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | AC2-168
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.5 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.13 | 4.12 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | W1-045
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 3.21 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 2.01 |  |  | 0.00023 |  |  | 0 |  | 1 | CAPACITY
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 1.37 |  |  | 0.00023 |  |  | 0 |  | 1 | CAPACITY | K20
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 0.4 | 0.32 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY | V3-051
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1086.27 |  |  | 0.00022 |  |  | 0.01494 |  | 1 | CAPACITY
920571 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 411.86 |  |  | 0.00023 |  |  | 0.04435 |  | 1 | NEW | AA2-161
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 361.29 |  |  | 0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 148.77 |  |  | 0.00023 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC1
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 39.5 | 31.71 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 28.1 |  |  | 0.00022 |  |  | 0.10478 |  | 1 | CAPACITY
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.82 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 353.26 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | 0.00022 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-076
913142 | Y1-033 E OP1 | 115 | 226 | 74 | 0 | 34.02 | 0 |  |  | 0.00022 |  |  | 0 |  | 1 | NEWENERGY | Y1-033
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 38.7 | 31.07 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
204638 | 27CAT TRAC | 13.2 | 227 | 58 | 0 | 32.3 | 25.93 |  |  | 0.00021 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
204555 | 27QUEEN ST | 115 | 227 | 74 | 0 | 5 | 0 |  |  | 0.00021 |  |  | 0 |  | 1 | NEWENERGY
204706 | 27CAT TRC2 | 13.2 | 227 | 58 | 0 | 13.9 | 11.16 |  |  | 0.00021 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 4.01 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY | Y1-033
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 3.05 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 140 | 182.2 | 146.28 |  |  | 0.00021 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 118.7 | 175.2 | 140.66 |  |  | 0.00021 |  |  | 0.04435 |  | 1 | CAPACITY | AE SPRINGDALE
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 118.7 | 172.2 | 138.25 |  |  | 0.00021 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | 0.00021 |  |  | 0.08446 |  | 1 | CAPACITY
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | 0.00021 |  |  | 0.08446 |  | 1 | CAPACITY
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 24.08 |  |  | 0.00021 |  |  | 0.10478 |  | 1 | CAPACITY
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 5.54 |  |  | 0.0002 |  |  | 0 |  | 1 | CAPACITY
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 853.3 | 685.08 |  |  | 0.00019 |  |  | 0.10478 |  | 1 | CAPACITY | Keys1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 853.1 | 684.92 |  |  | 0.00019 |  |  | 0.10478 |  | 1 | CAPACITY | Keys2
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 682.91 |  |  | 0.0002 |  |  | 0.10478 |  | 1 | CAPACITY | Cone1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 682.43 |  |  | 0.0002 |  |  | 0.10478 |  | 1 | CAPACITY | Cone2
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 400 | 321.14 |  |  | 0.0002 |  |  | 0.04435 |  | 1 | CAPACITY | AD2-114
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 0 |  |  | 0.0002 |  |  | 0 |  | 1 | NEWENERGY | K23
235622 | 01SBEND4 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | 0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
235620 | 01SBEND2 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | 0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
235621 | 01SBEND3 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | 0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
235619 | 01SBEND1 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | 0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 0 |  |  | 0.0002 |  |  | 0 |  | 1 | NEWENERGY | L13
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 0 |  |  | 0.0002 |  |  | 0 |  | 1 | NEWENERGY | O48
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | 0.0002 |  |  | 0.05 |  | 1 | MTX
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | 0.0002 |  |  | 0.05 |  | 1 | MTX
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 16.55 |  |  | 0.00019 |  |  | 0.07484 |  | 1 | CAPACITY
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 0 |  |  | 0.0002 |  |  | 0 |  | 1 | NEWENERGY | R40
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 6.1 |  |  | 0.00019 |  |  | 0 |  | 1 | CAPACITY
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 5.06 |  |  | 0.0002 |  |  | 0 |  | 1 | CAPACITY | O48
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 4.74 |  |  | 0.0002 |  |  | 0 |  | 1 | CAPACITY | L13
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 5.1 | 4.09 |  |  | 0.0002 |  |  | 0 |  | 1 | CAPACITY | K23
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 42 | 0 |  |  | 0.00018 |  |  | 0 |  | 1 | NEWENERGY | P60
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 68.24 |  |  | 0.00018 |  |  | 0.10478 |  | 1 | CAPACITY
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | 0.00018 |  |  | 0.08446 |  | 1 | CAPACITY
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | 0.00018 |  |  | 0.08446 |  | 1 | CAPACITY
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 42.95 |  |  | 0.00018 |  |  | 0.08446 |  | 1 | CAPACITY
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | 0.00018 |  |  | 0.08446 |  | 1 | CAPACITY
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 42.95 |  |  | 0.00018 |  |  | 0.08446 |  | 1 | CAPACITY
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 8.83 |  |  | 0.00018 |  |  | 0.12623 |  | 1 | CAPACITY
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 6.82 |  |  | 0.00018 |  |  | 0 |  | 1 | CAPACITY | P60
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 5.46 |  |  | 0.00019 |  |  | 0 |  | 1 | CAPACITY
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0 |  |  | 0.00018 |  |  | 0 |  | 1 | NEWENERGY | Y1-075
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | 0.00019 |  |  | 0 |  | 1 | CAPACITY
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.45 |  |  | 0.00019 |  |  | 0 |  | 1 | CAPACITY
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.72 |  |  | 0.00019 |  |  | 0 |  | 1 | CAPACITY | K22
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 0.00018 |  |  | 0 |  | 1 | CAPACITY | Y1-075
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 422.06 |  |  | 0.00017 |  |  | 0.10478 |  | 1 | CAPACITY
903644 | W3-099 E OP1 | 230 | 226 | 74 | 0 | 87 | 0 |  |  | 0.00017 |  |  | 0 |  | 1 | NEWENERGY | W3-099
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 60 | 0 |  |  | 0.00017 |  |  | 0 |  | 1 | NEWENERGY | R32
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 52 | 0 |  |  | 0.00017 |  |  | 0 |  | 1 | NEWENERGY | O18
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 23.2 | 0 |  |  | 0.00018 |  |  | 0 |  | 1 | NEWENERGY | K13
200805 | 26COLVER13 | 13.2 | 226 | 12 | 77 | 110 | 88.31 |  |  | 0.00017 |  |  | 0.10478 |  | 1 | CAPACITY
201144 | W3-099 C OP1 | 230 | 226 | 74 | 0 | 13 | 0 |  |  | 0.00017 |  |  | 0 |  | 1 | NEW | W3-099
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 24.24 |  |  | 0.00018 |  |  | 0.07484 |  | 1 | CAPACITY
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 10.44 |  |  | 0.00018 |  |  | 0.12623 |  | 1 | CAPACITY
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 10.19 |  |  | 0.00017 |  |  | 0 |  | 1 | CAPACITY | R32
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0 |  |  | 0.00018 |  |  | 0 |  | 1 | NEWENERGY | Y3-087
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 8.83 |  |  | 0.00018 |  |  | 0.12623 |  | 1 | CAPACITY
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 6.5 |  |  | 0.00017 |  |  | 0 |  | 1 | CAPACITY | O18
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.02 |  |  | 0.00018 |  |  | 0 |  | 1 | CAPACITY
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 2.57 |  |  | 0.00018 |  |  | 0 |  | 1 | CAPACITY | K13
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 1.84 |  |  | 0.00018 |  |  | 0 |  | 1 | CAPACITY | Y3-087
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | 0.00018 |  |  | 0 |  | 1 | CAPACITY
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 497.77 |  |  | 0.00017 |  |  | 0.10478 |  | 1 | CAPACITY
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 48 | 0 |  |  | 0.00016 |  |  | 0 |  | 1 | NEWENERGY | Q53
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 0 |  |  | 0.00017 |  |  | 0 |  | 1 | NEWENERGY | V3-030
200809 | 26SITHE | 138 | 226 | 15 | 0 | 36 | 28.9 |  |  | 0.00017 |  |  | 0.10478 |  | 1 | CAPACITY
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 5.14 |  |  | 0.00016 |  |  | 0 |  | 1 | CAPACITY | Q53
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 4.25 |  |  | 0.00017 |  |  | 0 |  | 1 | CAPACITY | V3-030
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 601.34 |  |  | 0.00015 |  |  | 0.10478 |  | 1 | CAPACITY
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 521.86 |  |  | 0.00016 |  |  | 0.10478 |  | 1 | CAPACITY
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 492.95 |  |  | 0.00016 |  |  | 0.10478 |  | 1 | CAPACITY
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 293.93 |  |  | 0.00015 |  |  | 0.10478 |  | 1 | CAPACITY | Bris2
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 0 |  |  | 0.00016 |  |  | 0 |  | 1 | NEWENERGY | N39
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 248.4 |  |  | 0.00015 |  |  | 0.10478 |  | 1 | CAPACITY | Bris1
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 0 |  |  | 0.00016 |  |  | 0 |  | 1 | NEWENERGY | O38
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 10.7 | 8.59 |  |  | 0.00016 |  |  | 0 |  | 1 | CAPACITY | N39
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.4 | 7.55 |  |  | 0.00016 |  |  | 0 |  | 1 | CAPACITY | O38
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 40 | 0 |  |  | 0.00014 |  |  | 0 |  | 1 | NEWENERGY | Q36
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 57 | 45.76 |  |  | 0.00015 |  |  | 0.08446 |  | 1 | CAPACITY
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | 0.00014 |  |  | 0 |  | 1 | ENERGY
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 6.66 |  |  | 0.00014 |  |  | 0 |  | 1 | CAPACITY | Q36
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 187.87 |  |  | 0.00014 |  |  | 0.0316 |  | 1 | CAPACITY
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 177.43 |  |  | 0.00014 |  |  | 0.0316 |  | 1 | CAPACITY
208947 | WSHO CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | 0.00013 |  |  | 0.08446 |  | 1 | CAPACITY
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 16.86 |  |  | 0.00014 |  |  | 0.07484 |  | 1 | CAPACITY
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 26.13 |  |  | 0.00014 |  |  | 0.07484 |  | 1 | CAPACITY
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 33.96 |  |  | 0.00012 |  |  | 0.10478 |  | 1 | CAPACITY
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4.82 |  |  | 0.00012 |  |  | 0 |  | 1 | CAPACITY
200665 | 26SHAWVL 3 | 22 | 226 | 12 | 120 | 174.2 | 139.86 |  |  | 0.00011 |  |  | 0.10478 |  | 1 | CAPACITY
200666 | 26SHAWVL 4 | 22 | 226 | 12 | 120 | 171 | 137.29 |  |  | 0.00011 |  |  | 0.10478 |  | 1 | CAPACITY
200722 | 26SHAWVL 2 | 18 | 226 | 12 | 62 | 124.7 | 100.12 |  |  | 0.00012 |  |  | 0.10478 |  | 1 | CAPACITY
200715 | 26SHAWVL 1 | 18 | 226 | 12 | 62 | 122 | 97.95 |  |  | 0.00012 |  |  | 0.10478 |  | 1 | CAPACITY
208942 | HARR CT | 12.5 | 229 | 55 | 0 | 42 | 33.72 |  |  | 0.00012 |  |  | 0.08446 |  | 1 | CAPACITY
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 24.08 |  |  | 0.00011 |  |  | 0.10478 |  | 1 | CAPACITY
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 9.64 |  |  | 0.00012 |  |  | 0.12623 |  | 1 | CAPACITY
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 8.19 |  |  | 0.00012 |  |  | 0.10478 |  | 1 | CAPACITY
208348 | EELI | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | 0.00012 |  |  | 0 |  | 1 | CAPACITY
210022 | LING 2 | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | 0.00012 |  |  | 0 |  | 1 | CAPACITY
236828 | 01GRAYMONT | 46 | 201 | 2 | 0 | 4 | 0 |  |  | 0.00011 |  |  | 0 |  | 1 | ENERGY
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | 0.00011 |  |  | 0 |  | 1 | MTX | AC1-025
210319 | WCAR 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | 0.00011 |  |  | 0 |  | 1 | CAPACITY
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | 9e-05 |  |  | 0.12623 |  | 1 | ENERGY
208697 | PRIN B34 | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | 9e-05 |  |  | 0 |  | 1 | CAPACITY
208885 | WNHO | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | 9e-05 |  |  | 0 |  | 1 | CAPACITY
922932 | AB1-082 OP | 46 | 201 | 55 | 0 | 19.9 | 0 |  |  | 9e-05 |  |  | 0.08446 |  | 1 | NEW
204664 | 27AES GEN3 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | 6e-05 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204662 | 27AES GEN1 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | 6e-05 |  |  | 0.04435 |  | 1 | CAPACITY | IRONWOOD
204663 | 27AES GEN2 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | 6e-05 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | 7e-05 |  |  | 0 |  | 1 | ENERGY
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.61 |  |  | 7e-05 |  |  | 0 |  | 1 | CAPACITY
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 0 |  |  | 6e-05 |  |  | 0 |  | 1 | NEWENERGY | Z1-069
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | 6e-05 |  |  | 0 |  | 1 | ENERGY
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 13.3 | 10.68 |  |  | 6e-05 |  |  | 0 |  | 1 | CAPACITY | Z1-069
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | 4e-05 |  |  | 0 |  | 1 | ENERGY
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0 |  |  | 4e-05 |  |  | 0 |  | 1 | NEWENERGY | X3-075
208580 | MGTN 2 | 12.5 | 229 | 2 | 0 | 4.8 | 3.85 |  |  | 4e-05 |  |  | 0 |  | 1 | CAPACITY
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY | P47
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 19 | 15.25 |  |  | 0 |  |  | 0.08446 |  | 1 | CAPACITY
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.8 | 12.69 |  |  | -1e-05 |  |  | 0 |  | 1 | CAPACITY | P47
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY | K02
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 17.18 |  |  | -2e-05 |  |  | 0.12623 |  | 1 | CAPACITY
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 16.86 |  |  | -2e-05 |  |  | 0.12623 |  | 1 | CAPACITY
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 16.86 |  |  | -3e-05 |  |  | 0.12623 |  | 1 | CAPACITY
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 389.39 |  |  | -5e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-115
920341 | AA2-132 | 34.5 | 226 | 55 | 0 | 19.9 | 0 |  |  | -5e-05 |  |  | 0.08446 |  | 1 | NEW
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 30.1 | 24.17 |  |  | -5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 4.82 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY
919201 | AA1-144 OP | 230 | 226 | 58 | 0 | 163 | 130.87 |  |  | -7e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-144
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 6 | 4.82 |  |  | -7e-05 |  |  | 0 |  | 1 | CAPACITY
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -7e-05 |  |  | 0 |  | 1 | CAPACITY | X1-109
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -7e-05 |  |  | 0.04435 |  | 1 | CAPACITY | X1-109
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.04 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 64.23 |  |  | -9e-05 |  |  | 0.10478 |  | 1 | CAPACITY
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 152.86 |  |  | -0.0001 |  |  | 0.04435 |  | 1 | CAPACITY | ONTELAUNEE
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 152.86 |  |  | -0.0001 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 139.94 |  |  | -0.0001 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
203932 | AA2-133 GEN | 13.8 | 226 | 55 | 0 | 19.89 | 0 |  |  | -0.0001 |  |  | 0.08446 |  | 1 | NEW
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 900.89 |  |  | -0.00011 |  |  | 0.01494 |  | 1 | CAPACITY
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 317.93 |  |  | -0.00012 |  |  | 0 |  | 1 | CAPACITY | Hummel
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 194.29 |  |  | -0.00012 |  |  | 0 |  | 1 | CAPACITY | Hummel
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.00012 |  |  | 0 |  | 1 | CAPACITY | Hummel
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.00012 |  |  | 0.04435 |  | 1 | CAPACITY | Hummel
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 0 |  |  | -0.00014 |  |  | 0 |  | 1 | NEWENERGY | P28
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | NEW
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 47.37 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | CAPACITY
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | P28
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 17.18 |  |  | -0.00014 |  |  | 0.12623 |  | 1 | CAPACITY
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | -0.00016 |  |  | 0 |  | 1 | MTX | Z1-082
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 0 |  |  | -0.00017 |  |  | 0 |  | 1 | NEWENERGY | W3-080
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.00017 |  |  | 0.08446 |  | 1 | CAPACITY
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.00017 |  |  | 0.08446 |  | 1 | CAPACITY
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.00017 |  |  | 0.08446 |  | 1 | CAPACITY
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.00017 |  |  | 0.08446 |  | 1 | CAPACITY
209018 | SUNBIPCT | 12.5 | 229 | 55 | 0 | 36 | 28.9 |  |  | -0.00018 |  |  | 0.08446 |  | 1 | CAPACITY
925442 | AC1-016 E | 26.4 | 231 | 75 | 0 | 5.45 | 0 |  |  | -0.00017 |  |  | 0 |  | 1 | NEWENERGY | AC1-016
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | -0.00017 |  |  | 0 |  | 1 | NEWENERGY | W2-102
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | -0.00017 |  |  | 0 |  | 1 | NEWENERGY | W4-103
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -0.00017 |  |  | 0 |  | 1 | NEWENERGY | Y3-026
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00017 |  |  | 0 |  | 1 | CAPACITY | Y3-026
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 2.97 |  |  | -0.00017 |  |  | 0 |  | 1 | CAPACITY | W3-080
925441 | AC1-016 C | 26.4 | 231 | 75 | 0 | 3.34 | 2.68 |  |  | -0.00017 |  |  | 0 |  | 1 | CAPACITY | AC1-016
212345 | PENS | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00018 |  |  | 0 |  | 1 | CAPACITY
219685 | NATIONAL_GYP | 26 | 231 | 2 | 0 | 2.8 | 2.25 |  |  | -0.00017 |  |  | 0 |  | 1 | CAPACITY
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.00017 |  |  | 0 |  | 1 | CAPACITY | W2-102
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.00017 |  |  | 0 |  | 1 | CAPACITY | W4-103
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 18.3 | 14.69 |  |  | -0.0002 |  |  | 0.12623 |  | 1 | CAPACITY
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 11.24 |  |  | -0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
212435 | SMIL | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.0002 |  |  | 0 |  | 1 | CAPACITY
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 898.96 |  |  | -0.0002 |  |  | 0.01494 |  | 1 | CAPACITY
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00021 |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00021 |  |  | 0.04435 |  | 1 | CAPACITY | MOXIE PATRIOT
208948 | WILL CT | 12.5 | 229 | 55 | 0 | 27.4 | 22 |  |  | -0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
212005 | ALWD | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.0002 |  |  | 0 |  | 1 | CAPACITY
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 608.97 |  |  | -0.00022 |  |  | 0.10478 |  | 1 | CAPACITY
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 608.49 |  |  | -0.00022 |  |  | 0.10478 |  | 1 | CAPACITY
213893 | PHLISST1 | 20 | 230 | 58 | 184 | 267 | 214.36 |  |  | -0.00022 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00021 |  |  | 0.04435 |  | 1 | CAPACITY | PHILLIPS ISLAND
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00021 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00022 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 38.54 |  |  | -0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 34.28 |  |  | -0.00022 |  |  | 0.10478 |  | 1 | CAPACITY
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 26.09 |  |  | -0.00022 |  |  | 0.10478 |  | 1 | CAPACITY
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 6.42 |  |  | -0.00022 |  |  | 0 |  | 1 | CAPACITY
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 4.9 |  |  | -0.00022 |  |  | 0 |  | 1 | CAPACITY
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1090.36 |  |  | -0.00024 |  |  | 0.01494 |  | 1 | CAPACITY
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00025 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-046
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | Z2-046
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 69.05 |  |  | -0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 65.83 |  |  | -0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.00025 |  |  | 0.08446 |  | 1 | CAPACITY
208941 | FISH CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00025 |  |  | 0.08446 |  | 1 | CAPACITY
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.4 | 9.15 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | Q27
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.81 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | N14
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 260.3 | 208.98 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 205.69 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | BETH1234
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | -0.00025 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill B
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | -0.00025 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill A
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200044 | BETH CT1 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00025 |  |  | 0.04435 |  | 1 | CAPACITY | BETH1234
200048 | BETH CT5 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00025 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  |  |  | -0.0003
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.6 |  |  |  | -0.0003
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1091.76 |  |  | -0.00027 |  |  | 0.01494 |  | 1 | CAPACITY
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  |  |  | -0.0003
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  |  |  | -0.0003
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  |  |  | -0.0003
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  |  |  | -0.0003
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  |  |  | -0.0003
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 35.57 |  |  | -0.00028 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 23.44 |  |  | -0.00028 |  |  | 0.04435 |  | 1 | CAPACITY | HUNLOCK
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  |  |  | -0.0003
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  |  |  | -0.0003
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.00029 |  |  | 0.05 |  | 1 | MTX | AB1-182
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 39.1 |  |  | -0.00028 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 38.86 |  |  | -0.00028 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
208944 | JENK CT | 12.5 | 229 | 55 | 0 | 28 | 22.48 |  |  | -0.00029 |  |  | 0.08446 |  | 1 | CAPACITY
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.65 |  |  | -0.00029 |  |  | 0 |  | 1 | CAPACITY | L18
211375 | BEAC | 69 | 229 | 2 | 0 | 20 | 0 |  |  | -0.00029 |  |  | 0.10478 |  | 1 | ENERGY
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 47.77 |  |  | -0.00029 |  |  | 0.08446 |  | 1 | CAPACITY
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 47.21 |  |  | -0.00029 |  |  | 0.08446 |  | 1 | CAPACITY
213798 | MERCK 3 | 13.8 | 230 | 2 | 13 | 35 | 28.1 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 23.76 |  |  | -0.00029 |  |  | 0.08446 |  | 1 | CAPACITY
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 22.48 |  |  | -0.0003 |  |  | 0.10478 |  | 1 | CAPACITY
208943 | HARW CT | 12.5 | 229 | 55 | 0 | 27.2 | 21.84 |  |  | -0.00029 |  |  | 0.08446 |  | 1 | CAPACITY
213797 | MERCK 2 | 13.8 | 230 | 2 | 4 | 25 | 20.07 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY
211374 | AVOC | 12.5 | 229 | 2 | 0 | 17.4 | 13.97 |  |  | -0.00029 |  |  | 0 |  | 1 | CAPACITY
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 3.29 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY
211591 | HARW | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00029 |  |  | 0 |  | 1 | CAPACITY
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G2
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G3
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G1
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | -0.00031 |  |  | 0.05 |  | 1 | MTX | Z2-107
209009 | PEIP 2 | 13.8 | 229 | 56 | 0 | 43.7 | 35.08 |  |  | -0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
209010 | PEIP 1 | 13.8 | 229 | 29 | 0 | 26.7 | 21.43 |  |  | -0.00031 |  |  | 0.10478 |  | 1 | CAPACITY
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | AC1-017
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | X1-070
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 7.23 |  |  | -0.00031 |  |  | 0 |  | 1 | CAPACITY | K21
209003 | KSTN IPP | 13.8 | 229 | 65 | 0 | 4.9 | 3.93 |  |  | -0.00031 |  |  | 0 |  | 1 | CAPACITY
925451 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 1.12 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY | AC1-017
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.96 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY | X1-070
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC1-071
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 7.02 |  |  | -0.00031 |  |  | 0 |  | 1 | NEW | AC1-071
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 0 |  |  | -0.00035 |  |  | 0 |  | 1 | NEWENERGY | AA2-017
209007 | NOEN IPP | 13.8 | 229 | 12 | 80 | 111.4 | 89.44 |  |  | -0.00035 |  |  | 0.10478 |  | 1 | CAPACITY
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 0 |  |  | -0.00035 |  |  | 0 |  | 1 | NEW | AA2-017
208940 | ALLE CT | 12.5 | 229 | 55 | 0 | 56 | 44.96 |  |  | -0.00034 |  |  | 0.08446 |  | 1 | CAPACITY
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00036 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00037 |  |  | 0.10478 |  | 1 | CAPACITY
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00037 |  |  | 0.10478 |  | 1 | CAPACITY
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 238 | 191.08 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00037 |  |  | 0.04435 |  | 1 | CAPACITY | LIBERTY EDDY
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
211065 | PSPA IPP | 13.8 | 229 | 75 | 0 | 18.4 | 6.74 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | U4-014
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.00036 |  |  | 0.08446 |  | 1 | CAPACITY
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 27.3 |  |  | -0.00037 |  |  | 0.08446 |  | 1 | CAPACITY
219123 | BCRR_COGEN | 13.8 | 231 | 64 | 0 | 6 | 0 |  |  | -0.00037 |  |  | 0.12623 |  | 1 | CAPACITY
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00037 |  |  | 0.08446 |  | 1 | CAPACITY
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00037 |  |  | 0.08446 |  | 1 | CAPACITY
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | T20
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 130.87 |  |  | -0.00037 |  |  | 0.04435 |  | 1 | CAPACITY | GRAYS FERRY
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 31.31 |  |  | -0.00037 |  |  | 0.08446 |  | 1 | CAPACITY
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.00037 |  |  | 0.08446 |  | 1 | CAPACITY
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.00038 |  |  | 0.08446 |  | 1 | CAPACITY
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.00038 |  |  | 0.08446 |  | 1 | CAPACITY
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00037 |  |  | 0.08446 |  | 1 | CAPACITY
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00037 |  |  | 0.08446 |  | 1 | CAPACITY
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.00041 |  |  | 0.08446 |  | 1 | CAPACITY
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.00041 |  |  | 0.08446 |  | 1 | CAPACITY
208946 | MACR CT | 12.5 | 229 | 55 | 0 | 72 | 57.81 |  |  | -0.00041 |  |  | 0.08446 |  | 1 | CAPACITY
208920 | WLPK | 12.5 | 229 | 60 | 0 | 40.9 | 32.84 |  |  | -0.00041 |  |  | 0.07484 |  | 1 | CAPACITY
219647 | COOPERSOLA E | 13.2 | 231 | 75 | 0 | 0.4 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AB1-063
214030 | WAYNEJCT | 13.8 | 230 | 2 | 0 | 8.8 | 7.07 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 120 |  |  |  | -0.0004
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.33 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00044 |  |  | 0.10478 |  | 1 | CAPACITY
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00044 |  |  | 0.10478 |  | 1 | CAPACITY
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 192.53 |  |  | -0.00044 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 160.57 |  |  | -0.00044 |  |  | 0.04435 |  | 1 | CAPACITY | LOWER MT BETHEL
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 160.57 |  |  | -0.00044 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 152 | 122.03 |  |  | -0.00045 |  |  | 0.08446 |  | 1 | CAPACITY
206341 | 28GIL 8 | 13.8 | 228 | 58 | 69.9 | 90 | 72.26 |  |  | -0.00045 |  |  | 0.04435 |  | 1 | CAPACITY | GILBERT
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 87 | 100 | 87.11 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | GILBERT
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 85.3 | 98 | 85.37 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | GILBERT
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AC1-030
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | X1-071
925561 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | AC1-030
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.28 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | X1-071
207402 | 28AA2-082 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.00048 |  |  | 0.05 |  | 1 | MTX | AA2-082
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | W4-073
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AD2-070
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | W1-127
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | W4-097
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | U2-059
925462 | AC1-018 E | 34.5 | 228 | 75 | 0 | 0.9 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AC1-018
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | AD2-070
925461 | AC1-018 C | 34.5 | 228 | 75 | 0 | 0.5 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEW | AC1-018
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | W1-127
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | W4-097
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | U2-059
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 20 | 16.06 |  |  | -0.00049 |  |  | 0.08446 |  | 1 | CAPACITY
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 4 | 3.21 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY
204651 | 27PORT CT | 13.8 | 227 | 56 | 4 | 35 | 28.1 |  |  | -0.00052 |  |  | 0.08446 |  | 1 | CAPACITY
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 134 | 107.58 |  |  | -0.00053 |  |  | 0.08446 |  | 1 | CAPACITY
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.00052 |  |  | 0.08446 |  | 1 | CAPACITY
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.00052 |  |  | 0.08446 |  | 1 | CAPACITY
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | W3-077
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 5.7 | 4.58 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | W3-077
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | W2-091
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY | W1-121 Z
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | W1-121 Z
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.46 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
900003 | DEANS E | 500 | 231 | 74 | 0 | 1779.4 | 0 |  |  | -0.00056 |  |  | 0 |  | 1 | NEWENERGY | OSW_DEANS
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00056 |  |  | 0.0316 |  | 1 | CAPACITY
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00056 |  |  | 0.0316 |  | 1 | CAPACITY
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00056 |  |  | 0.0316 |  | 1 | CAPACITY
206747 | 28DSM_X3-029 | 34.5 | 228 | 29 | 0 | 11.15 | 0 |  |  | -0.00056 |  |  | 0.10478 |  | 1 | ENERGY
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | -0.00056 |  |  | 0.08446 |  | 1 | ENERGY
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00057 |  |  | 0 |  | 1 | NEWENERGY | Y2-018
200006 | DEANS C | 500 | 231 | 74 | 0 | 762.6 | 762.6 |  |  | -0.00056 |  |  | 0 |  | 1 | CAPACITY | OSW_DEANS
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 0 |  |  | -0.00058 |  |  | 0 |  | 1 | NEWENERGY | W3-044
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00058 |  |  | 0 |  | 1 | CAPACITY | W3-044
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.0006 |  |  | 0 |  | 1 | NEWENERGY | W4-046
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 1.93 |  |  | -0.0006 |  |  | 0 |  | 1 | CAPACITY | W4-046
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.00061 |  |  | 0 |  | 1 | NEWENERGY | W2-016
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.00061 |  |  | 0 |  | 1 | CAPACITY | W2-016
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.00062 |  |  | 0 |  | 1 | NEWENERGY | V4-001
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.61 |  |  | -0.00062 |  |  | 0 |  | 1 | CAPACITY | V4-001
219913 | PENNSAU2 E | 26.4 | 231 | 75 | 0 | 8.2 | 0 |  |  | -0.00064 |  |  | 0 |  | 1 | NEWENERGY | AD2-042
219915 | CINNAMSOL E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.00064 |  |  | 0 |  | 1 | NEWENERGY | AD2-027
219912 | PENNSAU2 C | 26.4 | 231 | 75 | 0 | 5 | 0 |  |  | -0.00064 |  |  | 0 |  | 1 | NEW | AD2-042
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.63 | 3.72 |  |  | -0.00064 |  |  | 0 |  | 1 | CAPACITY
219914 | CINNAMSOL C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00064 |  |  | 0 |  | 1 | CAPACITY | AD2-027
933322 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | -0.00063 |  |  | 0 |  | 1 | MTX | AC2-144
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.4 |  |  | -0.00064 |  |  | 0 |  | 1 | CAPACITY
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00069 |  |  | 0 |  | 1 | NEWENERGY | W4-064
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00069 |  |  | 0 |  | 1 | CAPACITY | W4-064
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.0007 |  |  | 0 |  | 1 | NEWENERGY | X1-012
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 2.97 |  |  | -0.0007 |  |  | 0 |  | 1 | CAPACITY | X1-012
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | -0.0007 |  |  | 0.05 |  | 1 | MTX | AA2-061
218780 | PRINCENTON_U | 26 | 231 | 2 | 0 | 31.56 | 25.34 |  |  | -0.0007 |  |  | 0 |  | 1 | CAPACITY
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0 |  |  | -0.00071 |  |  | 0 |  | 1 | NEWENERGY | W3-106
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | -0.0007 |  |  | 0.05 |  | 1 | MTX | AA2-060
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0 |  |  | -0.0007 |  |  | 0 |  | 1 | NEWENERGY | Z1-096
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0 |  |  | -0.00071 |  |  | 0 |  | 1 | NEWENERGY | W3-110
206742 | 28SUX_V3-011 | 34.5 | 228 | 64 | 0 | 2 | 0 |  |  | -0.0007 |  |  | 0 |  | 1 | CAPACITY
219622 | TRENT_BIOGAS | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.0007 |  |  | 0 |  | 1 | CAPACITY
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 2.39 |  |  | -0.0007 |  |  | 0 |  | 1 | CAPACITY | Z1-096
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 2.29 |  |  | -0.00071 |  |  | 0 |  | 1 | CAPACITY | W3-110
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 2.99 |  |  | -0.00072 |  |  | 0 |  | 1 | CAPACITY | Y1-020
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0 |  |  | -0.00072 |  |  | 0 |  | 1 | NEWENERGY | AC2-175
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0 |  |  | -0.00072 |  |  | 0 |  | 1 | NEWENERGY | AE1-081
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.77 |  |  | -0.00072 |  |  | 0 |  | 1 | CAPACITY | AE1-081
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | V3-024
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | V2-009 2
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | W3-124
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | V2-009 1
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | X2-088
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00074 |  |  | 0 |  | 1 | CAPACITY | V3-024
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 1.52 |  |  | -0.00074 |  |  | 0 |  | 1 | CAPACITY | V2-009 2
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.87 |  |  | -0.00074 |  |  | 0 |  | 1 | CAPACITY | W3-124
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00074 |  |  | 0 |  | 1 | CAPACITY | V2-009 1
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.72 |  |  | -0.00074 |  |  | 0 |  | 1 | CAPACITY | X2-088
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | V2-009 3
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | V2-009 4
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 1.92 |  |  | -0.00074 |  |  | 0 |  | 1 | CAPACITY | V2-009 3
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 1.15 |  |  | -0.00074 |  |  | 0 |  | 1 | CAPACITY | V2-009 4
218455 | CINNBAY_CGEN | 26.4 | 231 | 75 | 0 | 9 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | NEWENERGY
924132 | NEWROADSO E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | NEWENERGY | AB2-057
217199 | EDGEBORO_2E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | NEWENERGY | V3-059
217198 | EDGEBORO_1E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | NEWENERGY | V3-058
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0 |  |  | -0.00075 |  |  | 0 |  | 1 | NEWENERGY | X2-089
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | NEWENERGY | W2-080
924131 | NEWROADSO C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00076 |  |  | 0 |  | 1 | CAPACITY | AB2-057
218781 | BRIS_MYERS | 26 | 231 | 2 | 0 | 3 | 2.41 |  |  | -0.00076 |  |  | 0 |  | 1 | CAPACITY
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00076 |  |  | 0 |  | 1 | CAPACITY | W2-080
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.61 |  |  | -0.00075 |  |  | 0 |  | 1 | CAPACITY | X2-089
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0 |  |  | -0.00077 |  |  | 0 |  | 1 | NEWENERGY | W2-052
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.00077 |  |  | 0 |  | 1 | CAPACITY | W2-052
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 538.72 |  |  | -0.00077 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-116
219001 | SEWAREN7GT | 25 | 231 | 58 | 101.5 | 324.6 | 260.61 |  |  | -0.00078 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-089
219002 | SEWAREN7ST | 18 | 231 | 58 | 96.3 | 216.4 | 173.74 |  |  | -0.00078 |  |  | 0 |  | 1 | CAPACITY | Z2-089
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | -0.00078 |  |  | 0 |  | 1 | ENERGY | Z2-089
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | -0.00078 |  |  | 0.04435 |  | 1 | ENERGY | Z2-089
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00078 |  |  | 0 |  | 1 | NEWENERGY | W3-029
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0 |  |  | -0.00078 |  |  | 0 |  | 1 | NEWENERGY | W3-003
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0 |  |  | -0.00077 |  |  | 0 |  | 1 | NEWENERGY | W2-050
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0 |  |  | -0.00077 |  |  | 0 |  | 1 | NEWENERGY | V3-070
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0 |  |  | -0.00077 |  |  | 0 |  | 1 | NEWENERGY | AB1-139
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0 |  |  | -0.00078 |  |  | 0 |  | 1 | NEW | AE1-156
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0 |  |  | -0.00078 |  |  | 0 |  | 1 | NEWENERGY | X2-075
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0 |  |  | -0.00078 |  |  | 0 |  | 1 | NEWENERGY | AE1-156
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.00078 |  |  | 0 |  | 1 | NEWENERGY | W1-132
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00078 |  |  | 0 |  | 1 | NEWENERGY | W2-061
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00078 |  |  | 0 |  | 1 | NEWENERGY | V4-070
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00078 |  |  | 0 |  | 1 | NEWENERGY | V4-069
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0 |  |  | -0.00077 |  |  | 0 |  | 1 | NEWENERGY | AE1-041
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.00078 |  |  | 0 |  | 1 | CAPACITY | W3-029
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.00077 |  |  | 0 |  | 1 | CAPACITY | V3-070
930901 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 2.01 |  |  | -0.00077 |  |  | 0 |  | 1 | CAPACITY | AB1-139
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 1.83 |  |  | -0.00078 |  |  | 0 |  | 1 | CAPACITY | X2-075
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00078 |  |  | 0 |  | 1 | CAPACITY | V4-070
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00078 |  |  | 0 |  | 1 | CAPACITY | V4-069
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00078 |  |  | 0 |  | 1 | CAPACITY | W2-061
938281 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.00077 |  |  | 0 |  | 1 | CAPACITY | AE1-041
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  |  |  | -0.0008
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 309 | 248.08 |  |  | -0.00079 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.00079 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC2
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.00079 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.00079 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC1
218344 | TOSCO_G6 | 18 | 231 | 2 | 90 | 180 | 144.51 |  |  | -0.0008 |  |  | 0.04435 |  | 1 | CAPACITY | TOSCO
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | -0.00079 |  |  | 0.08446 |  | 1 | CAPACITY
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | -0.00079 |  |  | 0.08446 |  | 1 | CAPACITY
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 35.24 |  |  | -0.00079 |  |  | 0.10478 |  | 1 | CAPACITY
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 309 | 248.08 |  |  | -0.00081 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 180 | 144.51 |  |  | -0.00081 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -0.00081 |  |  | 0.08446 |  | 1 | CAPACITY
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -0.00081 |  |  | 0.08446 |  | 1 | CAPACITY
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 30.03 |  |  | -0.00081 |  |  | 0.10478 |  | 1 | CAPACITY
933332 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | -0.0008 |  |  | 0 |  | 1 | MTX | AC2-145
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 64.31 |  |  | -0.00081 |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 52.35 |  |  | -0.00081 |  |  | 0.04435 |  | 1 | CAPACITY | CAMDEN COGEN TECH
925391 | AC1-010 C | 26.4 | 231 | 75 | 0 | 6 | 0 |  |  | -0.00081 |  |  | 0 |  | 1 | NEW | AC1-010
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 19.27 |  |  | -0.00081 |  |  | 0.10478 |  | 1 | CAPACITY
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -0.00081 |  |  | 0 |  | 1 | NEWENERGY | AC1-010
219765 | PARADISE E | 26.4 | 231 | 75 | 0 | 3.2 | 0 |  |  | -0.00081 |  |  | 0 |  | 1 | NEWENERGY | U4-036
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.3 | 9.07 |  |  | -0.00081 |  |  | 0.10478 |  | 1 | CAPACITY
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | -0.00081 |  |  | 0 |  | 1 | MTX | X2-013
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 5.3 |  |  | -0.00081 |  |  | 0 |  | 1 | CAPACITY
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0 |  |  | -0.00082 |  |  | 0 |  | 1 | NEWENERGY | W1-101
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00081 |  |  | 0 |  | 1 | CAPACITY | U4-036
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.43 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY | W1-101
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 169.24 |  |  | -0.00083 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.00083 |  |  | 0.10478 |  | 1 | CAPACITY
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.00083 |  |  | 0.10478 |  | 1 | CAPACITY
217825 | UMD_NJ | 26 | 231 | 2 | 0 | 10.5 | 8.43 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0 |  |  | -0.00082 |  |  | 0 |  | 1 | NEWENERGY | V3-067
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0 |  |  | -0.00082 |  |  | 0 |  | 1 | NEWENERGY | V3-068
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.23 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY | V3-067
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY | V3-068
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 207.94 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 202.48 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.00083 |  |  | 0.04435 |  | 1 | CAPACITY | DELANCY STREET
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 143.63 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 143.63 |  |  | -0.00083 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN2
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 76.11 |  |  | -0.00083 |  |  | 0.08446 |  | 1 | CAPACITY
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.00083 |  |  | 0.08446 |  | 1 | CAPACITY
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.00083 |  |  | 0.08446 |  | 1 | CAPACITY
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.00083 |  |  | 0.08446 |  | 1 | CAPACITY
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.00083 |  |  | 0.08446 |  | 1 | CAPACITY
218092 | PRIMEENG_G | 26.4 | 231 | 29 | 10 | 70.3 | 56.44 |  |  | -0.00083 |  |  | 0.10478 |  | 1 | CAPACITY
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 70.56 |  |  | -0.00083 |  |  | 0.08446 |  | 1 | CAPACITY
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.00083 |  |  | 0.04435 |  | 1 | CAPACITY | NEWARK BAY
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 27.46 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | NEWENERGY | V2-025
217831 | PB_NUTCLIF | 26 | 231 | 2 | 0 | 10.7 | 8.59 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY
217850 | MONTCLAIR_U | 26 | 231 | 2 | 0 | 10.6 | 8.51 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | NEWENERGY | W4-059
934302 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | NEWENERGY | AD1-054
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.74 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0 |  |  | -0.00084 |  |  | 0 |  | 1 | NEWENERGY | AB1-021
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | NEWENERGY | X1-072
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.85 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | NEWENERGY | V3-065
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | NEWENERGY | V3-066
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | X1-072
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00084 |  |  | 0 |  | 1 | CAPACITY | AB1-021
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.18 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | W4-059
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.17 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | V3-065
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | V3-066
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0 |  |  | -0.00085 |  |  | 0 |  | 1 | NEWENERGY | X2-087
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.00085 |  |  | 0 |  | 1 | CAPACITY | X2-087
937512 | AD2-210 E | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | -0.00088 |  |  | 0 |  | 1 | MTX | AD2-210
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.0009 |  |  | 0 |  | 1 | NEWENERGY | X1-095
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.0009 |  |  | 0 |  | 1 | CAPACITY | X1-095
900004 | SMITHBRG E | 500 | 228 | 74 | 0 | 820.4 | 0 |  |  | -0.00107 |  |  | 0 |  | 1 | NEWENERGY | OSW_SMITHB
200017 | SMITHBRG C | 500 | 228 | 74 | 0 | 327.6 | 327.6 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY | OSW_SMITHB
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0 |  |  | -0.00111 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0 |  |  | -0.00111 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
932032 | AC2-009 E | 13.2 | 231 | 75 | -0.5 | 0.49 | 0 |  |  | -0.00111 |  |  | 0 |  | 1 | NEWENERGY | AC2-009
932031 | AC2-009 C | 13.2 | 231 | 75 | -0.1 | 0.1 | 0 |  |  | -0.00111 |  |  | 0 |  | 1 | NEW | AC2-009
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00111 |  |  | 0 |  | 1 | CAPACITY | AA2-058
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEWENERGY | W2-036
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00114 |  |  | 0 |  | 1 | CAPACITY | W2-036
219650 | TRENT_COLLEG | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.00123 |  |  | 0 |  | 1 | CAPACITY
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0 |  |  | -0.00123 |  |  | 0 |  | 1 | NEWENERGY | W4-058
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.22 |  |  | -0.00123 |  |  | 0 |  | 1 | CAPACITY | W4-058
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -0.00163 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -0.00164 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 33.72 |  |  | -0.00163 |  |  | 0.04435 |  | 1 | CAPACITY | EAGLE POINT
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 24.08 |  |  | -0.00163 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00172 |  |  | 0 |  | 1 | NEWENERGY | Y2-081
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.00172 |  |  | 0 |  | 1 | CAPACITY | Y2-081
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  |  |  | -0.0025
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 245.67 |  |  | -0.00248 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.00248 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.00248 |  |  | 0.04435 |  | 1 | CAPACITY | RARITAN RIVER
207441 | AD1-113 ST | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.00248 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207435 | AD1-113 CT2 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.00248 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207434 | AD1-113 CT1 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.00248 |  |  | 0.04435 |  | 1 | NEW | RARITAN RIVER
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 97.1 | 111.6 | 97.21 |  |  | -0.00248 |  |  | 0.08446 |  | 1 | CAPACITY
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 90.9 | 104.5 | 91.03 |  |  | -0.00248 |  |  | 0.08446 |  | 1 | CAPACITY
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 199.11 |  |  | -0.00265 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.00265 |  |  | 0.04435 |  | 1 | CAPACITY | RED OAK
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 60.21 |  |  | -0.00267 |  |  | 0.10478 |  | 1 | CAPACITY
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 141.3 |  |  | -0.00269 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.00269 |  |  | 0 |  | 1 | CAPACITY | RED OAK
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0 |  |  | -0.00268 |  |  | 0 |  | 1 | NEWENERGY | W2-078
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.00268 |  |  | 0 |  | 1 | NEWENERGY | W1-113
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00268 |  |  | 0 |  | 1 | CAPACITY | W2-078
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 2.25 |  |  | -0.00268 |  |  | 0 |  | 1 | CAPACITY | W1-113
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 43.63 |  |  | -0.00277 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 46.17 |  |  | -0.00277 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 66.1 | 98 | 78.68 |  |  | -0.00279 |  |  | 0.08446 |  | 1 | CAPACITY
206327 | 28S RIV G1 | 13.8 | 228 | 57 | 86.9 | 99.9 | 87.02 |  |  | -0.00279 |  |  | 0.08446 |  | 1 | CAPACITY
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 87.02 |  |  | -0.00279 |  |  | 0.08446 |  | 1 | CAPACITY
207419 | AB2-139 E | 34.5 | 228 | 76 | 0 | 0.21 | 0 |  |  | -0.00286 |  |  | 0 |  | 1 | ENERGY | AB2-139
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0 |  |  | -0.00293 |  |  | 0 |  | 1 | NEWENERGY | AC1-207
207420 | AC1-207 C | 34.5 | 228 | 75 | 0 | 4.9 | 3.93 |  |  | -0.00293 |  |  | 0 |  | 1 | CAPACITY | AC1-207
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00304 |  |  | 0 |  | 1 | NEWENERGY | X1-085
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00304 |  |  | 0 |  | 1 | CAPACITY | X1-085
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00318 |  |  | 0 |  | 1 | NEWENERGY | W4-060
901032 | W1-024E OP1 | 34.5 | 228 | 0 | 0 | 0 | 0 |  |  | -0.00318 |  |  | 0 |  | 1 | NEW
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00319 |  |  | 0 |  | 1 | NEWENERGY | W1-032
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.00318 |  |  | 0 |  | 1 | CAPACITY | W4-060
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00318 |  |  | 0 |  | 1 | CAPACITY | W1-024
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00319 |  |  | 0 |  | 1 | CAPACITY | W1-032
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.00324 |  |  | 0.05 |  | 1 | MTX
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0 |  |  | -0.00355 |  |  | 0 |  | 1 | NEWENERGY | W2-019
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 1.85 |  |  | -0.00355 |  |  | 0 |  | 1 | CAPACITY | W2-019
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.00368 |  |  | 0 |  | 1 | NEWENERGY | W4-025
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00368 |  |  | 0 |  | 1 | NEWENERGY | W1-129
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | W4-025
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | W1-129
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00374 |  |  | 0 |  | 1 | NEWENERGY | X4-015
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00374 |  |  | 0 |  | 1 | CAPACITY | X4-015
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | W1-112
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | W1-112
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00383 |  |  | 0 |  | 1 | NEWENERGY | W2-082
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00383 |  |  | 0 |  | 1 | CAPACITY | W2-082
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 271.13 |  |  | -0.00392 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | -0.00392 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | -0.00392 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
206201 | 28JERSVGEN | 34.5 | 228 | 2 | 0 | 2 | 1.61 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY
920732 | AA2-184 E | 34.5 | 228 | 75 | 0 | 20 | 0 |  |  | -0.00428 |  |  | 0 |  | 1 | NEWENERGY | AA2-184
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00433 |  |  | 0 |  | 1 | NEWENERGY | W1-124
921743 | AA2-049 E | 34.5 | 228 | 76 | -3 | 3 | 0 |  |  | -0.00433 |  |  | 0 |  | 1 | MTX | AA2-049
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.00433 |  |  | 0 |  | 1 | CAPACITY | W1-124
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0 |  |  | -0.00435 |  |  | 0 |  | 1 | NEWENERGY | X1-037
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 3.37 |  |  | -0.00435 |  |  | 0 |  | 1 | CAPACITY | X1-037
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0 |  |  | -0.00453 |  |  | 0 |  | 1 | NEWENERGY | Z2-102
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 3.97 |  |  | -0.00453 |  |  | 0 |  | 1 | CAPACITY | Z2-102
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.00455 |  |  | 0 |  | 1 | NEWENERGY | W1-119
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.00455 |  |  | 0 |  | 1 | NEWENERGY | W1-120
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.00455 |  |  | 0 |  | 1 | CAPACITY | W1-120
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.00455 |  |  | 0 |  | 1 | CAPACITY | W1-119
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.00458 |  |  | 0 |  | 1 | NEWENERGY | X4-031
919662 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 |  |  | -0.00553 |  |  | 0.05 |  | 1 | MTX | AA2-048
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.00553 |  |  | 0 |  | 1 | NEWENERGY | W3-079
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.00553 |  |  | 0 |  | 1 | CAPACITY | W3-079
900005 | 28LARRABEE E | 230 | 228 | 74 | 0 | 840 | 0 |  |  | -0.00573 |  |  | 0 |  | 1 | NEWENERGY | OSW_LARRAB
206294 | 28LARRABEE C | 230 | 228 | 74 | 0 | 360 | 360 |  |  | -0.00573 |  |  | 0 |  | 1 | CAPACITY | OSW_LARRAB
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 175.82 |  |  | -0.00579 |  |  | 0.10478 |  | 1 | CAPACITY
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00582 |  |  | 0 |  | 1 | NEWENERGY | Y2-051
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00582 |  |  | 0 |  | 1 | CAPACITY | Y2-051
923463 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.00593 |  |  | 0 |  | 1 | NEWENERGY | AB1-163
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 58.9 | 47.29 |  |  | -0.00635 |  |  | 0.04435 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 58.9 | 47.29 |  |  | -0.00635 |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 55.49 |  |  | -0.0071 |  |  | 0.08446 |  | 1 | CAPACITY
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.00743 |  |  | 0.08446 |  | 1 | CAPACITY
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.00743 |  |  | 0.08446 |  | 1 | CAPACITY
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 61.6 | 88.4 | 70.97 |  |  | -0.00743 |  |  | 0.04435 |  | 1 | CAPACITY | LAKEWOOD
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 61.2 | 88.3 | 70.89 |  |  | -0.00743 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 76.92 |  |  | -0.00743 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
228471 | VALERO1 | 13.8 | 234 | 2 | 19.1 | 22 | 19.16 |  |  | -0.00778 |  |  | 0 |  | 1 | CAPACITY
228484 | VALERO4 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | -0.00778 |  |  | 0 |  | 1 | CAPACITY
228473 | VALERO3 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | -0.00778 |  |  | 0 |  | 1 | CAPACITY
228472 | VALERO2 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | -0.00778 |  |  | 0 |  | 1 | CAPACITY
923293 | AB1-138 E | 34.5 | 228 | 75 | 0 | 6 | 0 |  |  | -0.00786 |  |  | 0 |  | 1 | NEWENERGY | AB1-138
206280 | 28LAKEHURS | 34.5 | 228 | 64 | 0 | 13.8 | 11.08 |  |  | -0.00786 |  |  | 0.08446 |  | 1 | CAPACITY
923292 | AB1-138 C | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.00786 |  |  | 0 |  | 1 | CAPACITY | AB1-138
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | -0.00794 |  |  | 0 |  | 1 | ENERGY
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 192.69 |  |  | -0.00797 |  |  | 0.10478 |  | 1 | CAPACITY
900002 | 28OYSTER E | 230 | 228 | 74 | 0 | 586.7 | 0 |  |  | -0.01532 |  |  | 0 |  | 1 | NEWENERGY | OSW_OYSCK
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 27.3 |  |  | -0.01532 |  |  | 0.12623 |  | 1 | CAPACITY
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 27 |  |  | -0.01532 |  |  | 0.12623 |  | 1 | CAPACITY
206302 | 28OYSTER C | 230 | 228 | 74 | 0 | 229.3 | 229.3 |  |  | -0.01532 |  |  | 0 |  | 1 | CAPACITY | OSW_OYSCK
228357 | V2-046E | 12.9 | 234 | 75 | 12.9 | 12.9 | 0 |  |  | -0.01936 |  |  | 0 |  | 1 | NEWENERGY | V2-046
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 6.26 |  |  | -0.01936 |  |  | 0 |  | 1 | CAPACITY | V2-046
228343 | QUINTN#1 | 12.9 | 234 | 64 | 0 | 1.7 | 0 |  |  | -0.02648 |  |  | 0 |  | 1 | CAPACITY
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.6 | 39.8 | 34.67 |  |  | -0.05235 |  |  | 0.08446 |  | 1 | CAPACITY
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 32.75 |  |  | -0.05235 |  |  | 0.08446 |  | 1 | CAPACITY
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 4.8 | 0 |  |  | -0.05251 |  |  | 0 |  | 1 | NEW
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0 |  |  | -0.05259 |  |  | 0 |  | 1 | NEWENERGY | V4-054
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 3.05 |  |  | -0.05259 |  |  | 0 |  | 1 | CAPACITY | V4-054
227928 | V4-067E | 12.9 | 234 | 75 | 1.6 | 1.6 | 0 |  |  | -0.05732 |  |  | 0 |  | 1 | NEWENERGY | V4-067
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.79 |  |  | -0.05732 |  |  | 0 |  | 1 | CAPACITY | V4-067
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0 |  |  | -0.05738 |  |  | 0 |  | 1 | NEWENERGY | AB2-122
924701 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.56 |  |  | -0.05738 |  |  | 0 |  | 1 | CAPACITY | AB2-122
228721 | V2-035E | 12.9 | 234 | 75 | 1.2 | 1.2 | 0 |  |  | -0.06155 |  |  | 0 |  | 1 | NEWENERGY | V2-035
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.61 |  |  | -0.06155 |  |  | 0 |  | 1 | CAPACITY | V2-035
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 49.65 |  |  | -0.06515 |  |  | 0.10478 |  | 1 | CAPACITY
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.5 | 18.87 |  |  | -0.06693 |  |  | 0.08446 |  | 1 | CAPACITY
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 48.35 |  |  | -0.0701 |  |  | 0.08446 |  | 1 | CAPACITY
228203 | P06 | 13.8 | 234 | 57 | 80.6 | 92.7 | 80.75 |  |  | -0.07832 |  |  | 0.08446 |  | 1 | CAPACITY
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 73.09 |  |  | -0.08321 |  |  | 0.08446 |  | 1 | CAPACITY
228712 | V2-041E | 13.2 | 234 | 75 | 2.5 | 2.48 | 0 |  |  | -0.08832 |  |  | 0 |  | 1 | NEWENERGY | V2-041
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 1.22 |  |  | -0.08832 |  |  | 0 |  | 1 | CAPACITY | V2-041
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 74.48 |  |  | -0.0895 |  |  | 0.08446 |  | 1 | CAPACITY
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0 |  |  | -0.13483 |  |  | 0 |  | 1 | NEWENERGY | W1-130
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 2.57 |  |  | -0.13483 |  |  | 0 |  | 1 | CAPACITY | W1-130
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.61 |  |  | -0.15801 |  |  | 0 |  | 1 | CAPACITY
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0 |  |  | -0.20195 |  |  | 0 |  | 1 | NEWENERGY | W2-030
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 2.93 |  |  | -0.20195 |  |  | 0 |  | 1 | CAPACITY | W2-030
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0 |  |  | -0.20582 |  |  | 0 |  | 1 | NEWENERGY | AB1-001
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.7 |  |  | -0.20582 |  |  | 0 |  | 1 | CAPACITY | AB1-001
900001 | BLE E | 138 | 234 | 74 | 0 | 310.6 | 0 |  |  | -0.22035 |  |  | 0 |  | 1 | NEWENERGY | OSW_BLE
228110 | BLE C | 138 | 234 | 74 | 0 | 121.4 | 121.4 |  |  | -0.22035 |  |  | 0 |  | 1 | CAPACITY | OSW_BLE
227801 | ONTC&DCT | 13.8 | 234 | 56 | 38.6 | 38.6 | 0 |  |  | -0.24728 |  |  | 0.08446 |  | 1 | NEW
228014 | PVILLEG | 0.48 | 234 | 65 | 1.7 | 3 | 1.04 |  |  | -0.26757 |  |  | 0 |  | 1 | CAPACITY

## FG 28-GD-S2-S3
****** PJM Generator Deliverability Detailed Report ****** POWER-GEM [TARA Ver 2001.1a PJMGD RC3 64-bit - Wed Aug 18 16:44:58 2021]
FG Index | 3 | Monitored Facility:206316 28WINDSOR 230 219752 CLRKSVLL_1 230 1 / Contingency:PJM500_PS_P2-3_DEAN5_3-4[Breaker]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
813 | 108.49 | 107.94 | AC | 232.2 | 624.68 | 4.39 | 22.22 | -1.49 | 882 | 877.5 | 0.002076 | 0 | 12712.1 | 0 | 8376.5 | 0.07154 | 4405.61 | 4335.54 | 70.07 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited?
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0 | 5.6 | FiftyFifty | 0.2264 | 1.2678 |  | 0 | 1 | 1 | NEWENERGY | W2-078
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0 | 5 | FiftyFifty | 0.2264 | 1.132 |  | 0 | 1 | 1 | NEWENERGY | W1-113
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 | 3.1 | FiftyFifty | 0.2264 | 0.1386 |  | 0 | 1 | 1 | CAPACITY | W2-078
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 2.25 | 2.8 | FiftyFifty | 0.2264 | 0.1247 |  | 0 | 1 | 1 | CAPACITY | W1-113
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0 | 1.86 | FiftyFifty | 0.21396 | 0.398 |  | 0 | 1 | 1 | NEWENERGY | W1-032
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.92 | 1.14 | FiftyFifty | 0.21396 | 0.0481 |  | 0 | 1 | 1 | CAPACITY | W1-032
207419 | AB2-139 E | 34.5 | 228 | 76 | 0 | 0.21 | 0 | 0.21 | FiftyFifty | 0.21353 | 0.0448 |  | 0 | 1 | 1 | ENERGY | AB2-139
901032 | W1-024E OP1 | 34.5 | 228 | 0 | 0 | 0 | 0 | 2.5 | FiftyFifty | 0.20333 | 0.5083 |  | 0 | 1 | 1 | NEW
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 | 1.52 | FiftyFifty | 0.20333 | 0.061 |  | 0 | 1 | 1 | CAPACITY | W1-024
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0 | 8.2 | FiftyFifty | 0.20121 | 1.6499 |  | 0 | 1 | 1 | NEWENERGY | AC1-207
207420 | AC1-207 C | 34.5 | 228 | 75 | 0 | 4.9 | 3.93 | 4.9 | FiftyFifty | 0.20121 | 0.1944 |  | 0 | 1 | 1 | CAPACITY | AC1-207
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 | 3.1 | FiftyFifty | 0.1761 | 0.5459 |  | 0 | 1 | 1 | NEWENERGY | X1-085
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 | 1.9 | FiftyFifty | 0.1761 | 0.0659 |  | 0 | 1 | 1 | CAPACITY | X1-085
206201 | 28JERSVGEN | 34.5 | 228 | 2 | 0 | 2 | 1.61 | 2 | FiftyFifty | 0.17145 | 0.0676 |  | 0 | 1 | 1 | CAPACITY
900005 | 28LARRABEE E | 230 | 228 | 74 | 0 | 840 | 0 | 840 | FiftyFifty | 0.16934 | 142.2458 |  | 0 | 1 | 1 | NEWENERGY | OSW_LARRAB
206294 | 28LARRABEE C | 230 | 228 | 74 | 0 | 360 | 360 | 360 | FiftyFifty | 0.16934 |  |  | 0 | 1 | 1 | CAPACITY | OSW_LARRAB
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0 | 10.54 | FiftyFifty | 0.16642 | 1.7541 |  | 0 | 1 | 1 | NEWENERGY | X1-037
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 3.37 | 4.2 | FiftyFifty | 0.16642 | 0.1378 |  | 0 | 1 | 1 | CAPACITY | X1-037
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 | 3.1 | FiftyFifty | 0.16481 | 0.5109 |  | 0 | 1 | 1 | NEWENERGY | Y2-051
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 | 1.9 | FiftyFifty | 0.16481 | 0.0616 |  | 0 | 1 | 1 | CAPACITY | Y2-051
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 | 168.1 | FiftyFifty | 0.1634 | 5.4148 |  | 0.08446 | 0.9155 | 1 | CAPACITY
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 | 168.1 | FiftyFifty | 0.1634 | 5.4148 |  | 0.08446 | 0.8382 | 1 | CAPACITY
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 61.6 | 88.4 | 70.97 | 88.4 | FiftyFifty | 0.1634 | 2.8475 |  | 0.04435 | 0.801 | 1 | CAPACITY | LAKEWOOD
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 61.2 | 88.3 | 70.89 | 88.3 | FiftyFifty | 0.1634 | 2.8443 |  | 0 | 0.801 | 1 | CAPACITY | LAKEWOOD
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 76.92 | 88.3 | FiftyFifty | 0.1634 | 1.8596 |  | 0 | 0.801 | 1 | CAPACITY | LAKEWOOD
919662 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 | 7 | FiftyFifty/NFTIR | 0.16245 | 1.1371 |  | 0.05 | 0.761 | 1 | MTX NFTIR | AA2-048
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 | 4.4 | FiftyFifty | 0.16245 | 0.7148 |  | 0 | 0.761 | 1 | NEWENERGY | W3-079
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 | 2.6 | FiftyFifty | 0.16245 | 0.0832 |  | 0 | 0.801 | 1 | CAPACITY | W3-079
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0 | 2 | FiftyFifty | 0.15559 | 0.3112 |  | 0 | 0.761 | 1 | NEWENERGY | X4-031
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -20 | 20 | 0 | 20 | FiftyFifty/NFTIR | 0.15324 | 3.0648 |  | 0.05 | 0.7229 | 1 | MTX NFTIR
923293 | AB1-138 E | 34.5 | 228 | 75 | 0 | 6 | 0 | 6 | FiftyFifty | 0.15265 | 0.9159 |  | 0 | 0.6619 | 1 | NEWENERGY | AB1-138
206280 | 28LAKEHURS | 34.5 | 228 | 64 | 0 | 13.8 | 11.08 | 13.8 | FiftyFifty | 0.15265 | 0.4152 |  | 0.08446 | 0.6619 | 1 | CAPACITY
923292 | AB1-138 C | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 | 3.6 | FiftyFifty | 0.15265 | 0.1084 |  | 0 | 0.6619 | 1 | CAPACITY | AB1-138
923463 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0 | 5 | FiftyFifty | 0.14802 | 0.7401 |  | 0 | 0.6619 | 1 | NEWENERGY | AB1-163
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0 | 10.5 | FiftyFifty | 0.14738 | 1.5475 |  | 0 | 0.6619 | 1 | NEWENERGY | W1-124
921743 | AA2-049 E | 34.5 | 228 | 76 | -3 | 3 | 0 | 3 | FiftyFifty/NFTIR | 0.14738 | 0.4421 |  | 0 | 0.6619 | 1 | MTX NFTIR | AA2-049
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 | 6.4 | FiftyFifty | 0.14738 | 0.186 |  | 0 | 0.6619 | 1 | CAPACITY | W1-124
900004 | SMITHBRG E | 500 | 228 | 74 | 0 | 820.4 | 0 | 820.4 | FiftyFifty | 0.1465 | 120.1864 |  | 0 | 0.6619 | 1 | NEWENERGY | OSW_SMITHB
200017 | SMITHBRG C | 500 | 228 | 74 | 0 | 327.6 | 327.6 | 327.6 | FiftyFifty | 0.1465 |  |  | 0 | 0.6619 | 1 | CAPACITY | OSW_SMITHB
920732 | AA2-184 E | 34.5 | 228 | 75 | 0 | 20 | 0 | 20 | FiftyFifty | 0.14642 | 2.9285 |  | 0 | 0.6619 | 1 | NEWENERGY | AA2-184
900002 | 28OYSTER E | 230 | 228 | 74 | 0 | 586.7 | 0 | 586.7 | FiftyFifty | 0.14162 | 83.0873 |  | 0 | 0.5053 | 1 | NEWENERGY | OSW_OYSCK
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 27.3 | 34 | FiftyFifty | 0.14162 | 0.9493 |  | 0.12623 | 0.5783 | 1 | CAPACITY
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 27 | 31 | FiftyFifty | 0.14162 | 0.5659 |  | 0.12623 | 0.5053 | 1 | CAPACITY
206302 | 28OYSTER C | 230 | 228 | 74 | 0 | 229.3 | 229.3 | 229.3 | FiftyFifty | 0.14162 |  |  | 0 | 0.5053 | 1 | CAPACITY | OSW_OYSCK
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0 | 2.48 | FiftyFifty | 0.13126 | 0.3255 |  | 0 | 0.5053 | 1 | NEWENERGY | W1-112
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 | 1.52 | FiftyFifty | 0.13126 | 0.0394 |  | 0 | 0.5053 | 1 | CAPACITY | W1-112
900003 | DEANS E | 500 | 231 | 74 | 0 | 1779.4 | 0 | 1779.4 | FiftyFifty | 0.1297 | 230.797 |  | 0 | 0.5053 | 1 | NEWENERGY | OSW_DEANS
200006 | DEANS C | 500 | 231 | 74 | 0 | 762.6 | 762.6 | 762.6 | FiftyFifty | 0.1297 |  |  | 0 | 0.5053 | 1 | CAPACITY | OSW_DEANS
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0 | 5.46 | FiftyFifty | 0.1264 | 0.6902 |  | 0 | 0.5053 | 1 | NEWENERGY | W1-120
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0 | 5.46 | FiftyFifty | 0.1264 | 0.6902 |  | 0 | 0.5053 | 1 | NEWENERGY | W1-119
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 | 3.34 | FiftyFifty | 0.1264 | 0.0833 |  | 0 | 0.5053 | 1 | CAPACITY | W1-120
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 | 3.34 | FiftyFifty | 0.1264 | 0.0833 |  | 0 | 0.5053 | 1 | CAPACITY | W1-119
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0 | 8.06 | FiftyFifty | 0.12631 | 1.018 |  | 0 | 0.5053 | 1 | NEWENERGY | Z2-102
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 3.97 | 4.94 | FiftyFifty | 0.12631 | 0.123 |  | 0 | 0.5053 | 1 | CAPACITY | Z2-102
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0 | 10.5 | FiftyFifty | 0.12282 | 1.2896 |  | 0 | 0.5053 | 1 | NEWENERGY | W2-082
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 | 3.1 | FiftyFifty | 0.12282 | 0.0752 |  | 0 | 0.5053 | 1 | CAPACITY | W2-082
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 | 3.1 | FiftyFifty | 0.12238 | 0.3794 |  | 0 | 0.5053 | 1 | NEWENERGY | X4-015
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 | 1.9 | FiftyFifty | 0.12238 | 0.0458 |  | 0 | 0.5053 | 1 | CAPACITY | X4-015
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 | 4.4 | FiftyFifty | 0.12207 | 0.5371 |  | 0 | 0.5053 | 1 | NEWENERGY | W4-025
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0 | 3.1 | FiftyFifty | 0.12207 | 0.3784 |  | 0 | 0.5053 | 1 | NEWENERGY | W1-129
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 | 2.6 | FiftyFifty | 0.12207 | 0.0625 |  | 0 | 0.5053 | 1 | CAPACITY | W4-025
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 | 1.9 | FiftyFifty | 0.12207 | 0.0457 |  | 0 | 0.5053 | 1 | CAPACITY | W1-129
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0 | 3.7 | FiftyFifty | 0.12145 | 0.4494 |  | 0 | 0.5053 | 1 | NEWENERGY | W2-019
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 1.85 | 2.3 | FiftyFifty | 0.12145 | 0.0551 |  | 0 | 0.5053 | 1 | CAPACITY | W2-019
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0 | 6.2 | FiftyFifty | 0.11618 | 0.7203 |  | 0 | 0.5053 | 1 | NEWENERGY | W4-060
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 | 3.2 | FiftyFifty | 0.11618 | 0.0734 |  | 0 | 0.5053 | 1 | CAPACITY | W4-060
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0 | 1.22 | Adder/OL | 0.07353 | 0.0894 | 0.0025 | 0 |  | 1 | NEWENERGY | AB1-001
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  | 239.8 | LTF/CMTX | 0.07328 | 17.5691 | 0.4978
207435 | AD1-113 CT2 | 18 | 228 | 58 | 0 | 25 | 0 | 21.25 | Adder/OL | 0.07328 | 1.5572 | 0.0441 | 0 |  | 1 | NEW | RARITAN RIVER
207441 | AD1-113 ST | 18 | 228 | 58 | 0 | 25 | 0 | 21.25 | Adder/OL | 0.07328 | 1.5572 | 0.0441 | 0 |  | 1 | NEW | RARITAN RIVER
207434 | AD1-113 CT1 | 18 | 228 | 58 | 0 | 25 | 0 | 21.25 | Adder/OL | 0.07328 | 1.5572 | 0.0441 | 0.04435 |  | 1 | NEW | RARITAN RIVER
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  | 55.3 | CLTF | 0.00738 | 0.4081 | -0.1148
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.6 |  | 173.6 | CLTF | 0.00397 | 0.6899 | -0.3604
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 0.00398 | 0.2213 | -0.1155
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 0.00398 | 0.217 | -0.1134
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  | 258.3 | CLTF | 0.00394 | 1.0188 | -0.5363
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  | 210 | CLTF | 0.00388 | 0.8148 | -0.436
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 0.00383 | 0.1904 | -0.1032
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 0.00383 | 0.1916 | -0.1039
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  | 35 | CLTF | 0.00371 | 0.1299 | -0.0727
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  | 57.8 | CLTF | 0.00365 | 0.2109 | -0.1199
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  | 645 | LTF/CMTX | 0.00043 | 0.2748 | 1.3391
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  | 673 | LTF/CMTX NF | 0.00042 | 0.2813 | -1.3973
219123 | BCRR_COGEN | 13.8 | 231 | 64 | 0 | 6 | 0 | 5.1 | Adder/OL | -0.07259 | -0.3702 | 0.0106 | 0.12623 |  | 1 | CAPACITY
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 66.1 | 98 | 78.68 |  |  | 0.08592 |  |  | 0.08446 |  | 1 | CAPACITY
206327 | 28S RIV G1 | 13.8 | 228 | 57 | 86.9 | 99.9 | 87.02 |  |  | 0.08592 |  |  | 0.08446 |  | 1 | CAPACITY
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 87.02 |  |  | 0.08592 |  |  | 0.08446 |  | 1 | CAPACITY
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 43.63 |  |  | 0.08537 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 46.17 |  |  | 0.08537 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 141.3 |  |  | 0.08191 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | 0.08191 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 199.11 |  |  | 0.08024 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | 0.08024 |  |  | 0.04435 |  | 1 | CAPACITY | RED OAK
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.7 |  |  | 0.07353 |  |  | 0 |  | 1 | CAPACITY | AB1-001
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 245.67 |  |  | 0.07328 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | 0.07328 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | 0.07328 |  |  | 0.04435 |  | 1 | CAPACITY | RARITAN RIVER
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 97.1 | 111.6 | 97.21 |  |  | 0.07328 |  |  | 0.08446 |  | 1 | CAPACITY
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 90.9 | 104.5 | 91.03 |  |  | 0.07328 |  |  | 0.08446 |  | 1 | CAPACITY
900000 | CARDIFF E | 230 | 234 | 74 | 0 | 1235 | 0 |  |  | 0.06273 |  |  | 0 |  | 1 | NEWENERGY | OSW_CARDIF
227900 | CARDIFF C | 230 | 234 | 74 | 0 | 275 | 275 |  |  | 0.06273 |  |  | 0 |  | 1 | CAPACITY | OSW_CARDIF
227928 | V4-067E | 12.9 | 234 | 75 | 1.6 | 1.6 | 0 |  |  | 0.06008 |  |  | 0 |  | 1 | NEWENERGY | V4-067
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.79 |  |  | 0.06008 |  |  | 0 |  | 1 | CAPACITY | V4-067
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0 |  |  | 0.06008 |  |  | 0 |  | 1 | NEWENERGY | AB2-122
924701 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.56 |  |  | 0.06008 |  |  | 0 |  | 1 | CAPACITY | AB2-122
228014 | PVILLEG | 0.48 | 234 | 65 | 1.7 | 3 | 1.04 |  |  | 0.05893 |  |  | 0 |  | 1 | CAPACITY
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 |  |  | 0.05874 |  |  | 0.12623 |  | 1 | ENERGY
227801 | ONTC&DCT | 13.8 | 234 | 56 | 38.6 | 38.6 | 0 |  |  | 0.05873 |  |  | 0.08446 |  | 1 | NEW
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 |  |  | 0.05873 |  |  | 0.10478 |  | 1 | ENERGY
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0 |  |  | 0.05825 |  |  | 0 |  | 1 | NEWENERGY | W2-030
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 2.93 |  |  | 0.05825 |  |  | 0 |  | 1 | CAPACITY | W2-030
900001 | BLE E | 138 | 234 | 74 | 0 | 310.6 | 0 |  |  | 0.05354 |  |  | 0 |  | 1 | NEWENERGY | OSW_BLE
228110 | BLE C | 138 | 234 | 74 | 0 | 121.4 | 121.4 |  |  | 0.05354 |  |  | 0 |  | 1 | CAPACITY | OSW_BLE
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.61 |  |  | 0.05033 |  |  | 0 |  | 1 | CAPACITY
228203 | P06 | 13.8 | 234 | 57 | 80.6 | 92.7 | 80.75 |  |  | 0.04568 |  |  | 0.08446 |  | 1 | CAPACITY
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 74.48 |  |  | 0.04524 |  |  | 0.08446 |  | 1 | CAPACITY
228712 | V2-041E | 13.2 | 234 | 75 | 2.5 | 2.48 | 0 |  |  | 0.0444 |  |  | 0 |  | 1 | NEWENERGY | V2-041
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 1.22 |  |  | 0.0444 |  |  | 0 |  | 1 | CAPACITY | V2-041
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 73.09 |  |  | 0.04343 |  |  | 0.08446 |  | 1 | CAPACITY
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 998.11 |  |  | 0.04241 |  |  | 0.01494 |  | 1 | CAPACITY
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 992.1 |  |  | 0.04241 |  |  | 0.01494 |  | 1 | CAPACITY
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | 0.04241 |  |  | 0.08446 |  | 1 | ENERGY
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1026.43 |  |  | 0.04217 |  |  | 0.01494 |  | 1 | CAPACITY
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 48.35 |  |  | 0.04039 |  |  | 0.08446 |  | 1 | CAPACITY
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.5 | 18.87 |  |  | 0.03976 |  |  | 0.08446 |  | 1 | CAPACITY
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 49.65 |  |  | 0.03939 |  |  | 0.10478 |  | 1 | CAPACITY
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0 |  |  | 0.03896 |  |  | 0 |  | 1 | NEWENERGY | W1-130
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 2.57 |  |  | 0.03896 |  |  | 0 |  | 1 | CAPACITY | W1-130
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0 |  |  | 0.0358 |  |  | 0 |  | 1 | NEWENERGY | V4-054
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 3.05 |  |  | 0.0358 |  |  | 0 |  | 1 | CAPACITY | V4-054
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 4.8 | 0 |  |  | 0.03577 |  |  | 0 |  | 1 | NEW
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.6 | 39.8 | 34.67 |  |  | 0.03573 |  |  | 0.08446 |  | 1 | CAPACITY
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 32.75 |  |  | 0.03573 |  |  | 0.08446 |  | 1 | CAPACITY
228721 | V2-035E | 12.9 | 234 | 75 | 1.2 | 1.2 | 0 |  |  | 0.03228 |  |  | 0 |  | 1 | NEWENERGY | V2-035
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.61 |  |  | 0.03228 |  |  | 0 |  | 1 | CAPACITY | V2-035
228343 | QUINTN#1 | 12.9 | 234 | 64 | 0 | 1.7 | 0 |  |  | 0.02967 |  |  | 0 |  | 1 | CAPACITY
228357 | V2-046E | 12.9 | 234 | 75 | 12.9 | 12.9 | 0 |  |  | 0.02688 |  |  | 0 |  | 1 | NEWENERGY | V2-046
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 6.26 |  |  | 0.02688 |  |  | 0 |  | 1 | CAPACITY | V2-046
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | 0.02674 |  |  | 0.04435 |  | 1 | NEW | AA2-069
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 154.95 |  |  | 0.02674 |  |  | 0.04435 |  | 1 | CAPACITY | Garrison
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 93.29 |  |  | 0.02674 |  |  | 0 |  | 1 | CAPACITY | Garrison
232901 | NORTHST | 69 | 235 | 56 | 5 | 46 | 36.93 |  |  | 0.02674 |  |  | 0.08446 |  | 1 | CAPACITY
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 12.2 |  |  | 0.02674 |  |  | 0.10478 |  | 1 | CAPACITY
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 39.34 |  |  | 0.02629 |  |  | 0.08446 |  | 1 | CAPACITY
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 38.54 |  |  | 0.02629 |  |  | 0.08446 |  | 1 | CAPACITY
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 192.69 |  |  | 0.02626 |  |  | 0.10478 |  | 1 | CAPACITY
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0 |  |  | 0.02616 |  |  | 0 |  | 1 | NEWENERGY | W2-056
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 3.36 |  |  | 0.02616 |  |  | 0 |  | 1 | CAPACITY | W2-056
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0 |  |  | 0.0261 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 N
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 0.0261 |  |  | 0 |  | 1 | CAPACITY | AB1-025 N
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 152.54 |  |  | 0.02534 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.02534 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.02534 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.02534 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC2
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 0 |  |  | 0.02489 |  |  | 0 |  | 1 | NEWENERGY | AB1-056
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 330.7 |  |  | 0.02489 |  |  | 0.10478 |  | 1 | CAPACITY
930201 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 51.71 |  |  | 0.02489 |  |  | 0 |  | 1 | CAPACITY | AB1-056
232920 | IR10 | 13.2 | 235 | 55 | 12.6 | 16.1 | 12.93 |  |  | 0.02484 |  |  | 0.08446 |  | 1 | CAPACITY
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0 |  |  | 0.02483 |  |  | 0 |  | 1 | NEWENERGY | AB1-137
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 3.37 |  |  | 0.02483 |  |  | 0 |  | 1 | CAPACITY | AB1-137
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | 0.02476 |  |  | 0.10478 |  | 1 | ENERGY
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.02476 |  |  | 0 |  | 1 | NEWENERGY | Z2-077
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.02476 |  |  | 0 |  | 1 | NEWENERGY | Z2-076
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.02476 |  |  | 0 |  | 1 | CAPACITY | Z2-077
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.02476 |  |  | 0 |  | 1 | CAPACITY | Z2-076
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.41 |  |  | 0.02471 |  |  | 0 |  | 1 | CAPACITY
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.05 |  |  | 0.02461 |  |  | 0 |  | 1 | CAPACITY
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.02455 |  |  | 0.08446 |  | 1 | CAPACITY
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.02455 |  |  | 0.08446 |  | 1 | CAPACITY
917082 | CHERRYDALE E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.02441 |  |  | 0 |  | 1 | NEWENERGY | Z2-012
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0244 |  |  | 0 |  | 1 | NEWENERGY | W1-006
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0244 |  |  | 0 |  | 1 | NEWENERGY | W1-005
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0244 |  |  | 0 |  | 1 | NEWENERGY | W1-004
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.0244 |  |  | 0 |  | 1 | NEWENERGY | W1-003
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.0244 |  |  | 0.08446 |  | 1 | CAPACITY
232915 | OH NUG4 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.0244 |  |  | 0.08446 |  | 1 | CAPACITY
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.0244 |  |  | 0.08446 |  | 1 | CAPACITY
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.0244 |  |  | 0.08446 |  | 1 | CAPACITY
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 39.03 |  |  | 0.0244 |  |  | 0.08446 |  | 1 | CAPACITY
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 38.94 |  |  | 0.0244 |  |  | 0.08446 |  | 1 | CAPACITY
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 38.68 |  |  | 0.0244 |  |  | 0.08446 |  | 1 | CAPACITY
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 26.05 |  |  | 0.02441 |  |  | 0.08446 |  | 1 | CAPACITY
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.0244 |  |  | 0 |  | 1 | CAPACITY | W1-003
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.0244 |  |  | 0 |  | 1 | CAPACITY | W1-006
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.0244 |  |  | 0 |  | 1 | CAPACITY | W1-005
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.0244 |  |  | 0 |  | 1 | CAPACITY | W1-004
232905 | BAYVIEW1 | 24.9 | 235 | 65 | 0 | 12.5 | 10.04 |  |  | 0.02441 |  |  | 0.12623 |  | 1 | CAPACITY
917081 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.02441 |  |  | 0 |  | 1 | CAPACITY | Z2-012
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0 |  |  | 0.02433 |  |  | 0 |  | 1 | NEWENERGY | X1-032
293670 | O-025 C | 25 | 235 | 64 | 0 | 6 | 4.82 |  |  | 0.02433 |  |  | 0 |  | 1 | CAPACITY
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 0 |  |  | 0.02431 |  |  | 0 |  | 1 | NEWENERGY | AA1-102
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 45.76 |  |  | 0.02431 |  |  | 0 |  | 1 | CAPACITY | AA1-102
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 8.03 |  |  | 0.02431 |  |  | 0 |  | 1 | CAPACITY
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0 |  |  | 0.02422 |  |  | 0 |  | 1 | NEWENERGY | Y3-058
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 5.7 | 4.58 |  |  | 0.02422 |  |  | 0 |  | 1 | CAPACITY | Y3-058
232919 | VN10 | 13.2 | 235 | 55 | 12.4 | 14.3 | 12.46 |  |  | 0.02388 |  |  | 0 |  | 1 | CAPACITY
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 122.84 |  |  | 0.02379 |  |  | 0.10478 |  | 1 | CAPACITY
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0 |  |  | 0.02378 |  |  | 0 |  | 1 | NEWENERGY | Y1-080
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 1.03 |  |  | 0.02378 |  |  | 0 |  | 1 | CAPACITY | Y1-080
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.02348 |  |  | 0 |  | 1 | NEWENERGY | X3-008
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.02348 |  |  | 0 |  | 1 | CAPACITY | X3-008
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 55.4 |  |  | 0.02249 |  |  | 0.12623 |  | 1 | CAPACITY
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0 |  |  | 0.02188 |  |  | 0 |  | 1 | NEWENERGY | Y1-079
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.02188 |  |  | 0 |  | 1 | CAPACITY | Y1-079
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0 |  |  | 0.02149 |  |  | 0 |  | 1 | NEWENERGY | X3-066
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 2.28 | 1.83 |  |  | 0.02149 |  |  | 0 |  | 1 | CAPACITY | X3-066
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 57.24 |  |  | 0.0213 |  |  | 0.10478 |  | 1 | CAPACITY
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 45.76 |  |  | 0.0213 |  |  | 0.08446 |  | 1 | CAPACITY
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 44.16 |  |  | 0.0213 |  |  | 0.04435 |  | 1 | CAPACITY | DELAWARE CITY
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 14.29 |  |  | 0.0213 |  |  | 0.08446 |  | 1 | CAPACITY
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.02107 |  |  | 0 |  | 1 | NEWENERGY | AB1-142
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.02107 |  |  | 0 |  | 1 | NEWENERGY | AB1-141
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.02107 |  |  | 0 |  | 1 | CAPACITY | AB1-142
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.02107 |  |  | 0 |  | 1 | CAPACITY | AB1-141
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 19.11 |  |  | 0.02103 |  |  | 0.12623 |  | 1 | CAPACITY
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0 |  |  | 0.01927 |  |  | 0 |  | 1 | NEWENERGY | Y1-075
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 0.01927 |  |  | 0 |  | 1 | CAPACITY | Y1-075
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 58.9 | 47.29 |  |  | 0.0189 |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 58.9 | 47.29 |  |  | 0.0189 |  |  | 0.04435 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0 |  |  | 0.0187 |  |  | 0 |  | 1 | NEWENERGY | V4-005
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.88 |  |  | 0.0187 |  |  | 0 |  | 1 | CAPACITY | V4-005
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01861 |  |  | 0 |  | 1 | NEWENERGY | AB2-179
233931 | AB2-179 C | 0.38 | 235 | 75 | 0 | 38 | 30.51 |  |  | 0.01861 |  |  | 0 |  | 1 | CAPACITY | AB2-179
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 175.82 |  |  | 0.01638 |  |  | 0.10478 |  | 1 | CAPACITY
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.09 |  |  | 0.01578 |  |  | 0 |  | 1 | CAPACITY
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0 |  |  | 0.01555 |  |  | 0 |  | 1 | NEWENERGY | W2-071
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.85 |  |  | 0.01555 |  |  | 0 |  | 1 | CAPACITY | W2-071
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | 0.01516 |  |  | 0 |  | 1 | ENERGY
228471 | VALERO1 | 13.8 | 234 | 2 | 19.1 | 22 | 19.16 |  |  | 0.01492 |  |  | 0 |  | 1 | CAPACITY
228473 | VALERO3 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.01492 |  |  | 0 |  | 1 | CAPACITY
228484 | VALERO4 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.01492 |  |  | 0 |  | 1 | CAPACITY
228472 | VALERO2 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.01492 |  |  | 0 |  | 1 | CAPACITY
925112 | AB2-168 E | 34.5 | 235 | 75 | 0 | 5.2 | 0 |  |  | 0.01473 |  |  | 0 |  | 1 | NEWENERGY | AB2-168
925111 | AB2-168 C | 34.5 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.01473 |  |  | 0 |  | 1 | CAPACITY | AB2-168
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 55.49 |  |  | 0.01394 |  |  | 0.08446 |  | 1 | CAPACITY
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 13.81 |  |  | 0.01321 |  |  | 0.08446 |  | 1 | CAPACITY
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 18.47 |  |  | 0.01304 |  |  | 0.08446 |  | 1 | CAPACITY
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 18.39 |  |  | 0.01304 |  |  | 0.08446 |  | 1 | CAPACITY
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 139.7 |  |  | 0.01152 |  |  | 0.10478 |  | 1 | CAPACITY
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01152 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01152 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01141 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 69.05 |  |  | 0.01141 |  |  | 0.10478 |  | 1 | CAPACITY
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 11.4 |  |  | 0.01141 |  |  | 0.08446 |  | 1 | CAPACITY
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0 |  |  | 0.00831 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 S
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 0.00831 |  |  | 0 |  | 1 | CAPACITY | AB1-025 S
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 271.13 |  |  | 0.00786 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.00786 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.00786 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 369.31 |  |  | 0.00629 |  |  | 0.04435 |  | 1 | CAPACITY | Y1-065
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00629 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00629 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200054 | ROCKSP 3 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00629 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 3
200055 | ROCKSP 4 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00629 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 4
200052 | ROCKSP 1 | 18 | 225 | 57 | 145.7 | 167.5 | 145.91 |  |  | 0.00629 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 1
200053 | ROCKSP 2 | 18 | 225 | 57 | 144.9 | 166.5 | 145.04 |  |  | 0.00629 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 2
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 361.29 |  |  | 0.00502 |  |  | 0.10478 |  | 1 | CAPACITY
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 148.77 |  |  | 0.00502 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC1
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 60.21 |  |  | 0.00421 |  |  | 0.10478 |  | 1 | CAPACITY
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0 |  |  | 0.00158 |  |  | 0 |  | 1 | NEWENERGY | Y3-087
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 1.84 |  |  | 0.00158 |  |  | 0 |  | 1 | CAPACITY | Y3-087
937512 | AD2-210 E | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | 0.00134 |  |  | 0 |  | 1 | MTX | AD2-210
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 5.3 |  |  | 0.00133 |  |  | 0 |  | 1 | CAPACITY
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1034.24 |  |  | 0.00108 |  |  | 0.01494 |  | 1 | CAPACITY
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 306.69 |  |  | 0.00106 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00106 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00106 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA2
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 154.95 |  |  | 0.00106 |  |  | 0 |  | 1 | CAPACITY | DELTA
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00106 |  |  | 0 |  | 1 | CAPACITY | DELTA
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00106 |  |  | 0 |  | 1 | CAPACITY | DELTA
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00106 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1049.33 |  |  | 0.0008 |  |  | 0.01494 |  | 1 | CAPACITY
217825 | UMD_NJ | 26 | 231 | 2 | 0 | 10.5 | 8.43 |  |  | 0.00068 |  |  | 0 |  | 1 | CAPACITY
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0 |  |  | 0.00063 |  |  | 0 |  | 1 | NEWENERGY | X2-089
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.61 |  |  | 0.00063 |  |  | 0 |  | 1 | CAPACITY | X2-089
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0 |  |  | 0.00045 |  |  | 0 |  | 1 | NEWENERGY | X2-087
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 0.00045 |  |  | 0 |  | 1 | CAPACITY | X2-087
218344 | TOSCO_G6 | 18 | 231 | 2 | 90 | 180 | 144.51 |  |  | 0.00034 |  |  | 0.04435 |  | 1 | CAPACITY | TOSCO
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 309 | 248.08 |  |  | 0.00013 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | 0.00013 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | 0.00013 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | 0.00013 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC2
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | 0.00013 |  |  | 0.08446 |  | 1 | CAPACITY
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | 0.00013 |  |  | 0.08446 |  | 1 | CAPACITY
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 309 | 248.08 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 180 | 144.51 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 30.03 |  |  | -3e-05 |  |  | 0.10478 |  | 1 | CAPACITY
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0 |  |  | -0.00015 |  |  | 0 |  | 1 | NEWENERGY | W1-101
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.43 |  |  | -0.00015 |  |  | 0 |  | 1 | CAPACITY | W1-101
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0 |  |  | -0.00018 |  |  | 0 |  | 1 | NEWENERGY | V3-067
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0 |  |  | -0.00018 |  |  | 0 |  | 1 | NEWENERGY | V3-068
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.23 |  |  | -0.00018 |  |  | 0 |  | 1 | CAPACITY | V3-067
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.00018 |  |  | 0 |  | 1 | CAPACITY | V3-068
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.0002 |  |  | 0.10478 |  | 1 | CAPACITY
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.0002 |  |  | 0.10478 |  | 1 | CAPACITY
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00033 |  |  | 0 |  | 1 | NEWENERGY | X1-095
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | X1-095
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 169.24 |  |  | -0.00034 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN1
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00033 |  |  | 0.04435 |  | 1 | CAPACITY | PHILLIPS ISLAND
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.00034 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.00034 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.00034 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.00034 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
213893 | PHLISST1 | 20 | 230 | 58 | 184 | 267 | 214.36 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | W4-059
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.18 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | W4-059
934302 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AD1-054
218092 | PRIMEENG_G | 26.4 | 231 | 29 | 10 | 70.3 | 56.44 |  |  | -0.00041 |  |  | 0.10478 |  | 1 | CAPACITY
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 207.94 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 202.48 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.00042 |  |  | 0.04435 |  | 1 | CAPACITY | DELANCY STREET
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 143.63 |  |  | -0.00042 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN2
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 143.63 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 70.56 |  |  | -0.00042 |  |  | 0.08446 |  | 1 | CAPACITY
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.00042 |  |  | 0.04435 |  | 1 | CAPACITY | NEWARK BAY
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 27.46 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217831 | PB_NUTCLIF | 26 | 231 | 2 | 0 | 10.7 | 8.59 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY
217850 | MONTCLAIR_U | 26 | 231 | 2 | 0 | 10.6 | 8.51 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.74 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | X1-072
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.85 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | V3-065
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | X1-072
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.17 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | V3-065
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 76.11 |  |  | -0.00042 |  |  | 0.08446 |  | 1 | CAPACITY
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.00042 |  |  | 0.08446 |  | 1 | CAPACITY
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.00042 |  |  | 0.08446 |  | 1 | CAPACITY
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.00042 |  |  | 0.08446 |  | 1 | CAPACITY
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.00042 |  |  | 0.08446 |  | 1 | CAPACITY
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0 |  |  | -0.00044 |  |  | 0 |  | 1 | NEWENERGY | V3-066
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.00044 |  |  | 0 |  | 1 | CAPACITY | V3-066
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00045 |  |  | 0 |  | 1 | NEWENERGY | V2-025
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00061 |  |  | 0 |  | 1 | NEWENERGY | Y2-081
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.00061 |  |  | 0 |  | 1 | CAPACITY | Y2-081
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0 |  |  | -0.00066 |  |  | 0 |  | 1 | NEWENERGY | X3-075
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0 |  |  | -0.00069 |  |  | 0 |  | 1 | NEWENERGY | AB1-021
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00069 |  |  | 0 |  | 1 | CAPACITY | AB1-021
933332 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | MTX | AC2-145
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -0.00091 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 33.72 |  |  | -0.00093 |  |  | 0.04435 |  | 1 | CAPACITY | EAGLE POINT
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 24.08 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | -0.0014 |  |  | 0.0316 |  | 1 | CAPACITY
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | -0.0014 |  |  | 0.0316 |  | 1 | CAPACITY
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | -0.00142 |  |  | 0.0316 |  | 1 | CAPACITY
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | -0.00142 |  |  | 0.0316 |  | 1 | CAPACITY
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 256.27 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 134.08 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | -0.00209 |  |  | 0.04435 |  | 1 | CAPACITY | HUNTERSTOWN
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | -0.00228 |  |  | 0 |  | 1 | MTX | Z1-082
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | -0.00246 |  |  | 0 |  | 1 | ENERGY
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 45.76 |  |  | -0.00254 |  |  | 0.10478 |  | 1 | CAPACITY
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.5 | 24.49 |  |  | -0.00255 |  |  | 0.08446 |  | 1 | CAPACITY
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 30 | 24.08 |  |  | -0.00255 |  |  | 0.08446 |  | 1 | CAPACITY
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 246 |  |  | -0.00255 |  |  | 0.10478 |  | 1 | CAPACITY
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 102.85 |  |  | -0.00255 |  |  | 0.10478 |  | 1 | CAPACITY
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | -0.00255 |  |  | 0.08446 |  | 1 | ENERGY
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 10.68 |  |  | -0.00255 |  |  | 0.08446 |  | 1 | CAPACITY
220904 | CRANE G2 | 20 | 232 | 12 | 60 | 195 | 0 |  |  | -0.00257 |  |  | 0.10478 |  | 1 | NEW
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 516 |  |  | -0.00257 |  |  | 0.10478 |  | 1 | CAPACITY
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 512.95 |  |  | -0.00257 |  |  | 0.10478 |  | 1 | CAPACITY
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 318.73 |  |  | -0.00257 |  |  | 0.10478 |  | 1 | CAPACITY
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 140.6 | 112.88 |  |  | -0.00258 |  |  | 0.08446 |  | 1 | CAPACITY
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 91.2 |  |  | -0.00258 |  |  | 0.08446 |  | 1 | CAPACITY
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 83.5 |  |  | -0.00258 |  |  | 0.08446 |  | 1 | CAPACITY
220905 | CRANE GT | 4.16 | 232 | 55 | 0 | 14 | 0 |  |  | -0.00257 |  |  | 0.08446 |  | 1 | NEW
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 41.75 |  |  | -0.00258 |  |  | 0.08446 |  | 1 | CAPACITY
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0 |  |  | -0.00258 |  |  | 0 |  | 1 | NEWENERGY | AA2-072
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.21 |  |  | -0.00258 |  |  | 0 |  | 1 | CAPACITY
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.49 |  |  | -0.00259 |  |  | 0 |  | 1 | CAPACITY
226895 | WOAKV2-037 E | 69 | 233 | 65 | 0 | 4.5 | 0 |  |  | -0.00262 |  |  | 0 |  | 1 | ENERGY
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 695.27 |  |  | -0.00266 |  |  | 0.01494 |  | 1 | CAPACITY
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 675.85 |  |  | -0.00266 |  |  | 0.01494 |  | 1 | CAPACITY
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.76 |  |  | -0.00267 |  |  | 0 |  | 1 | CAPACITY
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | -0.00269 |  |  | 0.08446 |  | 1 | ENERGY
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0 |  |  | -0.0027 |  |  | 0 |  | 1 | NEWENERGY | AB2-157
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.69 |  |  | -0.0027 |  |  | 0 |  | 1 | CAPACITY
925011 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.64 |  |  | -0.0027 |  |  | 0 |  | 1 | CAPACITY | AB2-157
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 477.7 |  |  | -0.00271 |  |  | 0.10478 |  | 1 | CAPACITY
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 469.91 |  |  | -0.00271 |  |  | 0.10478 |  | 1 | CAPACITY
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | -0.00271 |  |  | 0.08446 |  | 1 | CAPACITY
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | -0.00271 |  |  | 0.08446 |  | 1 | CAPACITY
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 0 |  |  | -0.00272 |  |  | 0 |  | 1 | NEWENERGY | AC2-101
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 0 |  |  | -0.00272 |  |  | 0 |  | 1 | NEWENERGY | AC2-120
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | -0.00271 |  |  | 0.08446 |  | 1 | CAPACITY
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | -0.00271 |  |  | 0.08446 |  | 1 | CAPACITY
227024 | SMECOCT | 13.8 | 238 | 57 | 30 | 80.2 | 64.39 |  |  | -0.00271 |  |  | 0.08446 |  | 1 | CAPACITY
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 19.59 |  |  | -0.00271 |  |  | 0.08446 |  | 1 | CAPACITY
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 14.45 |  |  | -0.00271 |  |  | 0.08446 |  | 1 | CAPACITY
226915 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 9.92 |  |  | -0.00272 |  |  | 0 |  | 1 | CAPACITY | AC2-101
226912 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 8.39 |  |  | -0.00272 |  |  | 0 |  | 1 | CAPACITY | AC2-120
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 497.29 |  |  | -0.00272 |  |  | 0.10478 |  | 1 | CAPACITY
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 492.39 |  |  | -0.00272 |  |  | 0.10478 |  | 1 | CAPACITY
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 272.01 |  |  | -0.00272 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | -0.00272 |  |  | 0.04435 |  | 1 | CAPACITY | WALDORF
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | -0.00272 |  |  | 0 |  | 1 | CAPACITY | WALDORF
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00272 |  |  | 0.08446 |  | 1 | CAPACITY
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00272 |  |  | 0.08446 |  | 1 | CAPACITY
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00272 |  |  | 0.08446 |  | 1 | CAPACITY
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00272 |  |  | 0.08446 |  | 1 | CAPACITY
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | -0.00272 |  |  | 0.08446 |  | 1 | CAPACITY
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | -0.00272 |  |  | 0.08446 |  | 1 | CAPACITY
910861 | X3-087 C | 230 | 233 | 58 | 0 | 744 | 597.33 |  |  | -0.00277 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
917371 | Z2-060 | 230 | 233 | 58 | 0 | 116 | 93.13 |  |  | -0.00277 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
920642 | AA2-170 E | 230 | 233 | 58 | 0 | 19.1 | 0 |  |  | -0.00277 |  |  | 0.04435 |  | 1 | NEW | AA2-170
920641 | AA2-170 C | 230 | 233 | 58 | 0 | 92 | 73.86 |  |  | -0.00277 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-170
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 64.23 |  |  | -0.00277 |  |  | 0 |  | 1 | CAPACITY | PANDA
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | -0.00277 |  |  | 0 |  | 1 | CAPACITY | PANDA
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | -0.00277 |  |  | 0.04435 |  | 1 | CAPACITY | PANDA
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 330 | 264.94 |  |  | -0.00278 |  |  | 0 |  | 1 | CAPACITY | X4-035
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | -0.00278 |  |  | 0 |  | 1 | CAPACITY | X4-035
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | -0.00278 |  |  | 0.04435 |  | 1 | CAPACITY | X4-035
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | -0.00279 |  |  | 0.10478 |  | 1 | ENERGY
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | -0.00289 |  |  | 0.08446 |  | 1 | CAPACITY
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | -0.00289 |  |  | 0.08446 |  | 1 | CAPACITY
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 41.75 |  |  | -0.00289 |  |  | 0.10478 |  | 1 | CAPACITY
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 14.45 |  |  | -0.00289 |  |  | 0.08446 |  | 1 | CAPACITY
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 0 |  |  | -0.00297 |  |  | 0 |  | 1 | NEWENERGY | AB2-129
924771 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 0 |  |  | -0.00297 |  |  | 0 |  | 1 | NEW | AB2-129
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 245.67 |  |  | -0.00303 |  |  | 0 |  | 1 | CAPACITY | X4-039
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.00303 |  |  | 0.04435 |  | 1 | CAPACITY | X4-039
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.00303 |  |  | 0 |  | 1 | CAPACITY | X4-039
313821 | 6PACIFIC | 230 | 345 | 75 | 0 | 0.09 | 0 |  |  | -0.00304 |  |  | 0 |  | 1 | NEWENERGY
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 201.52 |  |  | -0.00308 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00308 |  |  | 0.04435 |  | 1 | CAPACITY | POSSUM POINT
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00308 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00308 |  |  | 0.10478 |  | 1 | CAPACITY
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00308 |  |  | 0.10478 |  | 1 | CAPACITY
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 28.74 |  |  | -0.00308 |  |  | 0.10478 |  | 1 | CAPACITY
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 28.66 |  |  | -0.00308 |  |  | 0.10478 |  | 1 | CAPACITY
314088 | 6VANDORN | 230 | 345 | 2 | 7 | 21 | 16.86 |  |  | -0.00308 |  |  | 0 |  | 1 | CAPACITY
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00311 |  |  | 0 |  | 1 | NEWENERGY | AC2-072
932521 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00311 |  |  | 0 |  | 1 | CAPACITY | AC2-072
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 0.68 | 0 |  |  | -0.00313 |  |  | 0 |  | 1 | NEWENERGY
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0 |  |  | -0.00314 |  |  | 0 |  | 1 | NEWENERGY | AC2-175
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0 |  |  | -0.00314 |  |  | 0 |  | 1 | NEWENERGY | AE1-081
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.77 |  |  | -0.00314 |  |  | 0 |  | 1 | CAPACITY | AE1-081
235002 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0 |  |  | -0.00316 |  |  | 0 |  | 1 | NEW | AC1-039
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0 |  |  | -0.00316 |  |  | 0 |  | 1 | NEWENERGY | AC1-039
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0 |  |  | -0.00316 |  |  | 0 |  | 1 | NEWENERGY | AA1-109
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 3.61 |  |  | -0.00316 |  |  | 0 |  | 1 | CAPACITY | AA1-109
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 1.61 |  |  | -0.00315 |  |  | 0 |  | 1 | CAPACITY
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00317 |  |  | 0.08446 |  | 1 | CAPACITY
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00317 |  |  | 0.08446 |  | 1 | CAPACITY
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 128.86 |  |  | -0.00317 |  |  | 0.08446 |  | 1 | CAPACITY
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 152.3 | 122.28 |  |  | -0.00317 |  |  | 0.10478 |  | 1 | CAPACITY
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00317 |  |  | 0.10478 |  | 1 | CAPACITY
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00317 |  |  | 0.10478 |  | 1 | CAPACITY
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 120.19 |  |  | -0.00317 |  |  | 0.10478 |  | 1 | CAPACITY
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.00318 |  |  | 0 |  | 1 | NEWENERGY | W1-116
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 4.27 |  |  | -0.00318 |  |  | 0 |  | 1 | CAPACITY | W1-116
315033 | 1BIRCHWDA | 18 | 345 | 13 | 85 | 238 | 191.08 |  |  | -0.00319 |  |  | 0.10478 |  | 1 | CAPACITY
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 0 |  |  | -0.00318 |  |  | 0 |  | 1 | NEWENERGY | AB2-029
314078 | 3REMNGTN | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00318 |  |  | 0 |  | 1 | CAPACITY | AB2-029
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.0032 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 2
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.0032 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 1
926738 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.0032 |  |  | 0 |  | 1 | CAPACITY | AC1-158 2
926737 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.0032 |  |  | 0 |  | 1 | CAPACITY | AC1-158 1
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00321 |  |  | 0.08446 |  | 1 | CAPACITY
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00321 |  |  | 0.08446 |  | 1 | CAPACITY
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 128.94 |  |  | -0.00321 |  |  | 0.08446 |  | 1 | CAPACITY
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 128.54 |  |  | -0.00321 |  |  | 0.08446 |  | 1 | CAPACITY
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 128.3 |  |  | -0.00321 |  |  | 0.08446 |  | 1 | CAPACITY
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0 |  |  | -0.0032 |  |  | 0 |  | 1 | NEWENERGY | AC2-136
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 6.98 |  |  | -0.0032 |  |  | 0 |  | 1 | CAPACITY
933251 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 4.41 |  |  | -0.0032 |  |  | 0 |  | 1 | CAPACITY | AC2-136
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 2.99 |  |  | -0.00321 |  |  | 0 |  | 1 | CAPACITY | Y1-020
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 761.83 |  |  | -0.00322 |  |  | 0.01494 |  | 1 | CAPACITY
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 761.51 |  |  | -0.00322 |  |  | 0.01494 |  | 1 | CAPACITY
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0 |  |  | -0.00323 |  |  | 0 |  | 1 | NEWENERGY | AB1-096
923872 | AB2-027 E | 34.5 | 201 | 75 | 0 | 5.5 | 0 |  |  | -0.00322 |  |  | 0 |  | 1 | NEWENERGY | AB2-027
235006 | AB2-027 C | 34.5 | 201 | 75 | 0 | 3.3 | 0 |  |  | -0.00322 |  |  | 0 |  | 1 | NEW | AB2-027
930521 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00323 |  |  | 0 |  | 1 | CAPACITY | AB1-096
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00322 |  |  | 0 |  | 1 | CAPACITY
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00323 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
923213 | AB1-125 E OP | 34.5 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.00323 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
923202 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.00323 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
923212 | AB1-125 C OP | 34.5 | 201 | 75 | 0 | 5.7 | 0 |  |  | -0.00323 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
316149 | AD1-046 E | 230 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00324 |  |  | 0 |  | 1 | NEWENERGY | AD1-044
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00324 |  |  | 0 |  | 1 | NEWENERGY | W4-102
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0 |  |  | -0.00325 |  |  | 0 |  | 1 | NEWENERGY | AB2-097
237799 | 01AA2-159 C | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.00324 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
920562 | AA2-159 E | 34.5 | 201 | 75 | 0 | 7.3 | 0 |  |  | -0.00324 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00324 |  |  | 0 |  | 1 | NEWENERGY | AE1-124
316148 | AD1-046 C | 230 | 345 | 75 | 0 | 30.7 | 24.65 |  |  | -0.00324 |  |  | 0 |  | 1 | CAPACITY | AD1-044
938961 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00324 |  |  | 0 |  | 1 | CAPACITY | AE1-124
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00324 |  |  | 0 |  | 1 | CAPACITY | W4-102
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 2.09 |  |  | -0.00325 |  |  | 0 |  | 1 | CAPACITY
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.88 |  |  | -0.00325 |  |  | 0 |  | 1 | CAPACITY
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 0 |  |  | -0.00325 |  |  | 0 |  | 1 | NEWENERGY | AB2-158
925021 | AB2-158 C | 230 | 345 | 75 | 0 | 61 | 48.97 |  |  | -0.00325 |  |  | 0 |  | 1 | CAPACITY | AB2-158
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 0 |  |  | -0.00326 |  |  | 0 |  | 1 | NEWENERGY | AC1-118
314766 | 6LOUISA | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00325 |  |  | 0 |  | 1 | NEWENERGY
314190 | 6WESTMOR | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00326 |  |  | 0 |  | 1 | CAPACITY | AC1-118
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 136.49 |  |  | -0.00327 |  |  | 0.08446 |  | 1 | CAPACITY
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | -0.00327 |  |  | 0.07484 |  | 1 | CAPACITY
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | -0.00327 |  |  | 0.07484 |  | 1 | CAPACITY
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 77.07 |  |  | -0.00326 |  |  | 0.07484 |  | 1 | CAPACITY
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | -0.00326 |  |  | 0.07484 |  | 1 | CAPACITY
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | -0.00326 |  |  | 0.07484 |  | 1 | CAPACITY
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0 |  |  | -0.00326 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 38.54 |  |  | -0.00326 |  |  | 0.07484 |  | 1 | CAPACITY
923192 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0 |  |  | -0.00326 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0 |  |  | -0.00326 |  |  | 0 |  | 1 | NEWENERGY | AA1-095
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 2.33 |  |  | -0.00326 |  |  | 0 |  | 1 | CAPACITY | AA1-095
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.00328 |  |  | 0.08446 |  | 1 | CAPACITY
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.00328 |  |  | 0.08446 |  | 1 | CAPACITY
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 126.85 |  |  | -0.00328 |  |  | 0.08446 |  | 1 | CAPACITY
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.00328 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.00328 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00328 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 5
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00328 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 6
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00328 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00328 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00328 |  |  | 0.08446 |  | 1 | CAPACITY
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00328 |  |  | 0.08446 |  | 1 | CAPACITY
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00328 |  |  | 0.08446 |  | 1 | CAPACITY
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 61.9 |  |  | -0.00328 |  |  | 0.08446 |  | 1 | CAPACITY
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00327 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00327 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 2
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00328 |  |  | 0 |  | 1 | NEWENERGY | AC2-138
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 19.99 |  |  | -0.00328 |  |  | 0.10478 |  | 1 | CAPACITY
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00327 |  |  | 0 |  | 1 | CAPACITY | South Anna 2
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00327 |  |  | 0 |  | 1 | CAPACITY | South Anna 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 19.27 |  |  | -0.00328 |  |  | 0.10478 |  | 1 | CAPACITY
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 6.3 | 5.06 |  |  | -0.00328 |  |  | 0 |  | 1 | CAPACITY | AC2-138
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0 |  |  | -0.00328 |  |  | 0 |  | 1 | NEWENERGY | AA1-092
314172 | 6DUNNSVL | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00328 |  |  | 0 |  | 1 | NEWENERGY
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 6.42 |  |  | -0.00328 |  |  | 0 |  | 1 | CAPACITY | AA1-092
314734 | 6CASHSCORNER | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00329 |  |  | 0 |  | 1 | NEWENERGY
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0 |  |  | -0.00329 |  |  | 0 |  | 1 | NEWENERGY | W3-110
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 2.29 |  |  | -0.00329 |  |  | 0 |  | 1 | CAPACITY | W3-110
314222 | 6HANOVER | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00329 |  |  | 0 |  | 1 | NEWENERGY
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 3.21 |  |  | -0.00331 |  |  | 0 |  | 1 | CAPACITY
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | -0.00332 |  |  | 0 |  | 1 | NEW | AC1-107
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00332 |  |  | 0 |  | 1 | NEW | AC1-107
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00332 |  |  | 0.04435 |  | 1 | NEW | AC1-107
926785 | AC1-164 E | 0.44 | 345 | 75 | 0 | 99.2 | 0 |  |  | -0.00332 |  |  | 0 |  | 1 | NEWENERGY | AC1-164
316114 | AB2-068 ST | 22 | 345 | 58 | 0 | 492 | 395.01 |  |  | -0.00332 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316112 | AB2-068 CT1 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00332 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-068
316113 | AB2-068 CT2 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00332 |  |  | 0 |  | 1 | CAPACITY | AB2-068
926784 | AC1-164 C | 0.44 | 345 | 75 | 0 | 220.8 | 177.27 |  |  | -0.00332 |  |  | 0 |  | 1 | NEW | AC1-164
314189 | 6PAPERMILL | 230 | 345 | 1 | 12 | 37 | 0 |  |  | -0.00332 |  |  | 0.10478 |  | 1 | ENERGY
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00332 |  |  | 0 |  | 1 | NEWENERGY | AC1-065
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 69.05 |  |  | -0.00332 |  |  | 0.10478 |  | 1 | CAPACITY
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 68.97 |  |  | -0.00332 |  |  | 0.10478 |  | 1 | CAPACITY
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 68.72 |  |  | -0.00332 |  |  | 0.10478 |  | 1 | CAPACITY
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 68.64 |  |  | -0.00332 |  |  | 0.10478 |  | 1 | CAPACITY
925863 | AC1-065 C | 0.39 | 345 | 75 | 0 | 41.8 | 33.56 |  |  | -0.00332 |  |  | 0 |  | 1 | CAPACITY | AC1-065
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.00332 |  |  | 0 |  | 1 | NEWENERGY | AC2-137
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00331 |  |  | 0 |  | 1 | NEWENERGY | AD2-030
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00332 |  |  | 0 |  | 1 | NEWENERGY | AE1-074
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00332 |  |  | 0 |  | 1 | NEWENERGY | AB2-024
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0 |  |  | -0.00331 |  |  | 0 |  | 1 | NEWENERGY | AC1-112
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00331 |  |  | 0 |  | 1 | NEWENERGY | AB1-027
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00332 |  |  | 0 |  | 1 | NEWENERGY | AD1-063
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 16.06 |  |  | -0.00332 |  |  | 0.12623 |  | 1 | CAPACITY
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0 |  |  | -0.00331 |  |  | 0 |  | 1 | NEWENERGY | AC2-070
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.3 | 13.09 |  |  | -0.00332 |  |  | 0.12623 |  | 1 | CAPACITY
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 11.96 |  |  | -0.00332 |  |  | 0.12623 |  | 1 | CAPACITY
938551 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00332 |  |  | 0 |  | 1 | CAPACITY | AE1-074
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00331 |  |  | 0 |  | 1 | CAPACITY | AD2-030
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 11.4 | 9.15 |  |  | -0.00332 |  |  | 0 |  | 1 | CAPACITY | AC2-137
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 8.83 |  |  | -0.00331 |  |  | 0.12623 |  | 1 | CAPACITY
314375 | 6CORRCTN | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00332 |  |  | 0 |  | 1 | CAPACITY | AB2-024
314187 | 3WAN 176 | 115 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00331 |  |  | 0 |  | 1 | NEWENERGY
314241 | 6OLDCHRC | 230 | 345 | 75 | 0 | 1.82 | 0 |  |  | -0.00331 |  |  | 0 |  | 1 | CAPACITY | AB1-027
932501 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 7.39 |  |  | -0.00331 |  |  | 0 |  | 1 | CAPACITY | AC2-070
934391 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.00332 |  |  | 0 |  | 1 | CAPACITY | AD1-063
314176 | 6HARMONY | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00332 |  |  | 0 |  | 1 | NEWENERGY
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 4.98 |  |  | -0.00331 |  |  | 0 |  | 1 | CAPACITY
314213 | 3CARVER | 115 | 345 | 75 | 0 | 0 | 0 |  |  | -0.00331 |  |  | 0 |  | 1 | NEWENERGY
315085 | 1SPRUNCC | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00332 |  |  | 0.10478 |  | 1 | NEW
315086 | 1SPRUNCD | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00332 |  |  | 0.10478 |  | 1 | NEW
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 104.93 |  |  | -0.00332 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 7
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 103.25 |  |  | -0.00332 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 8
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 53.15 |  |  | -0.00332 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 48.17 |  |  | -0.00332 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0 |  |  | -0.00332 |  |  | 0 |  | 1 | NEWENERGY | W3-106
314294 | 6ENON | 230 | 345 | 75 | 0 | 0.23 | 0 |  |  | -0.00332 |  |  | 0 |  | 1 | NEWENERGY
313828 | 3WHITEMARSH | 115 | 345 | 75 | 0 | 0.05 | 0 |  |  | -0.00333 |  |  | 0 |  | 1 | NEWENERGY
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | -0.00333 |  |  | 0.10478 |  | 1 | ENERGY
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 101.16 |  |  | -0.00333 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00333 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00333 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00333 |  |  | 0.04435 |  | 1 | CAPACITY | HOPEWELL HCF
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00333 |  |  | 0.10478 |  | 1 | CAPACITY
314177 | 3HAYES89 | 115 | 345 | 75 | 0 | 0.31 | 0 |  |  | -0.00333 |  |  | 0 |  | 1 | NEWENERGY
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 678.09 |  |  | -0.00335 |  |  | 0.01494 |  | 1 | CAPACITY
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 677.21 |  |  | -0.00335 |  |  | 0.01494 |  | 1 | CAPACITY
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 788.9 | 633.38 |  |  | -0.00334 |  |  | 0.10478 |  | 1 | CAPACITY
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 422.86 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 0 |  |  | -0.00334 |  |  | 0 |  | 1 | NEWENERGY | AB2-134
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00334 |  |  | 0.04435 |  | 1 | CAPACITY | WARREN COUNTY CC
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00334 |  |  | 0 |  | 1 | NEWENERGY | AB2-160
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 0 |  |  | -0.00334 |  |  | 0 |  | 1 | NEWENERGY | AB2-190
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 89.92 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY | AB2-190
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 69.77 |  |  | -0.00335 |  |  | 0.10478 |  | 1 | CAPACITY
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 69.69 |  |  | -0.00335 |  |  | 0.10478 |  | 1 | CAPACITY
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00335 |  |  | 0.10478 |  | 1 | CAPACITY
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00335 |  |  | 0.10478 |  | 1 | CAPACITY
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 57.65 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY | AB2-134
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 24.41 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY | AB2-160
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 23.76 |  |  | -0.00335 |  |  | 0.10478 |  | 1 | CAPACITY
316158 | AD2-164 | 230 | 345 | 57 | 0 | 26.7 | 21.44 |  |  | -0.00334 |  |  | 0.08446 |  | 1 | CAPACITY
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 12.04 |  |  | -0.00335 |  |  | 0.12623 |  | 1 | CAPACITY
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 8.03 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY
313812 | 6ROCKLANDING | 230 | 345 | 75 | 0 | 0.11 | 0 |  |  | -0.00334 |  |  | 0 |  | 1 | NEWENERGY
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY | AB2-161
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 88.96 |  |  | -0.00336 |  |  | 0.10478 |  | 1 | CAPACITY
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 87.83 |  |  | -0.00336 |  |  | 0.10478 |  | 1 | CAPACITY
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 86.31 |  |  | -0.00336 |  |  | 0.10478 |  | 1 | CAPACITY
314331 | 6POE | 230 | 345 | 75 | 0 | 12.27 | 0 |  |  | -0.00335 |  |  | 0 |  | 1 | NEWENERGY
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00335 |  |  | 0 |  | 1 | NEWENERGY | AE1-162
935212 | AD1-156 E | 230 | 345 | 75 | 0 | 7.92 | 0 |  |  | -0.00335 |  |  | 0 |  | 1 | NEWENERGY | AD1-156
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY | AB2-161
316258 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00335 |  |  | 0 |  | 1 | CAPACITY | AE1-162
935211 | AD1-156 C | 230 | 345 | 75 | 0 | 11.82 | 9.49 |  |  | -0.00335 |  |  | 0 |  | 1 | CAPACITY | AD1-156
314533 | 6SMITFLD | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00335 |  |  | 0 |  | 1 | NEWENERGY
206742 | 28SUX_V3-011 | 34.5 | 228 | 64 | 0 | 2 | 0 |  |  | -0.00335 |  |  | 0 |  | 1 | CAPACITY
314453 | 6CHRHLND | 230 | 345 | 75 | 0 | 0.08 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | NEWENERGY | AA1-139
314525 | 6KINGFORK | 230 | 345 | 75 | 0 | 24.3 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY
314550 | 6HICKORY | 230 | 345 | 75 | 0 | 22.93 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 63.18 |  |  | -0.00337 |  |  | 0 |  | 1 | CAPACITY | AA1-139
314466 | 6FENTRES | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY
314632 | 6AYDLETOLD | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | NEWENERGY
313717 | 6SLIGO L2192 | 230 | 345 | 75 | 0 | 12.34 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | NEWENERGY
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY | Z1-068
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY | AD1-060
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | -0.00336 |  |  | 0.05 |  | 1 | MTX | AA2-061
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY | AC1-147
316145 | AE1-027 E | 230 | 345 | 75 | 0 | 6.9 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY | AE1-027
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY | AC2-196
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY | AC1-027
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY | AB2-026
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | NEWENERGY | AC2-174
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | NEWENERGY | Z2-030
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | -0.00336 |  |  | 0.05 |  | 1 | MTX | AA2-060
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY | AE1-075
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY | AD1-144
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY | AD2-215
316147 | AE1-028 E | 230 | 345 | 75 | 0 | 4.4 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY | AE1-028
314333 | 6POWHATN | 230 | 345 | 75 | 0 | 3.97 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY | AB2-026
933571 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | NEW | AC2-174
314645 | 6SLIGO L269 | 230 | 345 | 75 | 0 | 3.22 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | NEWENERGY
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 12.2 |  |  | -0.00336 |  |  | 0.10478 |  | 1 | CAPACITY
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 12.04 |  |  | -0.00337 |  |  | 0.12623 |  | 1 | CAPACITY
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 11.96 |  |  | -0.00336 |  |  | 0.10478 |  | 1 | CAPACITY
316144 | AE1-027 C | 230 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY | AE1-027
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 10.36 |  |  | -0.00336 |  |  | 0.10478 |  | 1 | CAPACITY
926661 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 10.12 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY | AC1-147
938561 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY | AE1-075
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 9.55 |  |  | -0.00336 |  |  | 0.10478 |  | 1 | CAPACITY
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 9.05 |  |  | -0.00336 |  |  | 0.12623 |  | 1 | CAPACITY
933731 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 8.03 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY | AC2-196
316150 | AD2-215 C | 230 | 345 | 76 | 0 | 9.8 | 7.87 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY | AD2-215
935111 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 7.79 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY | AD1-144
314491 | 3PENDLTN | 115 | 345 | 75 | 0 | 1.89 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY | AC1-027
316146 | AE1-028 C | 230 | 345 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY | AE1-028
934362 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 4.58 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY | AD1-060
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 3.93 |  |  | -0.00337 |  |  | 0 |  | 1 | CAPACITY
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00337 |  |  | 0 |  | 1 | CAPACITY | Z2-030
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 1.61 |  |  | -0.00337 |  |  | 0 |  | 1 | CAPACITY
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.2 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY | Z1-068
314640 | 6KITTY HAWK | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | NEWENERGY
314487 | 3MCLAUGH | 115 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | NEWENERGY
901082 | W1-029 E | 230 | 345 | 74 | 0 | 261 | 0 |  |  | -0.00338 |  |  | 0 |  | 1 | NEWENERGY | W1-029
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | NEWENERGY | Y1-086
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00338 |  |  | 0 |  | 1 | CAPACITY | W1-029
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | NEWENERGY | AB2-022
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00338 |  |  | 0 |  | 1 | NEWENERGY | Z2-027
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 10.44 |  |  | -0.00337 |  |  | 0 |  | 1 | CAPACITY | AB2-022
314648 | 6SUNBURY | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | NEWENERGY
314638 | 6ELIZ CT | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | CAPACITY | Y1-086
314639 | 6TANGLEW | 230 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00338 |  |  | 0 |  | 1 | CAPACITY | Z2-027
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.56 |  |  | -0.00338 |  |  | 0 |  | 1 | CAPACITY
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00339 |  |  | 0 |  | 1 | NEWENERGY | AB2-025
314651 | 6WINFALL | 230 | 345 | 75 | 0 | 3.35 | 0 |  |  | -0.00338 |  |  | 0 |  | 1 | NEWENERGY
314435 | 6SAPONY | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00339 |  |  | 0 |  | 1 | CAPACITY | AB2-025
942852 | AE2-304 E | 230 | 345 | 75 | 0 | 1.4 | 0 |  |  | -0.00338 |  |  | 0 |  | 1 | NEWENERGY | AE2-304
942851 | AE2-304 C | 230 | 345 | 75 | 0 | 3.3 | 2.65 |  |  | -0.00338 |  |  | 0 |  | 1 | CAPACITY | AE2-304
314662 | 6S HERTFORD | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00338 |  |  | 0 |  | 1 | NEWENERGY
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 0 |  |  | -0.00339 |  |  | 0 |  | 1 | NEWENERGY | Z1-036
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | -0.0034 |  |  | 0.10478 |  | 1 | ENERGY
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00339 |  |  | 0 |  | 1 | CAPACITY | Z1-036
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00339 |  |  | 0 |  | 1 | NEWENERGY | X1-012
314637 | 6EDENTON | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.0034 |  |  | 0 |  | 1 | NEWENERGY | AA2-059
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 2.97 |  |  | -0.00339 |  |  | 0 |  | 1 | CAPACITY | X1-012
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 480.11 |  |  | -0.0034 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 452.01 |  |  | -0.00341 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.0034 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-086
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.0034 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.0034 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00341 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00341 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00341 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 0 |  |  | -0.0034 |  |  | 0 |  | 1 | NEW | AB2-015
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 0 |  |  | -0.0034 |  |  | 0 |  | 1 | NEWENERGY | AB2-015
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00341 |  |  | 0 |  | 1 | NEWENERGY | AA2-178
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00341 |  |  | 0 |  | 1 | CAPACITY | AA2-178
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00341 |  |  | 0.10478 |  | 1 | CAPACITY
314541 | 3WATKINS | 115 | 345 | 1 | 0 | 4 | 0 |  |  | -0.0034 |  |  | 0 |  | 1 | ENERGY
314566 | 3CRESWEL | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00341 |  |  | 0 |  | 1 | NEWENERGY
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 322.35 |  |  | -0.00342 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 198.31 |  |  | -0.00342 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00342 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00342 |  |  | 0.04435 |  | 1 | CAPACITY | BEAR GARDEN
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00342 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00342 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00342 |  |  | 0.04435 |  | 1 | CAPACITY | FLUVANNA
314594 | 6PLYMOTH | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00342 |  |  | 0 |  | 1 | NEWENERGY
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 0 |  |  | -0.00342 |  |  | 0 |  | 1 | NEWENERGY | AA2-088
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00342 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00342 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 2
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 0 |  |  | -0.00342 |  |  | 0 |  | 1 | NEWENERGY | AC1-116
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 30.51 |  |  | -0.00342 |  |  | 0 |  | 1 | CAPACITY | AA2-088
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEWENERGY | AC2-071
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00342 |  |  | 0 |  | 1 | CAPACITY | AB2-100 1
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00342 |  |  | 0 |  | 1 | CAPACITY | AB2-100 2
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEWENERGY | AB2-045
314589 | 3MURPHYS | 115 | 345 | 75 | 0 | 4.66 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | CAPACITY | V4-068
932511 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00343 |  |  | 0 |  | 1 | CAPACITY | AC2-071
314677 | 6BUCKING | 230 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | CAPACITY | AB2-045
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEWENERGY | V4-068
314620 | 6CASHIE | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEWENERGY
926451 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 3.77 |  |  | -0.00342 |  |  | 0 |  | 1 | CAPACITY | AC1-116
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00342 |  |  | 0 |  | 1 | CAPACITY
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEWENERGY | AA1-065
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY | AA1-063A
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 53.6 | 43.03 |  |  | -0.00343 |  |  | 0 |  | 1 | CAPACITY | AA1-065
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 40.87 |  |  | -0.00344 |  |  | 0 |  | 1 | CAPACITY | AA1-063A
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 40.14 |  |  | -0.00343 |  |  | 0.19858 |  | 1 | CAPACITY
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEW
314617 | 3TUNIS | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEWENERGY
314568 | 3EARLEYS | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY | AB2-099
314551 | 3AHOSKIE | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00344 |  |  | 0 |  | 1 | CAPACITY | AB2-099
314604 | 3SEABORD | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY
313826 | 6HYDRAULIC | 230 | 345 | 75 | 0 | 0.04 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEWENERGY
923262 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
923991 | AB2-040 C O1 | 115 | 345 | 75 | 0 | 44 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEW | AB2-040
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY | AB2-174
923992 | AB2-040 E O1 | 115 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY | AB2-040
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 0 |  |  | -0.00345 |  |  | 0 |  | 1 | NEWENERGY | AA2-053
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.00344 |  |  | 0.07484 |  | 1 | CAPACITY
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.00344 |  |  | 0.07484 |  | 1 | CAPACITY
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY | AB1-127
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY | AB1-128
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 44 |  |  | -0.00345 |  |  | 0 |  | 1 | CAPACITY | AA2-053
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 33.72 |  |  | -0.00344 |  |  | 0 |  | 1 | CAPACITY | AB2-174
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 32.44 |  |  | -0.00344 |  |  | 0 |  | 1 | CAPACITY | AB1-173
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY | AB1-173
314266 | 6NORTHAMPTON | 230 | 345 | 75 | 0 | 2.47 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 8.83 |  |  | -0.00345 |  |  | 0.12623 |  | 1 | CAPACITY
235041 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00344 |  |  | 0 |  | 1 | CAPACITY | AB1-128
235040 | 01AB1-127 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00344 |  |  | 0 |  | 1 | CAPACITY | AB1-127
314626 | 3WOODLND | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00344 |  |  | 0 |  | 1 | NEWENERGY
314596 | 3POPLR C | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00345 |  |  | 0 |  | 1 | NEWENERGY
314582 | 3KELFORD | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00345 |  |  | 0 |  | 1 | CAPACITY | Z2-043
314762 | 3JAMES R | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00345 |  |  | 0 |  | 1 | NEWENERGY
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.5 | 354.46 |  |  | -0.00345 |  |  | 0.10478 |  | 1 | CAPACITY
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 350.93 |  |  | -0.00345 |  |  | 0.10478 |  | 1 | CAPACITY
925122 | AB2-169 E | 115 | 345 | 75 | 0 | 35 | 0 |  |  | -0.00345 |  |  | 0 |  | 1 | NEWENERGY | AB2-169
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 0 |  |  | -0.00346 |  |  | 0 |  | 1 | NEWENERGY | AD1-085
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 76.6 | 61.5 |  |  | -0.00345 |  |  | 0.04435 |  | 1 | CAPACITY | ROSEMARY
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 40.38 |  |  | -0.00345 |  |  | 0.07484 |  | 1 | CAPACITY
314713 | 3PAMPLIN | 115 | 345 | 75 | 0 | 9.73 | 0 |  |  | -0.00346 |  |  | 0 |  | 1 | NEWENERGY
314807 | 3MT JACK | 115 | 345 | 75 | 0 | 9.7 | 0 |  |  | -0.00345 |  |  | 0 |  | 1 | NEWENERGY
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 38.54 |  |  | -0.00345 |  |  | 0.07484 |  | 1 | CAPACITY
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 47.5 | 38.13 |  |  | -0.00345 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
316143 | AD1-160 E | 115 | 345 | 75 | 0 | 9.1 | 0 |  |  | -0.00346 |  |  | 0 |  | 1 | NEWENERGY | AD1-160
925121 | AB2-169 C | 115 | 345 | 75 | 0 | 39 | 31.31 |  |  | -0.00345 |  |  | 0 |  | 1 | CAPACITY | AB2-169
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 35.9 | 28.82 |  |  | -0.00345 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00346 |  |  | 0 |  | 1 | NEWENERGY | AD1-157
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0 |  |  | -0.00345 |  |  | 0 |  | 1 | NEWENERGY | AC2-074
314578 | 3HORNRTN | 115 | 345 | 75 | 0 | 5.15 | 0 |  |  | -0.00345 |  |  | 0 |  | 1 | NEWENERGY
314579 | 6HORNRTN | 230 | 345 | 75 | 0 | 3.91 | 0 |  |  | -0.00345 |  |  | 0 |  | 1 | NEWENERGY
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 9.88 |  |  | -0.00346 |  |  | 0 |  | 1 | CAPACITY | AD1-085
932541 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00345 |  |  | 0 |  | 1 | CAPACITY | AC2-074
935221 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.00346 |  |  | 0 |  | 1 | CAPACITY | AD1-157
316142 | AD1-160 C | 115 | 345 | 75 | 0 | 6.6 | 5.3 |  |  | -0.00346 |  |  | 0 |  | 1 | CAPACITY | AD1-160
314559 | 3CAROLNA | 115 | 345 | 75 | 0 | 1.21 | 0 |  |  | -0.00345 |  |  | 0 |  | 1 | NEWENERGY
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 1.04 |  |  | -0.00346 |  |  | 0 |  | 1 | CAPACITY
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.64 |  |  | -0.00346 |  |  | 0 |  | 1 | CAPACITY
313853 | 3PONTONDP | 115 | 345 | 2 | 0 | 4 | 0 |  |  | -0.00346 |  |  | 0 |  | 1 | ENERGY
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 16 | 12.85 |  |  | -0.00346 |  |  | 0.12623 |  | 1 | CAPACITY
314603 | 3SCOT NK | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00346 |  |  | 0 |  | 1 | NEWENERGY
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00348 |  |  | 0 |  | 1 | NEWENERGY | AC1-054
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 0 |  |  | -0.00347 |  |  | 0 |  | 1 | NEWENERGY | AC1-036
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 35.73 |  |  | -0.00348 |  |  | 0 |  | 1 | CAPACITY | AC1-054
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00347 |  |  | 0 |  | 1 | NEWENERGY | AE1-098
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00347 |  |  | 0 |  | 1 | NEWENERGY | AE1-099
314593 | 3PARMELE | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00347 |  |  | 0 |  | 1 | NEWENERGY
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00347 |  |  | 0 |  | 1 | CAPACITY | AE1-099
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00347 |  |  | 0 |  | 1 | CAPACITY | AE1-098
925611 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 6.9 |  |  | -0.00347 |  |  | 0 |  | 1 | CAPACITY | AC1-036
314629 | 3MARTNCO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00347 |  |  | 0 |  | 1 | NEWENERGY
314798 | 3MERCK5 | 115 | 345 | 75 | 0 | 0.16 | 0 |  |  | -0.00347 |  |  | 0 |  | 1 | NEWENERGY
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00349 |  |  | 0 |  | 1 | NEWENERGY | AB2-043
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 0 |  |  | -0.00348 |  |  | 0 |  | 1 | NEWENERGY | AB2-060
919702 | AA2-057 E OP | 115 | 345 | 75 | 0 | 21.1 | 0 |  |  | -0.00349 |  |  | 0 |  | 1 | NEWENERGY | AA2-057
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 43.67 |  |  | -0.00348 |  |  | 0 |  | 1 | CAPACITY | AB2-060
313719 | 3CHESTNUT | 115 | 345 | 75 | 0 | 44.7 | 35.89 |  |  | -0.00349 |  |  | 0 |  | 1 | CAPACITY | AA2-057
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00349 |  |  | 0 |  | 1 | NEWENERGY | AB2-078
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00349 |  |  | 0 |  | 1 | NEWENERGY | AB2-077
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00349 |  |  | 0 |  | 1 | NEWENERGY | AB2-079
314574 | 6EVERETS | 230 | 345 | 75 | 0 | 5.89 | 0 |  |  | -0.00348 |  |  | 0 |  | 1 | NEWENERGY
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0 |  |  | -0.00348 |  |  | 0 |  | 1 | NEWENERGY | AA1-067
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 15.17 |  |  | -0.00349 |  |  | 0 |  | 1 | CAPACITY | AB2-043
924321 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00349 |  |  | 0 |  | 1 | NEW | AB2-079
924301 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00349 |  |  | 0 |  | 1 | NEW | AB2-077
924311 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00349 |  |  | 0 |  | 1 | NEW | AB2-078
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | Z2-088
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 53 | 42.55 |  |  | -0.0035 |  |  | 0 |  | 1 | CAPACITY | Z2-088
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.0035 |  |  | 0.08446 |  | 1 | CAPACITY
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.0035 |  |  | 0.08446 |  | 1 | CAPACITY
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.0035 |  |  | 0.07484 |  | 1 | CAPACITY
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.0035 |  |  | 0.07484 |  | 1 | CAPACITY
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.0035 |  |  | 0.07484 |  | 1 | CAPACITY
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.0035 |  |  | 0.07484 |  | 1 | CAPACITY
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.0035 |  |  | 0.07484 |  | 1 | CAPACITY
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.0035 |  |  | 0.07484 |  | 1 | CAPACITY
314608 | 3TARBORO | 115 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | Z2-044
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 12.04 |  |  | -0.0035 |  |  | 0.07484 |  | 1 | CAPACITY
314623 | 3WITAKRS | 115 | 345 | 75 | 0 | 2.51 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | CAPACITY | Z2-044
314557 | 3BETHELC | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY
314549 | 3TOT1 | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY
314607 | 3TAR RVR | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY
314545 | 3TOT5 | 115 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY
314560 | 3CNETO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 0 |  |  | -0.00351 |  |  | 0 |  | 1 | NEWENERGY | AB2-059
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00351 |  |  | 0 |  | 1 | NEWENERGY | AB1-081
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 52.99 |  |  | -0.00351 |  |  | 0 |  | 1 | CAPACITY | AB2-059
922922 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00351 |  |  | 0 |  | 1 | CAPACITY | AB1-081
314554 | 3BTLEBRO | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00351 |  |  | 0 |  | 1 | NEWENERGY
314205 | 3HEARTS | 115 | 345 | 75 | 0 | 0.41 | 0 |  |  | -0.00351 |  |  | 0 |  | 1 | NEWENERGY
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 0 |  |  | -0.00352 |  |  | 0 |  | 1 | NEWENERGY | T157
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 0 |  |  | -0.00352 |  |  | 0 |  | 1 | NEWENERGY | AC1-105
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 36.61 |  |  | -0.00352 |  |  | 0.10478 |  | 1 | CAPACITY
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 27.7 |  |  | -0.00352 |  |  | 0 |  | 1 | CAPACITY | AC1-105
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 16.46 |  |  | -0.00352 |  |  | 0 |  | 1 | CAPACITY | T157
315616 | AA1-038 C | 230 | 345 | 74 | 0 | 76.6 | 0 |  |  | -0.00354 |  |  | 0 |  | 1 | NEW | AA1-038
918232 | AA1-038 E | 230 | 345 | 74 | 0 | 66.7 | 0 |  |  | -0.00354 |  |  | 0 |  | 1 | NEWENERGY | AA1-038
314860 | 4E MILL | 138 | 345 | 2 | 0 | 50 | 0 |  |  | -0.00354 |  |  | 0.10478 |  | 1 | ENERGY
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 20.23 |  |  | -0.00354 |  |  | 0.10478 |  | 1 | CAPACITY
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 20.15 |  |  | -0.00354 |  |  | 0.10478 |  | 1 | CAPACITY
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00353 |  |  | 0 |  | 1 | NEWENERGY | W4-064
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00354 |  |  | 0 |  | 1 | CAPACITY
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00353 |  |  | 0 |  | 1 | CAPACITY | W4-064
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 404.48 |  |  | -0.00355 |  |  | 0.0316 |  | 1 | CAPACITY
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 403.68 |  |  | -0.00355 |  |  | 0.0316 |  | 1 | CAPACITY
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 403.27 |  |  | -0.00355 |  |  | 0.0316 |  | 1 | CAPACITY
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 403.2 |  |  | -0.00355 |  |  | 0.0316 |  | 1 | CAPACITY
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00355 |  |  | 0.0316 |  | 1 | CAPACITY
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00355 |  |  | 0.0316 |  | 1 | CAPACITY
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 0 |  |  | -0.00355 |  |  | 0 |  | 1 | NEWENERGY | K11
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 30.67 |  |  | -0.00355 |  |  | 0 |  | 1 | CAPACITY | K11
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 443.98 |  |  | -0.00356 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM2
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 440.13 |  |  | -0.00356 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 419.81 |  |  | -0.00356 |  |  | 0.10478 |  | 1 | CAPACITY
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 9.55 |  |  | -0.00356 |  |  | 0.08446 |  | 1 | CAPACITY
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 0 |  |  | -0.00359 |  |  | 0 |  | 1 | NEWENERGY | AC1-075
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 30.75 |  |  | -0.00359 |  |  | 0 |  | 1 | CAPACITY | AC1-075
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 0 |  |  | -0.00359 |  |  | 0 |  | 1 | NEWENERGY | AC1-080
926023 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 10.28 |  |  | -0.00359 |  |  | 0 |  | 1 | CAPACITY | AC1-080
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 68.3 |  |  |  | -0.0036
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 23.68 |  |  | -0.00364 |  |  | 0.12623 |  | 1 | CAPACITY
244012 | 05PINNACLE | 4 | 205 | 1 | 0 | 11 | 0 |  |  | -0.00366 |  |  | 0.10478 |  | 1 | ENERGY
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 42.07 |  |  | -0.00366 |  |  | 0.10478 |  | 1 | CAPACITY
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00367 |  |  | 0 |  | 1 | NEWENERGY | AC1-145
926645 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.00367 |  |  | 0 |  | 1 | CAPACITY | AC1-145
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.9 | 40.06 |  |  | -0.00368 |  |  | 0.07484 |  | 1 | CAPACITY
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 1044 |  |  |  | -0.0037
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 154.95 |  |  | -0.0037 |  |  | 0.0316 |  | 1 | CAPACITY
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 152.54 |  |  | -0.0037 |  |  | 0.0316 |  | 1 | CAPACITY
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 97.14 |  |  | -0.0037 |  |  | 0.0316 |  | 1 | CAPACITY
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 59.41 |  |  | -0.0037 |  |  | 0.0316 |  | 1 | CAPACITY
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 57 |  |  | -0.0037 |  |  | 0.0316 |  | 1 | CAPACITY
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 3.21 |  |  | -0.00371 |  |  | 0 |  | 1 | CAPACITY
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 144.51 |  |  | -0.00375 |  |  | 0.10478 |  | 1 | CAPACITY
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00374 |  |  | 0 |  | 1 | NEWENERGY | AC1-117
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | -0.00375 |  |  | 0.05 |  | 1 | MTX | AA1-100
926461 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00374 |  |  | 0 |  | 1 | NEW | AC1-117
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 6.42 |  |  | -0.00375 |  |  | 0 |  | 1 | CAPACITY
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | AD1-018
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEW | AD1-018
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00379 |  |  | 0 |  | 1 | CAPACITY | N47
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | U2-073 A
235520 | 01WVACO_S38 | 13.8 | 201 | 2 | 0 | 60 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEW
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 0 |  |  | -0.0038 |  |  | 0 |  | 1 | NEWENERGY | U2-073 B
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00379 |  |  | 0.07484 |  | 1 | CAPACITY
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00379 |  |  | 0.07484 |  | 1 | CAPACITY
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 25.9 | 20.79 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY | U2-073 A
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY | U2-073 B
270148 | AE1-018 E | 138 | 205 | 75 | 0 | 2.2 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY | AE1-018
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 3.29 |  |  | -0.0038 |  |  | 0 |  | 1 | CAPACITY
270147 | AE1-018 C | 138 | 205 | 75 | 0 | 2.8 | 2.25 |  |  | -0.00381 |  |  | 0 |  | 1 | CAPACITY | AE1-018
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 0 |  |  | -0.00381 |  |  | 0 |  | 1 | NEWENERGY | S14
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 11.24 |  |  | -0.00381 |  |  | 0 |  | 1 | CAPACITY | S14
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 0 |  |  | -0.00383 |  |  | 0 |  | 1 | NEWENERGY | Y1-006
913034 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 0 |  |  | -0.00383 |  |  | 0 |  | 1 | NEW | Y1-006
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | -0.00383 |  |  | 0.07484 |  | 1 | ENERGY
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00383 |  |  | 0 |  | 1 | MTX | AD2-205
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 14.1 | 11.32 |  |  | -0.00383 |  |  | 0.07484 |  | 1 | CAPACITY
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.7 | 7.79 |  |  | -0.00383 |  |  | 0 |  | 1 | CAPACITY
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 0 |  |  | -0.00383 |  |  | 0 |  | 1 | NEWENERGY | U2-030
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 6.26 |  |  | -0.00383 |  |  | 0 |  | 1 | CAPACITY | U2-030
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00386 |  |  | 0.08446 |  | 1 | CAPACITY
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00386 |  |  | 0.08446 |  | 1 | CAPACITY
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00386 |  |  | 0.08446 |  | 1 | CAPACITY
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00386 |  |  | 0.08446 |  | 1 | CAPACITY
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00386 |  |  | 0.08446 |  | 1 | CAPACITY
242677 | 05INDDRV | 138 | 205 | 64 | 0 | 45 | 36.13 |  |  | -0.00386 |  |  | 0.12623 |  | 1 | CAPACITY
923761 | AB2-010 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEW | AB2-010
923772 | AB2-011 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AB2-011
923771 | AB2-011 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEW | AB2-011
923762 | AB2-010 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | AB2-010
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  |  |  | -0.0039
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 489.98 |  |  | -0.00388 |  |  | 0.10478 |  | 1 | CAPACITY
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 127.4 | 102.28 |  |  | -0.00388 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 101.08 |  |  | -0.00388 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 106.7 | 85.67 |  |  | -0.00388 |  |  | 0 |  | 1 | CAPACITY
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 84.78 |  |  | -0.00388 |  |  | 0 |  | 1 | CAPACITY
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  |  |  | -0.0039
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 38 |  |  |  | -0.0039
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 0 |  |  | -0.00391 |  |  | 0 |  | 1 | NEWENERGY | K28
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 0 |  |  | -0.00391 |  |  | 0 |  | 1 | NEWENERGY | K28
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.4 | 13.97 |  |  | -0.00391 |  |  | 0 |  | 1 | CAPACITY | K28
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 1.3 | 1.04 |  |  | -0.0039 |  |  | 0 |  | 1 | CAPACITY
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 896 |  |  |  | -0.0039
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 180.64 |  |  | -0.00393 |  |  | 0.10478 |  | 1 | CAPACITY
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 93.13 |  |  | -0.00393 |  |  | 0.10478 |  | 1 | CAPACITY
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 64.23 |  |  | -0.00392 |  |  | 0.07484 |  | 1 | CAPACITY
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 56.2 |  |  | -0.00393 |  |  | 0.07484 |  | 1 | CAPACITY
342070 | 2PINE GROVE | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00393 |  |  | 0 |  | 1 | CAPACITY
342442 | 2W GLASGOW | 69 | 320 | 2 | 0 | 1 | 0.8 |  |  | -0.00392 |  |  | 0 |  | 1 | CAPACITY
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 0 |  |  | -0.00394 |  |  | 0 |  | 1 | NEWENERGY | M24
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 0 |  |  | -0.00394 |  |  | 0 |  | 1 | NEWENERGY | AB1-150
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | -0.00394 |  |  | 0.05 |  | 1 | MTX | M24 BAT
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00394 |  |  | 0 |  | 1 | CAPACITY | M24
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00393 |  |  | 0.07484 |  | 1 | CAPACITY
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00394 |  |  | 0.07484 |  | 1 | CAPACITY
931011 | AB1-150 C | 138 | 201 | 74 | 0 | 6.7 | 5.38 |  |  | -0.00394 |  |  | 0 |  | 1 | CAPACITY | AB1-150
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00393 |  |  | 0 |  | 1 | CAPACITY
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.55 |  |  | -0.00395 |  |  | 0 |  | 1 | CAPACITY
918472 | AA1-062 E | 138 | 201 | 74 | 0 | 195 | 0 |  |  | -0.00396 |  |  | 0 |  | 1 | NEWENERGY | AA1-062
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 244.87 |  |  | -0.00395 |  |  | 0.10478 |  | 1 | CAPACITY
247225 | 05FTHLG2 | 18 | 205 | 57 | 120 | 173.8 | 139.54 |  |  | -0.00395 |  |  | 0.08446 |  | 1 | CAPACITY
247224 | 05FTHLG1 | 18 | 205 | 57 | 120 | 173.7 | 139.46 |  |  | -0.00395 |  |  | 0.08446 |  | 1 | CAPACITY
247232 | 05RIVRG3 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00395 |  |  | 0.08446 |  | 1 | CAPACITY
247231 | 05RIVRG2 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00395 |  |  | 0.08446 |  | 1 | CAPACITY
247230 | 05RIVRG1 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00395 |  |  | 0.08446 |  | 1 | CAPACITY
292981 | N-007 E | 138 | 201 | 74 | 0 | 30.4 | 0 |  |  | -0.00396 |  |  | 0 |  | 1 | NEWENERGY | N07
235801 | 01WM_AA1_062 | 138 | 201 | 74 | 0 | 29 | 0 |  |  | -0.00396 |  |  | 0 |  | 1 | NEW | AA1-062
920072 | AA2-103 E | 138 | 201 | 76 | -20 | 20 | 0 |  |  | -0.00396 |  |  | 0.05 |  | 1 | MTX | AA2-103
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 60.94 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 60.78 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 60.7 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 60.53 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 11.88 |  |  | -0.00396 |  |  | 0.07484 |  | 1 | CAPACITY
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | -0.00396 |  |  | 0 |  | 1 | MTX | AB1-055
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00396 |  |  | 0 |  | 1 | CAPACITY | K19
235000 | N-007 C | 138 | 201 | 74 | 0 | 7.6 | 6.1 |  |  | -0.00396 |  |  | 0 |  | 1 | CAPACITY | N07
341329 | 2COLESBURG | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00396 |  |  | 0 |  | 1 | CAPACITY
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1067.8 |  |  | -0.00396 |  |  | 0.10478 |  | 1 | CAPACITY | AMG3
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  |  |  | -0.004
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 642.29 |  |  | -0.00396 |  |  | 0.10478 |  | 1 | CAPACITY
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 642.29 |  |  | -0.00396 |  |  | 0.10478 |  | 1 | CAPACITY
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 0 |  |  | -0.00396 |  |  | 0 |  | 1 | NEWENERGY | P59
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00396 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00396 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 0 |  |  | -0.00396 |  |  | 0 |  | 1 | NEWENERGY | U2-061
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00396 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00396 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00396 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 2
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00396 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 109.5 | 87.91 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 72.9 | 58.53 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 72.6 | 58.29 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | -0.004
925972 | AC1-073 E | 138 | 201 | 74 | 0 | 5.9 | 0 |  |  | -0.00396 |  |  | 0 |  | 1 | NEWENERGY | AC1-073
925971 | AC1-073 C | 138 | 201 | 74 | 0 | 5.8 | 0 |  |  | -0.00396 |  |  | 0 |  | 1 | NEW | AC1-073
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 9.39 |  |  | -0.00396 |  |  | 0 |  | 1 | CAPACITY | P59
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 5.22 |  |  | -0.00396 |  |  | 0 |  | 1 | CAPACITY | U2-061
342031 | 2PACTOLUS | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00397 |  |  | 0 |  | 1 | CAPACITY
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00398 |  |  | 0.10478 |  | 1 | CAPACITY
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00398 |  |  | 0.10478 |  | 1 | CAPACITY
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 62.8 |  |  |  | -0.004
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 106.94 |  |  | -0.00398 |  |  | 0.07484 |  | 1 | CAPACITY
208904 | HOLT 696 | 13.2 | 229 | 60 | 23 | 58.4 | 46.89 |  |  | -0.00398 |  |  | 0.07484 |  | 1 | CAPACITY
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 55 | 44.16 |  |  | -0.00397 |  |  | 0.10478 |  | 1 | CAPACITY
208903 | HOLT 695 | 13.2 | 229 | 60 | 26 | 53.2 | 42.71 |  |  | -0.00398 |  |  | 0.07484 |  | 1 | CAPACITY
919535 | V4-027 E | 0 | 229 | 75 | 0 | 3.1 | 0 |  |  | -0.00398 |  |  | 0 |  | 1 | NEWENERGY | V4-027
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 3.93 |  |  | -0.00398 |  |  | 0 |  | 1 | CAPACITY | V4-027
208474 | KINZ 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00398 |  |  | 0 |  | 1 | CAPACITY
341200 | 2BROMLEYEK | 69 | 320 | 2 | 0 | 2 | 1.61 |  |  | -0.00397 |  |  | 0 |  | 1 | CAPACITY
237085 | AD2-192 GEN | 23 | 201 | 57 | 0 | 600 | 0 |  |  | -0.00398 |  |  | 0.08446 |  | 1 | NEW
293798 | W4-005 E | 0.69 | 222 | 74 | 0 | 305.37 | 0 |  |  | -0.00398 |  |  | 0 |  | 1 | NEWENERGY | W4-005
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1396 | 1120.79 |  |  | -0.00398 |  |  | 0.10478 |  | 1 | CAPACITY | GVG2
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1371 | 1100.72 |  |  | -0.00398 |  |  | 0.10478 |  | 1 | CAPACITY | GVG1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1088.67 |  |  | -0.00398 |  |  | 0.10478 |  | 1 | CAPACITY | RKG1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1356 | 1088.67 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY | MTG1
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1043.71 |  |  | -0.00398 |  |  | 0.10478 |  | 1 | CAPACITY | RKG2
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 0 |  |  | -0.00398 |  |  | 0 |  | 1 | NEWENERGY | X2-022
274663 | QUAD CITI;2U | 18 | 222 | 48 | 150 | 911.7 | 731.97 |  |  | -0.00398 |  |  | 0.01494 |  | 1 | CAPACITY
274662 | QUAD CITI;1U | 18 | 222 | 48 | 150 | 911.1 | 731.48 |  |  | -0.00398 |  |  | 0.01494 |  | 1 | CAPACITY
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | S28
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | S27
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 124 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | ENERGY | L05_CE22
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | P36 2
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | P36 1
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | O29 1
293516 | O-009 E1 | 0.69 | 222 | 74 | 0 | 82.04 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | O09 1
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | P11 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | P11 2
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 0 |  |  | -0.00398 |  |  | 0 |  | 1 | NEWENERGY | W2-048
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 240.86 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | O29 2
293518 | O-009 E3 | 0.57 | 222 | 74 | 0 | 45.89 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | O09 3
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | O29 3
293517 | O-009 E2 | 0.6 | 222 | 74 | 0 | 41.67 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | O09 2
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 144.51 |  |  | -0.00398 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 136.16 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | NELSON
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 135.12 |  |  | -0.00399 |  |  | 0.04435 |  | 1 | CAPACITY | NELSON
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 134.32 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 134.16 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00398 |  |  | 0.04435 |  | 1 | CAPACITY | CORDOVA
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00398 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
919221 | AA1-146 | 345 | 222 | 58 | 0 | 157 | 126.05 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | CLIF4
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF2
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | CLIF1
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | CLIF5
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | CLIF6
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | CLIF3
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 99.47 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | NELSON
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 98.59 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | NELSON
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | NQ72
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 67.52 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF4
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF5
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | CLIF2
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF1
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF6
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF3
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 52.91 |  |  | -0.00398 |  |  | 0.07484 |  | 1 | CAPACITY
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 36.93 |  |  | -0.00399 |  |  | 0.07484 |  | 1 | CAPACITY
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 36.61 |  |  | -0.00398 |  |  | 0 |  | 1 | CAPACITY | W4-005
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 28.74 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | S28
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 27.94 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | S27
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | L05_CE22
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | O29 1
293513 | O-009 C1 | 0.69 | 222 | 74 | 0 | 20.5 | 16.46 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | O09 1
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | P11 2
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | P11 1
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | P36 2
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | P36 1
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 9.64 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | O29 2
293515 | O-009 C3 | 0.57 | 222 | 74 | 0 | 11.5 | 9.23 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | O09 3
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 8.91 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | O29 3
293514 | O-009 C2 | 0.6 | 222 | 74 | 0 | 10.4 | 8.35 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | O09 2
342550 | 4BAVARIAN LF | 138 | 320 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY
341584 | 2GRIFFIN | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00398 |  |  | 0 |  | 1 | CAPACITY
295110 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 2.57 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | NQ72
274656 | BYRON ;1U | 25 | 222 | 45 | 700 | 1168.5 | 938.14 |  |  | -0.00399 |  |  | 0.01494 |  | 1 | CAPACITY
274657 | BYRON ;2U | 25 | 222 | 45 | 700 | 1141.5 | 916.46 |  |  | -0.00399 |  |  | 0.01494 |  | 1 | CAPACITY
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 200 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | Q57
274658 | DRESDEN ;2U | 18 | 222 | 48 | 150 | 902.5 | 724.58 |  |  | -0.004 |  |  | 0.01494 |  | 1 | CAPACITY
274659 | DRESDEN ;3U | 18 | 222 | 48 | 150 | 895.5 | 718.96 |  |  | -0.004 |  |  | 0.01494 |  | 1 | CAPACITY
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | Z2-087
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | O50
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | O22 2
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | P10
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 589.3 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY | ZIMM
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 570.03 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | AA1-018
235587 | 01HARRN3 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY
235586 | 01HARRN2 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY
235585 | 01HARRN1 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | O51 2
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | O51 1
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | N15
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 470.47 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | ZIMM
927091 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.004 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-204
927093 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | AC1-204
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 415.88 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 415.88 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 409.46 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY
274687 | WILL CNTY;4U | 20 | 222 | 15 | 0 | 510 | 409.46 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY | WILL4
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | AC1-089
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | P26
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 81.6 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | O22 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | P46
930062 | AB1-014 E | 138 | 212 | 75 | 0 | 77.5 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | AB1-014
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 522.66 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 284.53 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK8
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 263.34 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK7
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.004 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-169
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | O35
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 225.6 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.00399 |  |  | 0.10478 |  | 1 | CAPACITY
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | NQ71
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 45.5 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | Z1-073
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | AB1-169
916211 | Z1-072 E | 0.6 | 222 | 74 | 0 | 44.8 | 0 |  |  | -0.00399 |  |  | 0 |  | 1 | NEWENERGY | Z1-072
274708 | KENDALL ;3C | 18 | 222 | 58 | 140 | 184.3 | 147.97 |  |  | -0.004 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 3
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 146.36 |  |  | -0.004 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 2
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 146.36 |  |  | -0.004 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 138 | 182.3 | 146.36 |  |  | -0.004 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 4
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.004 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 2
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.004 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 1
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 132.47 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 31.5 |  |  |  | -0.004
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | -0.004 |  |  | 0.08446 |  | 1 | ENERGY
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 99.72 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY | KYG1
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY | KYG3
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY | KYG5
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | KYG4
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | KYG2
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 97.87 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Kendall 2
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 97.87 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Kendall 1
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 97.87 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Kendall 3
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 97.87 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Kendall 4
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 96.42 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 115.4 | 92.65 |  |  | -0.004 |  |  | 0.04435 |  | 1 | CAPACITY | EQUISTAR MORRIS
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | AC1-048
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 75.6 | 104 | 83.5 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 72.7 | 101.6 | 81.57 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00399 |  |  | 0.05 |  | 1 | MTX | AA2-123
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.004 |  |  | 0.05 |  | 1 | MTX | Z1-108
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.004 |  |  | 0.05 |  | 1 | MTX | Z1-107
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 80.93 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 71.2 | 100.6 | 80.77 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 133.1 | 153 | 133.28 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 129.7 | 149.1 | 129.88 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 128.6 | 147.8 | 128.75 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 81.5 | 65.43 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS
250166 | HLCRST AB114 | 138 | 212 | 75 | 0 | 76 | 61.02 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | AB1-014
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 58.77 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 58.45 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | KYG1
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | KYG3
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | KYG5
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY | KYG2
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY | KYG4
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 55.4 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEW | AC1-048
205910 | AC2-053 E | 0.39 | 227 | 74 | 0 | 12.4 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | AC2-053
251828 | CLNTESP1 | 34.5 | 212 | 76 | 0 | 12 | 0 |  |  | -0.004 |  |  | 0.05 |  | 1 | MTX | Z1-080
926103 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 45.76 |  |  | -0.00399 |  |  | 0.05 |  | 1 | NEW | AC1-089
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.004 |  |  | 0.05 |  | 1 | MTX | Z1-106
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.004 |  |  | 0.05 |  | 1 | MTX | Z1-106
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 40.54 |  |  | -0.004 |  |  | 0.04435 |  | 1 | CAPACITY | MIDDLETOWN COKE
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | Q57
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | O50
205909 | AC2-053 C | 0.39 | 227 | 74 | 0 | 7.6 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEW | AC2-053
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00399 |  |  | 0.07484 |  | 1 | CAPACITY
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00399 |  |  | 0.07484 |  | 1 | CAPACITY
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00399 |  |  | 0.07484 |  | 1 | CAPACITY
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 28.18 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | O22 2
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -0.004 |  |  | 0.05 |  | 1 | MTX | Z1-065
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 24.08 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 20.3 | 27.6 | 22.16 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 22 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | N15
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 21.68 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274889 | BRIGHTSTK;1U | 0.7 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | Z2-087
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 20.07 |  |  | -0.00399 |  |  | 0.08446 |  | 1 | CAPACITY
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | O51 1
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | O51 2
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 17.58 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | P26
274891 | OTTER CRK;1U | 0.69 | 222 | 74 | 0 | 19.5 | 15.66 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | AA1-018
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 15.58 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | P46
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 14.77 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | O22 1
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | Z1-073
276173 | Z2-081 | 138 | 222 | 2 | 0 | 13.3 | 10.68 |  |  | -0.004 |  |  | 0.12623 |  | 1 | CAPACITY
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 10.36 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
904211 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 9.71 |  |  | -0.004 |  |  | 0.07484 |  | 1 | CAPACITY
904201 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 8.51 |  |  | -0.004 |  |  | 0.07484 |  | 1 | CAPACITY
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 10.3 | 8.27 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | O35
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 8.19 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | P10
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | MTX | Y3-099
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | MTX | Y3-100
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 10 | 8.03 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | Z1-072
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.6 | 7.71 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY
295108 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 5.7 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY | NQ71
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00399 |  |  | 0 |  | 1 | CAPACITY
276159 | W4-082 | 138 | 222 | 64 | 0 | 5.8 | 4.66 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.8 | 3.85 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 949.78 |  |  | -0.004 |  |  | 0.01494 |  | 1 | CAPACITY
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 926.5 |  |  | -0.004 |  |  | 0.01494 |  | 1 | CAPACITY
274661 | LASCO STA;2U | 25 | 222 | 49 | 150 | 1135.9 | 911.97 |  |  | -0.004 |  |  | 0.01494 |  | 1 | CAPACITY
274660 | LASCO STA;1U | 25 | 222 | 49 | 150 | 1131.2 | 908.19 |  |  | -0.004 |  |  | 0.01494 |  | 1 | CAPACITY
930042 | AB1-006 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | AB1-006
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | U3-002 2
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00401 |  |  | 0 |  | 1 | NEWENERGY | V3-007
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00401 |  |  | 0 |  | 1 | NEWENERGY | U2-090
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 159.7 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | S06
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | Q01 3
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | S37
293799 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | S36
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | Q01 4
253317 | AC1-085 B_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 B
253314 | AC1-085 A_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 A
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 443.18 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 437.96 |  |  | -0.004 |  |  | 0.10478 |  | 1 | CAPACITY
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | Q01 21
247943 | T-127 E | 0.74 | 205 | 74 | 0 | 80 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | T127 5
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 80 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | T126 2
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 80 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | T126 3
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 80 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | T127 4
247903 | 05FR-22G E | 0.69 | 205 | 75 | 0 | 78.8 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | Q01 22
247900 | 05FR-11G E | 0.6 | 205 | 75 | 0 | 78.3 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | Q01 11
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | Q01 12
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 294 | 236.04 |  |  | -0.004 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-079
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 219 | 175.82 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Z1-079
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 131.75 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 130.06 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
276592 | O-012 C | 138 | 222 | 64 | 0 | 20 | 0 |  |  | -0.004 |  |  | 0.12623 |  | 1 | ENERGY
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 80.21 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
243415 | 05WWVSTA | 69 | 205 | 61 | 60 | 96 | 77.08 |  |  | -0.004 |  |  | 0.07484 |  | 1 | CAPACITY
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 65.51 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.8 | 64.87 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 64.31 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 62.14 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | AC1-085 B
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | AC1-085 A
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00401 |  |  | 0.08446 |  | 1 | CAPACITY
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00401 |  |  | 0.08446 |  | 1 | CAPACITY
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00401 |  |  | 0.08446 |  | 1 | CAPACITY
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00401 |  |  | 0.08446 |  | 1 | CAPACITY
251953 | 08MADSN2 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
251958 | 08MADSN7 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
251956 | 08MADSN5 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
251954 | 08MADSN3 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
251959 | 08MADSN8 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
251955 | 08MADSN4 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
251957 | 08MADSN6 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
251952 | 08MADSN1 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 56.84 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 43.03 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 37.49 |  |  | -0.00401 |  |  | 0.07484 |  | 1 | CAPACITY
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | S37
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | S36
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 42.68 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 42.6 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 42.51 |  |  | -0.004 |  |  | 0.08446 |  | 1 | CAPACITY
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 23.36 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Q01 4
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | X3-005
930041 | AB1-006 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | AB1-006
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00401 |  |  | 0 |  | 1 | CAPACITY | V3-007
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00401 |  |  | 0 |  | 1 | CAPACITY | U2-090
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 20.79 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | S06
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 20.63 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Q01 11
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 16.22 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | T127 5
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 12.28 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | T126 3
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 12.2 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | T126 2
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 10.6 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | U3-002 1
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Q01 22
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Q01 21
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 10.28 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | U3-002 2
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Q01 12
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | Q01 3
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 9.47 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | T127 4
247968 | Z2-115 E | 12 | 205 | 74 | 0 | 1.25 | 0 |  |  | -0.00401 |  |  | 0 |  | 1 | NEWENERGY | Z2-115
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 2.73 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY | X3-005
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 1 |  |  | -0.00401 |  |  | 0 |  | 1 | CAPACITY | Z2-115
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1402 |  |  |  | -0.004
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1148 | 921.68 |  |  | -0.00402 |  |  | 0.01494 |  | 1 | CAPACITY
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 0 |  |  | -0.00401 |  |  | 0 |  | 1 | NEWENERGY | AC2-176
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 0 |  |  | -0.00401 |  |  | 0 |  | 1 | NEWENERGY | S71
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 268.96 |  |  | -0.00402 |  |  | 0.08446 |  | 1 | CAPACITY
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 201.52 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY | X2-052
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 193.49 |  |  | -0.00402 |  |  | 0.08446 |  | 1 | CAPACITY
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY | X2-052
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00402 |  |  | 0.04435 |  | 1 | CAPACITY | X2-052
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 0 |  |  | -0.00402 |  |  | 0 |  | 1 | NEWENERGY | AC2-067
902531 | W2-040 C | 69 | 209 | 75 | 0 | 20 | 0 |  |  | -0.00401 |  |  | 0 |  | 1 | NEW | W2-040
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 80.69 |  |  | -0.00401 |  |  | 0.08446 |  | 1 | CAPACITY
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 64.23 |  |  | -0.00401 |  |  | 0.10478 |  | 1 | CAPACITY
902532 | W2-040 E | 69 | 209 | 75 | 0 | 12.4 | 0 |  |  | -0.00401 |  |  | 0 |  | 1 | NEWENERGY | W2-040
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 48.09 |  |  | -0.00401 |  |  | 0.08446 |  | 1 | CAPACITY
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 47.93 |  |  | -0.00401 |  |  | 0.08446 |  | 1 | CAPACITY
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 46.65 |  |  | -0.00401 |  |  | 0.08446 |  | 1 | CAPACITY
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 46.41 |  |  | -0.00401 |  |  | 0.08446 |  | 1 | CAPACITY
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 21.28 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY | AC2-067
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 19.27 |  |  | -0.00401 |  |  | 0 |  | 1 | CAPACITY | S71
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 22.91 |  |  | -0.00401 |  |  | 0.08446 |  | 1 | CAPACITY
933594 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 13.57 |  |  | -0.00401 |  |  | 0 |  | 1 | CAPACITY | AC2-176
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00402 |  |  | 0.12623 |  | 1 | CAPACITY
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 8.03 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0 |  |  | -0.00401 |  |  | 0 |  | 1 | NEWENERGY | V4-073
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.76 |  |  | -0.00401 |  |  | 0 |  | 1 | CAPACITY
904721 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00401 |  |  | 0 |  | 1 | CAPACITY | V4-073
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 814.5 |  |  | -0.00402 |  |  | 0.01494 |  | 1 | CAPACITY
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY | AA2-116
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00402 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-116
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 267.35 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY | AA2-116
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 162.9 |  |  | -0.00402 |  |  | 0.08446 |  | 1 | CAPACITY
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00402 |  |  | 0 |  | 1 | NEWENERGY | AC1-165
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00402 |  |  | 0 |  | 1 | NEWENERGY | AC1-166
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00403 |  |  | 0.08446 |  | 1 | CAPACITY
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00403 |  |  | 0.08446 |  | 1 | CAPACITY
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00403 |  |  | 0.08446 |  | 1 | CAPACITY
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 65.03 |  |  | -0.00403 |  |  | 0.08446 |  | 1 | CAPACITY
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00402 |  |  | 0 |  | 1 | NEWENERGY | AC1-068
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00402 |  |  | 0 |  | 1 | NEWENERGY | AC1-069
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 64.23 |  |  | -0.00403 |  |  | 0.08446 |  | 1 | CAPACITY
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 63.43 |  |  | -0.00403 |  |  | 0.08446 |  | 1 | CAPACITY
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY | AC1-069
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY | AC1-068
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY | AC1-166
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY | AC1-165
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0 |  |  | -0.00403 |  |  | 0 |  | 1 | NEWENERGY | Z2-113
247969 | Z2-116 E | 138 | 205 | 76 | 0 | 1.3 | 0 |  |  | -0.00402 |  |  | 0 |  | 1 | NEWENERGY | Z2-116
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 4.82 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 3.13 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY
247604 | X1-042 | 12 | 205 | 64 | 0 | 3 | 2.41 |  |  | -0.00403 |  |  | 0 |  | 1 | CAPACITY
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.8 | 2.25 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 2.09 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 1.85 |  |  | -0.00403 |  |  | 0 |  | 1 | CAPACITY | Z2-113
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.5 | 1.2 |  |  | -0.00403 |  |  | 0 |  | 1 | CAPACITY
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00402 |  |  | 0 |  | 1 | CAPACITY | Z2-116
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 120.8 | 0 |  |  | -0.00404 |  |  | 0 |  | 1 | NEWENERGY | R49
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 0 |  |  | -0.00404 |  |  | 0 |  | 1 | NEWENERGY | T131
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 0 |  |  | -0.00404 |  |  | 0 |  | 1 | NEWENERGY | AC1-173
247528 | 05COVRT1 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00404 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 1
247529 | 05COVRT2 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00404 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 2
247530 | 05COVRT3 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00404 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 3
247531 | 05COVRT4 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00404 |  |  | 0 |  | 1 | CAPACITY | Covert 1
247533 | 05COVRT6 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00404 |  |  | 0 |  | 1 | CAPACITY | Covert 3
247532 | 05COVRT5 | 16.5 | 205 | 58 | 90 | 131.2 | 105.33 |  |  | -0.00404 |  |  | 0 |  | 1 | CAPACITY | Covert 2
927184 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -0.00403 |  |  | 0.05 |  | 1 | MTX | AC1-212
932312 | AC2-045 E | 69 | 205 | 75 | 0 | 6.2 | 0 |  |  | -0.00403 |  |  | 0 |  | 1 | NEWENERGY | AC2-045
247521 | T131 | 0.69 | 205 | 74 | 22.4 | 30 | 24.08 |  |  | -0.00404 |  |  | 0 |  | 1 | CAPACITY | T131
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 18.39 |  |  | -0.00404 |  |  | 0 |  | 1 | CAPACITY | R49
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00404 |  |  | 0.07484 |  | 1 | CAPACITY
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00404 |  |  | 0.07484 |  | 1 | CAPACITY
932311 | AC2-045 C | 69 | 205 | 75 | 0 | 3.8 | 0 |  |  | -0.00403 |  |  | 0 |  | 1 | NEW | AC2-045
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00403 |  |  | 0.12623 |  | 1 | CAPACITY
926865 | AC1-173 C | 0.65 | 205 | 75 | 0 | 9.9 | 7.95 |  |  | -0.00404 |  |  | 0 |  | 1 | CAPACITY | AC1-173
AC1-212 | BATTERY_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | -0.004
927183 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.53 |  |  | -0.00403 |  |  | 0 |  | 1 | CAPACITY | AC1-212
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 94.4 | 0 |  |  | -0.00405 |  |  | 0 |  | 1 | NEWENERGY | R60 3
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00405 |  |  | 0 |  | 1 | NEWENERGY | R60 2
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00405 |  |  | 0 |  | 1 | NEWENERGY | R60 1
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00405 |  |  | 0 |  | 1 | NEWENERGY | V1-011
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00404 |  |  | 0.08446 |  | 1 | CAPACITY
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00404 |  |  | 0.08446 |  | 1 | CAPACITY
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00404 |  |  | 0.08446 |  | 1 | CAPACITY
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00404 |  |  | 0.08446 |  | 1 | CAPACITY
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 120.19 |  |  | -0.00404 |  |  | 0.08446 |  | 1 | CAPACITY
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 13.25 |  |  | -0.00405 |  |  | 0 |  | 1 | CAPACITY | R60 3
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00405 |  |  | 0 |  | 1 | CAPACITY | R60 2
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00405 |  |  | 0 |  | 1 | CAPACITY | R60 1
247607 | V1-011 C | 34.5 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00405 |  |  | 0 |  | 1 | CAPACITY | V1-011
294740 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -0.00404 |  |  | 0 |  | 1 | ENERGY
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00406 |  |  | 0 |  | 1 | NEWENERGY | U2-072
247919 | U2-041 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00406 |  |  | 0 |  | 1 | NEWENERGY | U2-041
247506 | U2-041 C | 345 | 205 | 74 | 0 | 39 | 0 |  |  | -0.00406 |  |  | 0 |  | 1 | CAPACITY | U2-041
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00406 |  |  | 0 |  | 1 | NEWENERGY | V3-028
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 31.31 |  |  | -0.00406 |  |  | 0 |  | 1 | CAPACITY | U2-072
247549 | V3-028 C | 345 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00406 |  |  | 0 |  | 1 | CAPACITY | V3-028
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00405 |  |  | 0 |  | 1 | MTX
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00406 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-067
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00406 |  |  | 0 |  | 1 | CAPACITY | AB2-067
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00406 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-044
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 292.88 |  |  | -0.00406 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00406 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00406 |  |  | 0.04435 |  | 1 | CAPACITY | WATERFORD
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00406 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 618.28 |  |  | -0.00408 |  |  | 0.10478 |  | 1 | CAPACITY
893022 | V2-006 E | 138 | 205 | 74 | 0 | 130.5 | 0 |  |  | -0.00408 |  |  | 0 |  | 1 | NEWENERGY | V2-006
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 238.45 |  |  | -0.00407 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00407 |  |  | 0.04435 |  | 1 | CAPACITY | WASHINGTON
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00407 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
893021 | V2-006 C | 138 | 205 | 74 | 0 | 19.5 | 0 |  |  | -0.00408 |  |  | 0 |  | 1 | NEWENERGY | V2-006
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00407 |  |  | 0 |  | 1 | CAPACITY
245413 | 05S FULTHA | 69 | 205 | 65 | 0 | 0.85 | 0 |  |  | -0.00408 |  |  | 0 |  | 1 | ENERGY
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 318.8 | 255.95 |  |  | -0.00408 |  |  | 0 |  | 1 | CAPACITY | RONCO
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 225.4 | 180.96 |  |  | -0.00409 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 0 |  |  | -0.00409 |  |  | 0 |  | 1 | NEWENERGY | U1-059
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00408 |  |  | 0.04435 |  | 1 | CAPACITY | RONCO
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00408 |  |  | 0 |  | 1 | CAPACITY | RONCO
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.00409 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.00409 |  |  | 0.04435 |  | 1 | CAPACITY | DRESDEN
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 0 |  |  | -0.00409 |  |  | 0 |  | 1 | NEWENERGY | W1-056
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 64.31 |  |  | -0.00408 |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 52.35 |  |  | -0.00408 |  |  | 0.04435 |  | 1 | CAPACITY | CAMDEN COGEN TECH
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 0 |  |  | -0.00409 |  |  | 0 |  | 1 | NEWENERGY | U1-059
930262 | AB1-065 E | 34.5 | 201 | 75 | 0 | 6.8 | 0 |  |  | -0.00409 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
925391 | AC1-010 C | 26.4 | 231 | 75 | 0 | 6 | 0 |  |  | -0.00408 |  |  | 0 |  | 1 | NEW | AC1-010
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 19.27 |  |  | -0.00408 |  |  | 0.10478 |  | 1 | CAPACITY
235013 | 01AB1-065 C | 34.5 | 201 | 75 | 0 | 4.1 | 0 |  |  | -0.00409 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -0.00408 |  |  | 0 |  | 1 | NEWENERGY | AC1-010
219765 | PARADISE E | 26.4 | 231 | 75 | 0 | 3.2 | 0 |  |  | -0.00408 |  |  | 0 |  | 1 | NEWENERGY | U4-036
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.3 | 9.07 |  |  | -0.00408 |  |  | 0.10478 |  | 1 | CAPACITY
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | -0.00408 |  |  | 0 |  | 1 | MTX | X2-013
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.93 |  |  | -0.00409 |  |  | 0 |  | 1 | CAPACITY | W1-056
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00408 |  |  | 0 |  | 1 | CAPACITY | U4-036
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 533.66 |  |  | -0.00409 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-173
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.00409 |  |  | 0.08446 |  | 1 | CAPACITY
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.00409 |  |  | 0.08446 |  | 1 | CAPACITY
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.66 | 96.07 |  |  | -0.00409 |  |  | 0.08446 |  | 1 | CAPACITY
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 17.66 |  |  | -0.00409 |  |  | 0.08446 |  | 1 | CAPACITY
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 8.83 |  |  | -0.00409 |  |  | 0.10478 |  | 1 | CAPACITY
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 10.19 |  |  | -0.00412 |  |  | 0.10478 |  | 1 | CAPACITY
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00413 |  |  | 0.07484 |  | 1 | CAPACITY
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00413 |  |  | 0.07484 |  | 1 | CAPACITY
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 15.25 |  |  | -0.00413 |  |  | 0.07484 |  | 1 | CAPACITY
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 634.42 |  |  | -0.00414 |  |  | 0.10478 |  | 1 | CAPACITY
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00414 |  |  | 0 |  | 1 | NEWENERGY | U4-029
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00414 |  |  | 0 |  | 1 | NEWENERGY | U4-028
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 0 |  |  | -0.00414 |  |  | 0 |  | 1 | NEWENERGY
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00414 |  |  | 0 |  | 1 | NEW | U4-028
247552 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00414 |  |  | 0 |  | 1 | NEW | U4-029
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00414 |  |  | 0 |  | 1 | NEWENERGY | V4-010
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 261.89 |  |  | -0.00414 |  |  | 0 |  | 1 | CAPACITY | OREGON
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 248.73 |  |  | -0.00414 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00414 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00414 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-107
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00414 |  |  | 0 |  | 1 | CAPACITY | OREGON
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00414 |  |  | 0.04435 |  | 1 | CAPACITY | OREGON
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00414 |  |  | 0.08446 |  | 1 | CAPACITY
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00414 |  |  | 0.10478 |  | 1 | CAPACITY
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00414 |  |  | 0.10478 |  | 1 | CAPACITY
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00414 |  |  | 0.08446 |  | 1 | CAPACITY
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 109.19 |  |  | -0.00415 |  |  | 0.10478 |  | 1 | CAPACITY
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 0 |  |  | -0.00414 |  |  | 0 |  | 1 | NEW | V4-010
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00414 |  |  | 0.08446 |  | 1 | CAPACITY
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00414 |  |  | 0.08446 |  | 1 | CAPACITY
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 10.68 |  |  | -0.00415 |  |  | 0.10478 |  | 1 | CAPACITY
924440 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 389.39 |  |  | -0.00416 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-093
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 364.2 | 292.4 |  |  | -0.00417 |  |  | 0 |  | 1 | CAPACITY | FREMONT
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 170 | 136.49 |  |  | -0.00417 |  |  | 0.04435 |  | 1 | CAPACITY | FREMONT
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 166.4 | 133.6 |  |  | -0.00417 |  |  | 0 |  | 1 | CAPACITY | FREMONT
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 780.51 |  |  | -0.00418 |  |  | 0.01494 |  | 1 | CAPACITY
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | -0.00419 |  |  | 0 |  | 1 | NEW | AB1-069
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00419 |  |  | 0 |  | 1 | NEW | AB1-069
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00419 |  |  | 0.04435 |  | 1 | NEW | AB1-069
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 4.41 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY | N32
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 8.03 |  |  | -0.00419 |  |  | 0 |  | 1 | CAPACITY
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 7.95 |  |  | -0.00419 |  |  | 0 |  | 1 | CAPACITY
936011 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 16.06 |  |  | -0.00422 |  |  | 0.10478 |  | 1 | CAPACITY
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 1.85 |  |  | -0.00422 |  |  | 0 |  | 1 | CAPACITY
903052 | W2-094 E | 115 | 227 | 75 | 0 | 1.9 | 0 |  |  | -0.00424 |  |  | 0 |  | 1 | NEWENERGY | W2-094
205911 | 27W2-094 | 115 | 227 | 75 | 0 | 1.1 | 0 |  |  | -0.00424 |  |  | 0 |  | 1 | NEWENERGY | W2-094
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 11.24 |  |  | -0.00425 |  |  | 0.12623 |  | 1 | CAPACITY
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 498.09 |  |  | -0.00427 |  |  | 0.10478 |  | 1 | CAPACITY
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00426 |  |  | 0.10478 |  | 1 | CAPACITY
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00427 |  |  | 0.10478 |  | 1 | CAPACITY
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 272 | 218.38 |  |  | -0.00426 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00426 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00426 |  |  | 0.04435 |  | 1 | CAPACITY | Y2-050
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00426 |  |  | 0.08446 |  | 1 | CAPACITY
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 41.03 |  |  | -0.00426 |  |  | 0.12623 |  | 1 | CAPACITY
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 39.82 |  |  | -0.00426 |  |  | 0.12623 |  | 1 | CAPACITY
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 62.22 |  |  | -0.00427 |  |  | 0.08446 |  | 1 | CAPACITY
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00427 |  |  | 0.08446 |  | 1 | CAPACITY
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 60.86 |  |  | -0.00427 |  |  | 0.08446 |  | 1 | CAPACITY
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 60.29 |  |  | -0.00427 |  |  | 0.08446 |  | 1 | CAPACITY
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 503.47 |  |  | -0.00429 |  |  | 0.04435 |  | 1 | CAPACITY | AVON LAKE
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 91.93 |  |  | -0.00431 |  |  | 0.07484 |  | 1 | CAPACITY
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 61.42 |  |  | -0.00431 |  |  | 0.07484 |  | 1 | CAPACITY
237082 | AA2-121 | 345 | 201 | 58 | 0 | 830 | 666.37 |  |  | -0.00431 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-121
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 21 | 16.86 |  |  | -0.00432 |  |  | 0.12623 |  | 1 | CAPACITY
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 3.21 |  |  | -0.00431 |  |  | 0 |  | 1 | CAPACITY
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 81.57 |  |  | -0.00434 |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND
253970 | 15BI2 | 13.8 | 215 | 58 | 60 | 96.2 | 77.24 |  |  | -0.00434 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.7 | 39.1 |  |  | -0.00434 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0 |  |  | -0.00434 |  |  | 0 |  | 1 | NEWENERGY | AC2-168
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 14.53 |  |  | -0.00434 |  |  | 0.08446 |  | 1 | CAPACITY
933531 | AC2-168 C | 138 | 215 | 75 | 0 | 7.55 | 6.06 |  |  | -0.00434 |  |  | 0 |  | 1 | CAPACITY | AC2-168
253900 | 15BVRVL1 | 22 | 215 | 44 | 843.9 | 970 | 844.97 |  |  | -0.00435 |  |  | 0.01494 |  | 1 | CAPACITY
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00434 |  |  | 0.10478 |  | 1 | CAPACITY
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00434 |  |  | 0.10478 |  | 1 | CAPACITY
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 783.39 |  |  | -0.00435 |  |  | 0.01494 |  | 1 | CAPACITY
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 455.62 |  |  | -0.00434 |  |  | 0.10478 |  | 1 | CAPACITY
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.00434 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.00434 |  |  | 0 |  | 1 | CAPACITY | AA1-123
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 233.87 |  |  | -0.00434 |  |  | 0.10478 |  | 1 | CAPACITY
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.00434 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.00434 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-123
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 77.88 |  |  | -0.00434 |  |  | 0.07484 |  | 1 | CAPACITY
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 51.78 |  |  | -0.00434 |  |  | 0.07484 |  | 1 | CAPACITY
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 51.38 |  |  | -0.00434 |  |  | 0.07484 |  | 1 | CAPACITY
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.00435 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.00435 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00435 |  |  | 0.04435 |  | 1 | CAPACITY | Y3-103
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00435 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00435 |  |  | 0 |  | 1 | CAPACITY | Y3-103
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 300.6 | 241.34 |  |  | -0.00436 |  |  | 0 |  | 1 | CAPACITY | Z2-028
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00436 |  |  | 0 |  | 1 | CAPACITY | Z2-028
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00436 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-028
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | -0.00436 |  |  | 0.10478 |  | 1 | ENERGY
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 24.6 | 19.75 |  |  | -0.00436 |  |  | 0.12623 |  | 1 | CAPACITY
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 19.5 | 15.66 |  |  | -0.00437 |  |  | 0.08446 |  | 1 | CAPACITY
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 0 |  |  | -0.00438 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 0 |  |  | -0.00438 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 329.17 |  |  | -0.00438 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00438 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00438 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-044
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 3.21 |  |  | -0.00438 |  |  | 0 |  | 1 | CAPACITY
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 16.46 |  |  | -0.0044 |  |  | 0.12623 |  | 1 | CAPACITY
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 60 | 48.17 |  |  | -0.00442 |  |  | 0.08446 |  | 1 | CAPACITY
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0 |  |  | -0.00443 |  |  | 0 |  | 1 | NEWENERGY | W1-045
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.13 | 4.12 |  |  | -0.00443 |  |  | 0 |  | 1 | CAPACITY | W1-045
208876 | WLAN | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00443 |  |  | 0 |  | 1 | CAPACITY
239024 | 02NWCAG5 | 16.5 | 202 | 58 | 23 | 141 | 113.2 |  |  | -0.00444 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
239023 | 02NWCAG4 | 14.4 | 202 | 58 | 20 | 92 | 73.86 |  |  | -0.00443 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 2.01 |  |  | -0.00443 |  |  | 0 |  | 1 | CAPACITY
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 1.37 |  |  | -0.00444 |  |  | 0 |  | 1 | CAPACITY | K20
239022 | 02NWCAG3 | 14.4 | 202 | 58 | 20 | 92.3 | 74.11 |  |  | -0.00445 |  |  | 0.04435 |  | 1 | CAPACITY | NEW CASTLE
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 261.73 |  |  | -0.00447 |  |  | 0 |  | 1 | CAPACITY | T-174
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00447 |  |  | 0 |  | 1 | CAPACITY | T-174
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00447 |  |  | 0.04435 |  | 1 | CAPACITY | T-174
208769 | SISO | 12.5 | 229 | 2 | 0 | 2.48 | 0 |  |  | -0.00446 |  |  | 0 |  | 1 | ENERGY
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.5 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1086.27 |  |  | -0.0045 |  |  | 0.01494 |  | 1 | CAPACITY
920571 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 411.86 |  |  | -0.00451 |  |  | 0.04435 |  | 1 | NEW | AA2-161
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.82 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 3.05 |  |  | -0.00456 |  |  | 0 |  | 1 | CAPACITY
913142 | Y1-033 E OP1 | 115 | 226 | 74 | 0 | 34.02 | 0 |  |  | -0.00462 |  |  | 0 |  | 1 | NEWENERGY | Y1-033
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 4.01 |  |  | -0.00462 |  |  | 0 |  | 1 | CAPACITY | Y1-033
209030 | FRFA O01 | 12.5 | 229 | 2 | 0 | 3.2 | 0 |  |  | -0.00462 |  |  | 0 |  | 1 | NEW
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 0.4 | 0.32 |  |  | -0.00462 |  |  | 0 |  | 1 | CAPACITY | V3-051
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 353.26 |  |  | -0.00471 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00471 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00471 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-076
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 140 | 182.2 | 146.28 |  |  | -0.00474 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 118.7 | 175.2 | 140.66 |  |  | -0.00474 |  |  | 0.04435 |  | 1 | CAPACITY | AE SPRINGDALE
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 118.7 | 172.2 | 138.25 |  |  | -0.00474 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.00474 |  |  | 0.08446 |  | 1 | CAPACITY
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.00474 |  |  | 0.08446 |  | 1 | CAPACITY
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 19.6 | 15.74 |  |  | -0.00473 |  |  | 0.08446 |  | 1 | CAPACITY
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 39.5 | 31.71 |  |  | -0.00475 |  |  | 0.08446 |  | 1 | CAPACITY
219001 | SEWAREN7GT | 25 | 231 | 58 | 101.5 | 324.6 | 260.61 |  |  | -0.00482 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-089
219002 | SEWAREN7ST | 18 | 231 | 58 | 96.3 | 216.4 | 173.74 |  |  | -0.00482 |  |  | 0 |  | 1 | CAPACITY | Z2-089
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | -0.00482 |  |  | 0 |  | 1 | ENERGY | Z2-089
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | -0.00482 |  |  | 0.04435 |  | 1 | ENERGY | Z2-089
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 5.54 |  |  | -0.00482 |  |  | 0 |  | 1 | CAPACITY
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00484 |  |  | 0 |  | 1 | NEWENERGY | K23
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 0 |  |  | -0.00484 |  |  | 0 |  | 1 | NEWENERGY | L13
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 0 |  |  | -0.00484 |  |  | 0 |  | 1 | NEWENERGY | O48
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | -0.00484 |  |  | 0.05 |  | 1 | MTX
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | -0.00484 |  |  | 0.05 |  | 1 | MTX
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 0 |  |  | -0.00484 |  |  | 0 |  | 1 | NEWENERGY | R40
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 5.06 |  |  | -0.00484 |  |  | 0 |  | 1 | CAPACITY | O48
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 4.74 |  |  | -0.00484 |  |  | 0 |  | 1 | CAPACITY | L13
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 5.1 | 4.09 |  |  | -0.00484 |  |  | 0 |  | 1 | CAPACITY | K23
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 28.1 |  |  | -0.00489 |  |  | 0.10478 |  | 1 | CAPACITY
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 6.1 |  |  | -0.00491 |  |  | 0 |  | 1 | CAPACITY
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 682.91 |  |  | -0.00499 |  |  | 0.10478 |  | 1 | CAPACITY | Cone1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 682.43 |  |  | -0.00499 |  |  | 0.10478 |  | 1 | CAPACITY | Cone2
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 38.7 | 31.07 |  |  | -0.00499 |  |  | 0.08446 |  | 1 | CAPACITY
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 400 | 321.14 |  |  | -0.00501 |  |  | 0.04435 |  | 1 | CAPACITY | AD2-114
235619 | 01SBEND1 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00501 |  |  | 0.08446 |  | 1 | CAPACITY
235620 | 01SBEND2 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00501 |  |  | 0.08446 |  | 1 | CAPACITY
235621 | 01SBEND3 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00501 |  |  | 0.08446 |  | 1 | CAPACITY
235622 | 01SBEND4 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00501 |  |  | 0.08446 |  | 1 | CAPACITY
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 5.46 |  |  | -0.00501 |  |  | 0 |  | 1 | CAPACITY
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.02 |  |  | -0.00502 |  |  | 0 |  | 1 | CAPACITY
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 853.3 | 685.08 |  |  | -0.00502 |  |  | 0.10478 |  | 1 | CAPACITY | Keys1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 853.1 | 684.92 |  |  | -0.00502 |  |  | 0.10478 |  | 1 | CAPACITY | Keys2
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00503 |  |  | 0 |  | 1 | CAPACITY
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.45 |  |  | -0.00503 |  |  | 0 |  | 1 | CAPACITY
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.72 |  |  | -0.00503 |  |  | 0 |  | 1 | CAPACITY | K22
204555 | 27QUEEN ST | 115 | 227 | 74 | 0 | 5 | 0 |  |  | -0.00504 |  |  | 0 |  | 1 | NEWENERGY
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 42.95 |  |  | -0.00505 |  |  | 0.08446 |  | 1 | CAPACITY
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 42.95 |  |  | -0.00505 |  |  | 0.08446 |  | 1 | CAPACITY
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00505 |  |  | 0.08446 |  | 1 | CAPACITY
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00505 |  |  | 0.08446 |  | 1 | CAPACITY
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00505 |  |  | 0.08446 |  | 1 | CAPACITY
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 68.24 |  |  | -0.00505 |  |  | 0.10478 |  | 1 | CAPACITY
204638 | 27CAT TRAC | 13.2 | 227 | 58 | 0 | 32.3 | 25.93 |  |  | -0.00506 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
204706 | 27CAT TRC2 | 13.2 | 227 | 58 | 0 | 13.9 | 11.16 |  |  | -0.00506 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
903644 | W3-099 E OP1 | 230 | 226 | 74 | 0 | 87 | 0 |  |  | -0.00509 |  |  | 0 |  | 1 | NEWENERGY | W3-099
201144 | W3-099 C OP1 | 230 | 226 | 74 | 0 | 13 | 0 |  |  | -0.00509 |  |  | 0 |  | 1 | NEW | W3-099
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 42 | 0 |  |  | -0.0051 |  |  | 0 |  | 1 | NEWENERGY | P60
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 24.08 |  |  | -0.0051 |  |  | 0.10478 |  | 1 | CAPACITY
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 6.82 |  |  | -0.0051 |  |  | 0 |  | 1 | CAPACITY | P60
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 24.24 |  |  | -0.00512 |  |  | 0.07484 |  | 1 | CAPACITY
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00514 |  |  | 0.12623 |  | 1 | CAPACITY
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00514 |  |  | 0 |  | 1 | CAPACITY
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 23.2 | 0 |  |  | -0.00516 |  |  | 0 |  | 1 | NEWENERGY | K13
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 2.57 |  |  | -0.00516 |  |  | 0 |  | 1 | CAPACITY | K13
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 10.44 |  |  | -0.00517 |  |  | 0.12623 |  | 1 | CAPACITY
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00519 |  |  | 0.12623 |  | 1 | CAPACITY
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 422.06 |  |  | -0.00521 |  |  | 0.10478 |  | 1 | CAPACITY
200805 | 26COLVER13 | 13.2 | 226 | 12 | 77 | 110 | 88.31 |  |  | -0.00522 |  |  | 0.10478 |  | 1 | CAPACITY
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 60 | 0 |  |  | -0.00524 |  |  | 0 |  | 1 | NEWENERGY | R32
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 52 | 0 |  |  | -0.00524 |  |  | 0 |  | 1 | NEWENERGY | O18
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 10.19 |  |  | -0.00524 |  |  | 0 |  | 1 | CAPACITY | R32
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00524 |  |  | 0 |  | 1 | CAPACITY | O18
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 497.77 |  |  | -0.00524 |  |  | 0.10478 |  | 1 | CAPACITY
200809 | 26SITHE | 138 | 226 | 15 | 0 | 36 | 28.9 |  |  | -0.00524 |  |  | 0.10478 |  | 1 | CAPACITY
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 0 |  |  | -0.00531 |  |  | 0 |  | 1 | NEWENERGY | V3-030
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 4.25 |  |  | -0.00531 |  |  | 0 |  | 1 | CAPACITY | V3-030
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 521.86 |  |  | -0.00532 |  |  | 0.10478 |  | 1 | CAPACITY
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 492.95 |  |  | -0.00532 |  |  | 0.10478 |  | 1 | CAPACITY
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 48 | 0 |  |  | -0.00537 |  |  | 0 |  | 1 | NEWENERGY | Q53
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 16.55 |  |  | -0.00537 |  |  | 0.07484 |  | 1 | CAPACITY
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 5.14 |  |  | -0.00537 |  |  | 0 |  | 1 | CAPACITY | Q53
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 57 | 45.76 |  |  | -0.00539 |  |  | 0.08446 |  | 1 | CAPACITY
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 0 |  |  | -0.00546 |  |  | 0 |  | 1 | NEWENERGY | N39
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00546 |  |  | 0 |  | 1 | NEWENERGY | O38
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00546 |  |  | 0 |  | 1 | CAPACITY | N39
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.4 | 7.55 |  |  | -0.00546 |  |  | 0 |  | 1 | CAPACITY | O38
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0 |  |  | -0.00549 |  |  | 0 |  | 1 | NEWENERGY | W2-052
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.00549 |  |  | 0 |  | 1 | CAPACITY | W2-052
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 187.87 |  |  | -0.00552 |  |  | 0.0316 |  | 1 | CAPACITY
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 177.43 |  |  | -0.00552 |  |  | 0.0316 |  | 1 | CAPACITY
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 26.13 |  |  | -0.00552 |  |  | 0.07484 |  | 1 | CAPACITY
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 40 | 0 |  |  | -0.00559 |  |  | 0 |  | 1 | NEWENERGY | Q36
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 6.66 |  |  | -0.00559 |  |  | 0 |  | 1 | CAPACITY | Q36
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | -0.00572 |  |  | 0 |  | 1 | ENERGY
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 33.96 |  |  | -0.00574 |  |  | 0.10478 |  | 1 | CAPACITY
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4.82 |  |  | -0.00578 |  |  | 0 |  | 1 | CAPACITY
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 16.86 |  |  | -0.00581 |  |  | 0.07484 |  | 1 | CAPACITY
219647 | COOPERSOLA E | 13.2 | 231 | 75 | 0 | 0.4 | 0 |  |  | -0.00581 |  |  | 0 |  | 1 | NEWENERGY | AB1-063
200722 | 26SHAWVL 2 | 18 | 226 | 12 | 62 | 124.7 | 100.12 |  |  | -0.00585 |  |  | 0.10478 |  | 1 | CAPACITY
200715 | 26SHAWVL 1 | 18 | 226 | 12 | 62 | 122 | 97.95 |  |  | -0.00585 |  |  | 0.10478 |  | 1 | CAPACITY
200666 | 26SHAWVL 4 | 22 | 226 | 12 | 120 | 171 | 137.29 |  |  | -0.00592 |  |  | 0.10478 |  | 1 | CAPACITY
200665 | 26SHAWVL 3 | 22 | 226 | 12 | 120 | 174.2 | 139.86 |  |  | -0.00592 |  |  | 0.10478 |  | 1 | CAPACITY
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 601.34 |  |  | -0.00596 |  |  | 0.10478 |  | 1 | CAPACITY
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 293.93 |  |  | -0.00596 |  |  | 0.10478 |  | 1 | CAPACITY | Bris2
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 248.4 |  |  | -0.00596 |  |  | 0.10478 |  | 1 | CAPACITY | Bris1
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0 |  |  | -0.00596 |  |  | 0 |  | 1 | NEWENERGY | W2-036
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00596 |  |  | 0 |  | 1 | CAPACITY | W2-036
922932 | AB1-082 OP | 46 | 201 | 55 | 0 | 19.9 | 0 |  |  | -0.00599 |  |  | 0.08446 |  | 1 | NEW
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00605 |  |  | 0.0316 |  | 1 | CAPACITY
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00605 |  |  | 0.0316 |  | 1 | CAPACITY
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00605 |  |  | 0.0316 |  | 1 | CAPACITY
236828 | 01GRAYMONT | 46 | 201 | 2 | 0 | 4 | 0 |  |  | -0.00604 |  |  | 0 |  | 1 | ENERGY
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | -0.00605 |  |  | 0 |  | 1 | MTX | AC1-025
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 538.72 |  |  | -0.00611 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-116
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0 |  |  | -0.00611 |  |  | 0 |  | 1 | NEWENERGY | AB1-139
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0 |  |  | -0.00611 |  |  | 0 |  | 1 | NEWENERGY | AE1-041
930901 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 2.01 |  |  | -0.00611 |  |  | 0 |  | 1 | CAPACITY | AB1-139
938281 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.00611 |  |  | 0 |  | 1 | CAPACITY | AE1-041
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 0 |  |  | -0.00623 |  |  | 0 |  | 1 | NEWENERGY | Z1-069
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00623 |  |  | 0 |  | 1 | CAPACITY | Z1-069
208947 | WSHO CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00628 |  |  | 0.08446 |  | 1 | CAPACITY
208348 | EELI | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00651 |  |  | 0 |  | 1 | CAPACITY
208942 | HARR CT | 12.5 | 229 | 55 | 0 | 42 | 33.72 |  |  | -0.00655 |  |  | 0.08446 |  | 1 | CAPACITY
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 9.64 |  |  | -0.00655 |  |  | 0.12623 |  | 1 | CAPACITY
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 8.19 |  |  | -0.00655 |  |  | 0.10478 |  | 1 | CAPACITY
210319 | WCAR 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00656 |  |  | 0 |  | 1 | CAPACITY
210022 | LING 2 | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00655 |  |  | 0 |  | 1 | CAPACITY
933322 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | -0.00659 |  |  | 0 |  | 1 | MTX | AC2-144
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 24.08 |  |  | -0.00665 |  |  | 0.10478 |  | 1 | CAPACITY
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | -0.0067 |  |  | 0 |  | 1 | ENERGY
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 19 | 15.25 |  |  | -0.00676 |  |  | 0.08446 |  | 1 | CAPACITY
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 134 | 107.58 |  |  | -0.00682 |  |  | 0.08446 |  | 1 | CAPACITY
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 0 |  |  | -0.00685 |  |  | 0 |  | 1 | NEWENERGY | P47
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.8 | 12.69 |  |  | -0.00685 |  |  | 0 |  | 1 | CAPACITY | P47
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00692 |  |  | 0 |  | 1 | NEWENERGY | K02
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 16.86 |  |  | -0.007 |  |  | 0.12623 |  | 1 | CAPACITY
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 17.18 |  |  | -0.00701 |  |  | 0.12623 |  | 1 | CAPACITY
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 16.86 |  |  | -0.00701 |  |  | 0.12623 |  | 1 | CAPACITY
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | -0.00708 |  |  | 0.12623 |  | 1 | ENERGY
208885 | WNHO | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00708 |  |  | 0 |  | 1 | CAPACITY
208697 | PRIN B34 | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00708 |  |  | 0 |  | 1 | CAPACITY
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 31.31 |  |  | -0.00712 |  |  | 0.08446 |  | 1 | CAPACITY
920341 | AA2-132 | 34.5 | 226 | 55 | 0 | 19.9 | 0 |  |  | -0.00724 |  |  | 0.08446 |  | 1 | NEW
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00724 |  |  | 0.08446 |  | 1 | CAPACITY
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00724 |  |  | 0.08446 |  | 1 | CAPACITY
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 20 | 16.06 |  |  | -0.00729 |  |  | 0.08446 |  | 1 | CAPACITY
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | -0.00736 |  |  | 0 |  | 1 | ENERGY
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.61 |  |  | -0.00736 |  |  | 0 |  | 1 | CAPACITY
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 120 |  |  |  | -0.0074
919201 | AA1-144 OP | 230 | 226 | 58 | 0 | 163 | 130.87 |  |  | -0.00741 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-144
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00744 |  |  | 0 |  | 1 | CAPACITY | X1-109
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00744 |  |  | 0.04435 |  | 1 | CAPACITY | X1-109
204662 | 27AES GEN1 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00744 |  |  | 0.04435 |  | 1 | CAPACITY | IRONWOOD
204663 | 27AES GEN2 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00744 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204664 | 27AES GEN3 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00744 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.04 |  |  | -0.00745 |  |  | 0 |  | 1 | CAPACITY
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00759 |  |  | 0.10478 |  | 1 | CAPACITY
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 27.3 |  |  | -0.00762 |  |  | 0.08446 |  | 1 | CAPACITY
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00765 |  |  | 0.10478 |  | 1 | CAPACITY
203932 | AA2-133 GEN | 13.8 | 226 | 55 | 0 | 19.89 | 0 |  |  | -0.00771 |  |  | 0.08446 |  | 1 | NEW
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00773 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00774 |  |  | 0.04435 |  | 1 | CAPACITY | LIBERTY EDDY
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 238 | 191.08 |  |  | -0.00775 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00782 |  |  | 0.08446 |  | 1 | CAPACITY
204651 | 27PORT CT | 13.8 | 227 | 56 | 4 | 35 | 28.1 |  |  | -0.00787 |  |  | 0.08446 |  | 1 | CAPACITY
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | -0.00794 |  |  | 0 |  | 1 | ENERGY
208580 | MGTN 2 | 12.5 | 229 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00794 |  |  | 0 |  | 1 | CAPACITY
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 0 |  |  | -0.00803 |  |  | 0 |  | 1 | NEWENERGY | P28
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | -0.00803 |  |  | 0.10478 |  | 1 | NEW
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 47.37 |  |  | -0.00803 |  |  | 0.10478 |  | 1 | CAPACITY
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00803 |  |  | 0 |  | 1 | CAPACITY | P28
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 17.18 |  |  | -0.00803 |  |  | 0.12623 |  | 1 | CAPACITY
219913 | PENNSAU2 E | 26.4 | 231 | 75 | 0 | 8.2 | 0 |  |  | -0.00808 |  |  | 0 |  | 1 | NEWENERGY | AD2-042
219915 | CINNAMSOL E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.00808 |  |  | 0 |  | 1 | NEWENERGY | AD2-027
219912 | PENNSAU2 C | 26.4 | 231 | 75 | 0 | 5 | 0 |  |  | -0.00808 |  |  | 0 |  | 1 | NEW | AD2-042
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.63 | 3.72 |  |  | -0.00808 |  |  | 0 |  | 1 | CAPACITY
219914 | CINNAMSOL C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00808 |  |  | 0 |  | 1 | CAPACITY | AD2-027
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.4 |  |  | -0.00808 |  |  | 0 |  | 1 | CAPACITY
208920 | WLPK | 12.5 | 229 | 60 | 0 | 40.9 | 32.84 |  |  | -0.00819 |  |  | 0.07484 |  | 1 | CAPACITY
206747 | 28DSM_X3-029 | 34.5 | 228 | 29 | 0 | 11.15 | 0 |  |  | -0.00849 |  |  | 0.10478 |  | 1 | ENERGY
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | -0.00849 |  |  | 0.08446 |  | 1 | ENERGY
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 4 | 3.21 |  |  | -0.0085 |  |  | 0 |  | 1 | CAPACITY
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 18.3 | 14.69 |  |  | -0.00854 |  |  | 0.12623 |  | 1 | CAPACITY
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00868 |  |  | 0.10478 |  | 1 | CAPACITY
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00868 |  |  | 0.10478 |  | 1 | CAPACITY
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 192.53 |  |  | -0.00868 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 160.57 |  |  | -0.00868 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 160.57 |  |  | -0.00868 |  |  | 0.04435 |  | 1 | CAPACITY | LOWER MT BETHEL
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00884 |  |  | 0 |  | 1 | NEWENERGY | Y2-018
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 317.93 |  |  | -0.00896 |  |  | 0 |  | 1 | CAPACITY | Hummel
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 194.29 |  |  | -0.00896 |  |  | 0 |  | 1 | CAPACITY | Hummel
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.00896 |  |  | 0.04435 |  | 1 | CAPACITY | Hummel
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.00896 |  |  | 0 |  | 1 | CAPACITY | Hummel
208946 | MACR CT | 12.5 | 229 | 55 | 0 | 72 | 57.81 |  |  | -0.00917 |  |  | 0.08446 |  | 1 | CAPACITY
209018 | SUNBIPCT | 12.5 | 229 | 55 | 0 | 36 | 28.9 |  |  | -0.00916 |  |  | 0.08446 |  | 1 | CAPACITY
212345 | PENS | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00916 |  |  | 0 |  | 1 | CAPACITY
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 389.39 |  |  | -0.00918 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-115
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 30.1 | 24.17 |  |  | -0.00923 |  |  | 0.08446 |  | 1 | CAPACITY
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 34.28 |  |  | -0.00924 |  |  | 0.10478 |  | 1 | CAPACITY
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 26.09 |  |  | -0.00924 |  |  | 0.10478 |  | 1 | CAPACITY
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 6.42 |  |  | -0.00924 |  |  | 0 |  | 1 | CAPACITY
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 4.9 |  |  | -0.00924 |  |  | 0 |  | 1 | CAPACITY
212435 | SMIL | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00923 |  |  | 0 |  | 1 | CAPACITY
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 11.24 |  |  | -0.00925 |  |  | 0.08446 |  | 1 | CAPACITY
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 152 | 122.03 |  |  | -0.00927 |  |  | 0.08446 |  | 1 | CAPACITY
206341 | 28GIL 8 | 13.8 | 228 | 58 | 69.9 | 90 | 72.26 |  |  | -0.00927 |  |  | 0.04435 |  | 1 | CAPACITY | GILBERT
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 87 | 100 | 87.11 |  |  | -0.00927 |  |  | 0 |  | 1 | CAPACITY | GILBERT
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 85.3 | 98 | 85.37 |  |  | -0.00927 |  |  | 0 |  | 1 | CAPACITY | GILBERT
208948 | WILL CT | 12.5 | 229 | 55 | 0 | 27.4 | 22 |  |  | -0.00926 |  |  | 0.08446 |  | 1 | CAPACITY
212005 | ALWD | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00926 |  |  | 0 |  | 1 | CAPACITY
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 69.05 |  |  | -0.00928 |  |  | 0.10478 |  | 1 | CAPACITY
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 65.83 |  |  | -0.00928 |  |  | 0.10478 |  | 1 | CAPACITY
208941 | FISH CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00928 |  |  | 0.08446 |  | 1 | CAPACITY
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.4 | 9.15 |  |  | -0.00928 |  |  | 0 |  | 1 | CAPACITY | Q27
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.81 |  |  | -0.00928 |  |  | 0 |  | 1 | CAPACITY | N14
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00929 |  |  | 0.04435 |  | 1 | CAPACITY | MOXIE PATRIOT
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00929 |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 4.82 |  |  | -0.00929 |  |  | 0 |  | 1 | CAPACITY
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 608.97 |  |  | -0.00931 |  |  | 0.10478 |  | 1 | CAPACITY
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 608.49 |  |  | -0.00931 |  |  | 0.10478 |  | 1 | CAPACITY
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00939 |  |  | 0.08446 |  | 1 | CAPACITY
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 6 | 4.82 |  |  | -0.00939 |  |  | 0 |  | 1 | CAPACITY
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 0 |  |  | -0.0094 |  |  | 0 |  | 1 | NEWENERGY | AA2-017
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 0 |  |  | -0.0094 |  |  | 0 |  | 1 | NEW | AA2-017
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00943 |  |  | 0 |  | 1 | NEWENERGY | W4-046
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 1.93 |  |  | -0.00943 |  |  | 0 |  | 1 | CAPACITY | W4-046
211065 | PSPA IPP | 13.8 | 229 | 75 | 0 | 18.4 | 6.74 |  |  | -0.00944 |  |  | 0 |  | 1 | NEWENERGY | U4-014
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 0 |  |  | -0.00952 |  |  | 0 |  | 1 | NEWENERGY | AC1-071
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 7.02 |  |  | -0.00952 |  |  | 0 |  | 1 | NEW | AC1-071
211375 | BEAC | 69 | 229 | 2 | 0 | 20 | 0 |  |  | -0.00954 |  |  | 0.10478 |  | 1 | ENERGY
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 47.77 |  |  | -0.00954 |  |  | 0.08446 |  | 1 | CAPACITY
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 47.21 |  |  | -0.00954 |  |  | 0.08446 |  | 1 | CAPACITY
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 23.76 |  |  | -0.00954 |  |  | 0.08446 |  | 1 | CAPACITY
208943 | HARW CT | 12.5 | 229 | 55 | 0 | 27.2 | 21.84 |  |  | -0.00954 |  |  | 0.08446 |  | 1 | CAPACITY
211591 | HARW | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00954 |  |  | 0 |  | 1 | CAPACITY
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00954 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G1
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00954 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G2
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00954 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G3
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.00954 |  |  | 0.05 |  | 1 | MTX | AB1-182
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | -0.00954 |  |  | 0.05 |  | 1 | MTX | Z2-107
209009 | PEIP 2 | 13.8 | 229 | 56 | 0 | 43.7 | 35.08 |  |  | -0.00954 |  |  | 0.08446 |  | 1 | CAPACITY
208944 | JENK CT | 12.5 | 229 | 55 | 0 | 28 | 22.48 |  |  | -0.00954 |  |  | 0.08446 |  | 1 | CAPACITY
209010 | PEIP 1 | 13.8 | 229 | 29 | 0 | 26.7 | 21.43 |  |  | -0.00954 |  |  | 0.10478 |  | 1 | CAPACITY
211374 | AVOC | 12.5 | 229 | 2 | 0 | 17.4 | 13.97 |  |  | -0.00954 |  |  | 0 |  | 1 | CAPACITY
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 7.23 |  |  | -0.00954 |  |  | 0 |  | 1 | CAPACITY | K21
209003 | KSTN IPP | 13.8 | 229 | 65 | 0 | 4.9 | 3.93 |  |  | -0.00954 |  |  | 0 |  | 1 | CAPACITY
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.65 |  |  | -0.00954 |  |  | 0 |  | 1 | CAPACITY | L18
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 39.1 |  |  | -0.00956 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 38.86 |  |  | -0.00956 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 35.57 |  |  | -0.00956 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 23.44 |  |  | -0.00956 |  |  | 0.04435 |  | 1 | CAPACITY | HUNLOCK
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1091.76 |  |  | -0.0096 |  |  | 0.01494 |  | 1 | CAPACITY
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 64.23 |  |  | -0.00978 |  |  | 0.10478 |  | 1 | CAPACITY
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 152.86 |  |  | -0.00985 |  |  | 0.04435 |  | 1 | CAPACITY | ONTELAUNEE
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 152.86 |  |  | -0.00985 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 139.94 |  |  | -0.00985 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
209007 | NOEN IPP | 13.8 | 229 | 12 | 80 | 111.4 | 89.44 |  |  | -0.00998 |  |  | 0.10478 |  | 1 | CAPACITY
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.33 |  |  | -0.01015 |  |  | 0 |  | 1 | CAPACITY
208940 | ALLE CT | 12.5 | 229 | 55 | 0 | 56 | 44.96 |  |  | -0.01024 |  |  | 0.08446 |  | 1 | CAPACITY
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.01028 |  |  | 0 |  | 1 | CAPACITY | Z2-046
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.01028 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-046
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1090.36 |  |  | -0.01028 |  |  | 0.01494 |  | 1 | CAPACITY
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 0 |  |  | -0.0105 |  |  | 0 |  | 1 | NEWENERGY | W3-044
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 6.1 |  |  | -0.0105 |  |  | 0 |  | 1 | CAPACITY | W3-044
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.01062 |  |  | 0 |  | 1 | NEWENERGY | W3-077
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 5.7 | 4.58 |  |  | -0.01062 |  |  | 0 |  | 1 | CAPACITY | W3-077
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.01062 |  |  | 0 |  | 1 | CAPACITY | W2-091
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01071 |  |  | 0 |  | 1 | NEWENERGY | W1-127
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0 |  |  | -0.01071 |  |  | 0 |  | 1 | NEWENERGY | U2-059
925462 | AC1-018 E | 34.5 | 228 | 75 | 0 | 0.9 | 0 |  |  | -0.01071 |  |  | 0 |  | 1 | NEWENERGY | AC1-018
925461 | AC1-018 C | 34.5 | 228 | 75 | 0 | 0.5 | 0 |  |  | -0.01071 |  |  | 0 |  | 1 | NEW | AC1-018
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01071 |  |  | 0 |  | 1 | CAPACITY | W1-127
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.01071 |  |  | 0 |  | 1 | CAPACITY | U2-059
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.01075 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.01125 |  |  | 0 |  | 1 | NEWENERGY | W4-073
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.01125 |  |  | 0 |  | 1 | CAPACITY
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 130.87 |  |  | -0.01229 |  |  | 0.04435 |  | 1 | CAPACITY | GRAYS FERRY
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.01263 |  |  | 0.08446 |  | 1 | CAPACITY
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.01307 |  |  | 0.08446 |  | 1 | CAPACITY
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.01307 |  |  | 0.08446 |  | 1 | CAPACITY
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.01318 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.01318 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.01318 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.01318 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.01318 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200048 | BETH CT5 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.01318 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
200044 | BETH CT1 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.01318 |  |  | 0.04435 |  | 1 | CAPACITY | BETH1234
207402 | 28AA2-082 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.01359 |  |  | 0.05 |  | 1 | MTX | AA2-082
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.01386 |  |  | 0.08446 |  | 1 | CAPACITY
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.01386 |  |  | 0.08446 |  | 1 | CAPACITY
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0 |  |  | -0.01518 |  |  | 0 |  | 1 | NEWENERGY | AD2-070
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 2.81 |  |  | -0.01518 |  |  | 0 |  | 1 | CAPACITY | AD2-070
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.01551 |  |  | 0 |  | 1 | NEWENERGY | V4-001
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.61 |  |  | -0.01551 |  |  | 0 |  | 1 | CAPACITY | V4-001
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 900.89 |  |  | -0.01676 |  |  | 0.01494 |  | 1 | CAPACITY
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.0171 |  |  | 0 |  | 1 | NEWENERGY | W4-097
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.0171 |  |  | 0 |  | 1 | CAPACITY | W4-097
214030 | WAYNEJCT | 13.8 | 230 | 2 | 0 | 8.8 | 7.07 |  |  | -0.01722 |  |  | 0 |  | 1 | CAPACITY
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.01747 |  |  | 0.08446 |  | 1 | CAPACITY
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.01747 |  |  | 0.08446 |  | 1 | CAPACITY
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.01833 |  |  | 0 |  | 1 | NEWENERGY | AC1-030
925561 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.01833 |  |  | 0 |  | 1 | CAPACITY | AC1-030
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0 |  |  | -0.01844 |  |  | 0 |  | 1 | NEWENERGY | X1-071
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.28 |  |  | -0.01844 |  |  | 0 |  | 1 | CAPACITY | X1-071
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 22.48 |  |  | -0.01943 |  |  | 0.10478 |  | 1 | CAPACITY
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 898.96 |  |  | -0.02132 |  |  | 0.01494 |  | 1 | CAPACITY
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.02548 |  |  | 0.08446 |  | 1 | CAPACITY
218455 | CINNBAY_CGEN | 26.4 | 231 | 75 | 0 | 9 | 0 |  |  | -0.0263 |  |  | 0 |  | 1 | NEWENERGY
924132 | NEWROADSO E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.0263 |  |  | 0 |  | 1 | NEWENERGY | AB2-057
217198 | EDGEBORO_1E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.0263 |  |  | 0 |  | 1 | NEWENERGY | V3-058
217199 | EDGEBORO_2E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.0263 |  |  | 0 |  | 1 | NEWENERGY | V3-059
924131 | NEWROADSO C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.0263 |  |  | 0 |  | 1 | CAPACITY | AB2-057
218781 | BRIS_MYERS | 26 | 231 | 2 | 0 | 3 | 2.41 |  |  | -0.0263 |  |  | 0 |  | 1 | CAPACITY
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0 |  |  | -0.02969 |  |  | 0 |  | 1 | NEWENERGY | AC1-017
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0 |  |  | -0.02969 |  |  | 0 |  | 1 | NEWENERGY | X1-070
925451 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 1.12 |  |  | -0.02969 |  |  | 0 |  | 1 | CAPACITY | AC1-017
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.96 |  |  | -0.02969 |  |  | 0 |  | 1 | CAPACITY | X1-070
213798 | MERCK 3 | 13.8 | 230 | 2 | 13 | 35 | 28.1 |  |  | -0.03136 |  |  | 0 |  | 1 | CAPACITY
213797 | MERCK 2 | 13.8 | 230 | 2 | 4 | 25 | 20.07 |  |  | -0.03136 |  |  | 0 |  | 1 | CAPACITY
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 3.29 |  |  | -0.03136 |  |  | 0 |  | 1 | CAPACITY
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 0 |  |  | -0.03795 |  |  | 0 |  | 1 | NEWENERGY | W3-080
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.03795 |  |  | 0.08446 |  | 1 | CAPACITY
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.03795 |  |  | 0.08446 |  | 1 | CAPACITY
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.03795 |  |  | 0.08446 |  | 1 | CAPACITY
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.03795 |  |  | 0.08446 |  | 1 | CAPACITY
925442 | AC1-016 E | 26.4 | 231 | 75 | 0 | 5.45 | 0 |  |  | -0.03795 |  |  | 0 |  | 1 | NEWENERGY | AC1-016
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | -0.03795 |  |  | 0 |  | 1 | NEWENERGY | W4-103
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | -0.03795 |  |  | 0 |  | 1 | NEWENERGY | W2-102
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -0.03795 |  |  | 0 |  | 1 | NEWENERGY | Y3-026
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.03795 |  |  | 0 |  | 1 | CAPACITY | Y3-026
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 2.97 |  |  | -0.03795 |  |  | 0 |  | 1 | CAPACITY | W3-080
925441 | AC1-016 C | 26.4 | 231 | 75 | 0 | 3.34 | 2.68 |  |  | -0.03795 |  |  | 0 |  | 1 | CAPACITY | AC1-016
219685 | NATIONAL_GYP | 26 | 231 | 2 | 0 | 2.8 | 2.25 |  |  | -0.03795 |  |  | 0 |  | 1 | CAPACITY
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.03795 |  |  | 0 |  | 1 | CAPACITY | W2-102
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.03795 |  |  | 0 |  | 1 | CAPACITY | W4-103
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03858 |  |  | 0.08446 |  | 1 | CAPACITY
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03858 |  |  | 0.08446 |  | 1 | CAPACITY
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03858 |  |  | 0.08446 |  | 1 | CAPACITY
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03858 |  |  | 0.08446 |  | 1 | CAPACITY
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03858 |  |  | 0.08446 |  | 1 | CAPACITY
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03858 |  |  | 0.08446 |  | 1 | CAPACITY
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.03858 |  |  | 0.08446 |  | 1 | CAPACITY
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 38.54 |  |  | -0.03858 |  |  | 0.08446 |  | 1 | CAPACITY
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 260.3 | 208.98 |  |  | -0.04097 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | -0.04097 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | -0.04097 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill B
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 205.69 |  |  | -0.04099 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | -0.04099 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | -0.04099 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill A
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0 |  |  | -0.04551 |  |  | 0 |  | 1 | NEWENERGY | W2-080
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.04551 |  |  | 0 |  | 1 | CAPACITY | W2-080
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0 |  |  | -0.05899 |  |  | 0 |  | 1 | NEWENERGY | X2-075
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 1.83 |  |  | -0.05899 |  |  | 0 |  | 1 | CAPACITY | X2-075
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.0599 |  |  | 0.08446 |  | 1 | CAPACITY
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 1.04 |  |  | -0.0599 |  |  | 0 |  | 1 | CAPACITY | T20
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.06153 |  |  | 0 |  | 1 | NEWENERGY | V3-024
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0 |  |  | -0.06153 |  |  | 0 |  | 1 | NEWENERGY | V2-009 2
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0 |  |  | -0.06153 |  |  | 0 |  | 1 | NEWENERGY | X2-088
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.06153 |  |  | 0 |  | 1 | CAPACITY | V3-024
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 1.52 |  |  | -0.06153 |  |  | 0 |  | 1 | CAPACITY | V2-009 2
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.72 |  |  | -0.06153 |  |  | 0 |  | 1 | CAPACITY | X2-088
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.06165 |  |  | 0 |  | 1 | NEWENERGY | W3-029
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0 |  |  | -0.06165 |  |  | 0 |  | 1 | NEWENERGY | W3-003
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0 |  |  | -0.06165 |  |  | 0 |  | 1 | NEW | AE1-156
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0 |  |  | -0.06165 |  |  | 0 |  | 1 | NEWENERGY | AE1-156
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.06165 |  |  | 0 |  | 1 | NEWENERGY | W1-132
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.06165 |  |  | 0 |  | 1 | NEWENERGY | V4-070
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.06165 |  |  | 0 |  | 1 | NEWENERGY | V4-069
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.06165 |  |  | 0 |  | 1 | NEWENERGY | W2-061
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.06165 |  |  | 0 |  | 1 | CAPACITY | W3-029
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.06165 |  |  | 0 |  | 1 | CAPACITY | V4-069
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.06165 |  |  | 0 |  | 1 | CAPACITY | V4-070
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.06165 |  |  | 0 |  | 1 | CAPACITY | W2-061
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0 |  |  | -0.06202 |  |  | 0 |  | 1 | NEWENERGY | W3-124
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0 |  |  | -0.06202 |  |  | 0 |  | 1 | NEWENERGY | V2-009 1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.87 |  |  | -0.06202 |  |  | 0 |  | 1 | CAPACITY | W3-124
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.06202 |  |  | 0 |  | 1 | CAPACITY | V2-009 1
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.07263 |  |  | 0 |  | 1 | NEWENERGY | W2-016
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.07263 |  |  | 0 |  | 1 | CAPACITY | W2-016
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0 |  |  | -0.07307 |  |  | 0 |  | 1 | NEWENERGY | V3-070
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.07307 |  |  | 0 |  | 1 | CAPACITY | V3-070
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  |  |  | -0.0733
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0 |  |  | -0.08081 |  |  | 0 |  | 1 | NEWENERGY | V2-009 3
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0 |  |  | -0.08081 |  |  | 0 |  | 1 | NEWENERGY | V2-009 4
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 1.92 |  |  | -0.08081 |  |  | 0 |  | 1 | CAPACITY | V2-009 3
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 1.15 |  |  | -0.08081 |  |  | 0 |  | 1 | CAPACITY | V2-009 4
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0 |  |  | -0.08449 |  |  | 0 |  | 1 | NEWENERGY | W2-050
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0 |  |  | -0.10368 |  |  | 0 |  | 1 | NEWENERGY | W1-121 Z
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.10368 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.10368 |  |  | 0 |  | 1 | CAPACITY | W1-121 Z
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.46 |  |  | -0.10368 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
218780 | PRINCENTON_U | 26 | 231 | 2 | 0 | 31.56 | 25.34 |  |  | -0.1329 |  |  | 0 |  | 1 | CAPACITY
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0 |  |  | -0.1329 |  |  | 0 |  | 1 | NEWENERGY | Z1-096
219622 | TRENT_BIOGAS | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.1329 |  |  | 0 |  | 1 | CAPACITY
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 2.39 |  |  | -0.1329 |  |  | 0 |  | 1 | CAPACITY | Z1-096
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 35.24 |  |  | -0.17728 |  |  | 0.10478 |  | 1 | CAPACITY
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0 |  |  | -0.30817 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0 |  |  | -0.30817 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
932032 | AC2-009 E | 13.2 | 231 | 75 | -0.5 | 0.49 | 0 |  |  | -0.30817 |  |  | 0 |  | 1 | NEWENERGY | AC2-009
932031 | AC2-009 C | 13.2 | 231 | 75 | -0.1 | 0.1 | 0 |  |  | -0.30817 |  |  | 0 |  | 1 | NEW | AC2-009
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.30817 |  |  | 0 |  | 1 | CAPACITY | AA2-058
219650 | TRENT_COLLEG | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.39748 |  |  | 0 |  | 1 | CAPACITY
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0 |  |  | -0.39748 |  |  | 0 |  | 1 | NEWENERGY | W4-058
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.22 |  |  | -0.39748 |  |  | 0 |  | 1 | CAPACITY | W4-058

## FG 28-GD-S2-S138
****** PJM Generator Deliverability Detailed Report ****** POWER-GEM [TARA Ver 2001.1a PJMGD RC3 64-bit - Wed Aug 18 16:46:46 2021]
FG Index | 138 | Monitored Facility:227945 LEWIS #2 138 227902 LEWIS #1 138 1 / Contingency:AE_P7-1 AE3TOWER[Tower]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
286.8 | 105 | 102.62 | AC | 153.35 | 148.65 | -1.39 | 0.89 | -0.36 | 301.14 | 294.3 | 0.000204 | 0 | 12850.4 | 0 | 11615.4 | 0.05 | 1246.31 | 1235 | 11.31 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited?
900000 | CARDIFF E | 230 | 234 | 74 | 0 | 1235 | 0 | 1235 | FiftyFifty | 0.12036 | 148.6483 |  | 0 | 1 | 1 | NEWENERGY | OSW_CARDIF
227900 | CARDIFF C | 230 | 234 | 74 | 0 | 275 | 275 | 275 | FiftyFifty | 0.12036 |  |  | 0 | 1 | 1 | CAPACITY | OSW_CARDIF
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  | 105 | LTF/CMTX NF | 0.00189 | 0.1988 | -0.0214
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  | 673 | LTF/CMTX NF | 0.00093 | 0.6277 | -0.137
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  | 55.3 | CLTF | 0.00062 | 0.0345 | -0.0113
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  | 258.3 | CLTF | 4e-05 | 0.0091 | -0.0526
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  | 210 | CLTF | 3e-05 | 0.0065 | -0.0428
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.6 |  | 173.6 | CLTF | 4e-05 | 0.0065 | -0.0353
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 4e-05 | 0.0021 | -0.0113
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 4e-05 | 0.002 | -0.0111
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 3e-05 | 0.0014 | -0.0102
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 3e-05 | 0.0014 | -0.0101
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  | 57.8 | CLTF | 2e-05 | 0.0009 | -0.0118
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  | 35 | CLTF | 2e-05 | 0.0007 | -0.0071
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 | 4.67 | Adder/OL | -0.12189 | -0.5698 | 0.001 | 0.10478 |  | 1 | ENERGY
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 | 6.63 | Adder/OL | -0.12378 | -0.8207 | 0.0013 | 0.12623 |  | 1 | ENERGY
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0 |  |  | 0.0079 |  |  | 0 |  | 1 | NEWENERGY | AB2-122
924701 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.56 |  |  | 0.0079 |  |  | 0 |  | 1 | CAPACITY | AB2-122
227928 | V4-067E | 12.9 | 234 | 75 | 1.6 | 1.6 | 0 |  |  | 0.00782 |  |  | 0 |  | 1 | NEWENERGY | V4-067
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.79 |  |  | 0.00782 |  |  | 0 |  | 1 | CAPACITY | V4-067
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 998.11 |  |  | 0.00309 |  |  | 0.01494 |  | 1 | CAPACITY
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 992.1 |  |  | 0.00309 |  |  | 0.01494 |  | 1 | CAPACITY
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | 0.00309 |  |  | 0.08446 |  | 1 | ENERGY
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1026.43 |  |  | 0.00306 |  |  | 0.01494 |  | 1 | CAPACITY
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | 0.00181 |  |  | 0.04435 |  | 1 | NEW | AA2-069
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 154.95 |  |  | 0.00181 |  |  | 0.04435 |  | 1 | CAPACITY | Garrison
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 93.29 |  |  | 0.00181 |  |  | 0 |  | 1 | CAPACITY | Garrison
232901 | NORTHST | 69 | 235 | 56 | 5 | 46 | 36.93 |  |  | 0.00181 |  |  | 0.08446 |  | 1 | CAPACITY
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 12.2 |  |  | 0.00181 |  |  | 0.10478 |  | 1 | CAPACITY
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 39.34 |  |  | 0.00178 |  |  | 0.08446 |  | 1 | CAPACITY
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 38.54 |  |  | 0.00178 |  |  | 0.08446 |  | 1 | CAPACITY
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 152.54 |  |  | 0.00171 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00171 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00171 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00171 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC2
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 0 |  |  | 0.00166 |  |  | 0 |  | 1 | NEWENERGY | AB1-056
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 330.7 |  |  | 0.00166 |  |  | 0.10478 |  | 1 | CAPACITY
930201 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 51.71 |  |  | 0.00166 |  |  | 0 |  | 1 | CAPACITY | AB1-056
232920 | IR10 | 13.2 | 235 | 55 | 12.6 | 16.1 | 12.93 |  |  | 0.00165 |  |  | 0.08446 |  | 1 | CAPACITY
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0 |  |  | 0.00165 |  |  | 0 |  | 1 | NEWENERGY | AB1-137
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 3.37 |  |  | 0.00165 |  |  | 0 |  | 1 | CAPACITY | AB1-137
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | 0.00165 |  |  | 0.10478 |  | 1 | ENERGY
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.00165 |  |  | 0 |  | 1 | NEWENERGY | Z2-077
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.00165 |  |  | 0 |  | 1 | NEWENERGY | Z2-076
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.00165 |  |  | 0 |  | 1 | CAPACITY | Z2-076
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.00165 |  |  | 0 |  | 1 | CAPACITY | Z2-077
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.41 |  |  | 0.00164 |  |  | 0 |  | 1 | CAPACITY
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.05 |  |  | 0.00163 |  |  | 0 |  | 1 | CAPACITY
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.00163 |  |  | 0.08446 |  | 1 | CAPACITY
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.00163 |  |  | 0.08446 |  | 1 | CAPACITY
917082 | CHERRYDALE E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00162 |  |  | 0 |  | 1 | NEWENERGY | Z2-012
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00162 |  |  | 0 |  | 1 | NEWENERGY | W1-005
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00162 |  |  | 0 |  | 1 | NEWENERGY | W1-004
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00162 |  |  | 0 |  | 1 | NEWENERGY | W1-006
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00162 |  |  | 0 |  | 1 | NEWENERGY | W1-003
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.00162 |  |  | 0.08446 |  | 1 | CAPACITY
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.00162 |  |  | 0.08446 |  | 1 | CAPACITY
232915 | OH NUG4 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.00162 |  |  | 0.08446 |  | 1 | CAPACITY
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.00162 |  |  | 0.08446 |  | 1 | CAPACITY
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 39.03 |  |  | 0.00162 |  |  | 0.08446 |  | 1 | CAPACITY
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 38.94 |  |  | 0.00162 |  |  | 0.08446 |  | 1 | CAPACITY
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 38.68 |  |  | 0.00162 |  |  | 0.08446 |  | 1 | CAPACITY
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 26.05 |  |  | 0.00162 |  |  | 0.08446 |  | 1 | CAPACITY
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.00162 |  |  | 0 |  | 1 | CAPACITY | W1-006
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.00162 |  |  | 0 |  | 1 | CAPACITY | W1-003
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.00162 |  |  | 0 |  | 1 | CAPACITY | W1-005
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.00162 |  |  | 0 |  | 1 | CAPACITY | W1-004
232905 | BAYVIEW1 | 24.9 | 235 | 65 | 0 | 12.5 | 10.04 |  |  | 0.00162 |  |  | 0.12623 |  | 1 | CAPACITY
917081 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.00162 |  |  | 0 |  | 1 | CAPACITY | Z2-012
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 0 |  |  | 0.00161 |  |  | 0 |  | 1 | NEWENERGY | AA1-102
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 45.76 |  |  | 0.00161 |  |  | 0 |  | 1 | CAPACITY | AA1-102
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0 |  |  | 0.0016 |  |  | 0 |  | 1 | NEWENERGY | Y3-058
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0 |  |  | 0.00161 |  |  | 0 |  | 1 | NEWENERGY | X1-032
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 8.03 |  |  | 0.00161 |  |  | 0 |  | 1 | CAPACITY
293670 | O-025 C | 25 | 235 | 64 | 0 | 6 | 4.82 |  |  | 0.00161 |  |  | 0 |  | 1 | CAPACITY
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 5.7 | 4.58 |  |  | 0.0016 |  |  | 0 |  | 1 | CAPACITY | Y3-058
232919 | VN10 | 13.2 | 235 | 55 | 12.4 | 14.3 | 12.46 |  |  | 0.00157 |  |  | 0 |  | 1 | CAPACITY
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 122.84 |  |  | 0.00156 |  |  | 0.10478 |  | 1 | CAPACITY
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0 |  |  | 0.00156 |  |  | 0 |  | 1 | NEWENERGY | Y1-080
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 1.03 |  |  | 0.00156 |  |  | 0 |  | 1 | CAPACITY | Y1-080
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00154 |  |  | 0 |  | 1 | NEWENERGY | X3-008
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.00154 |  |  | 0 |  | 1 | CAPACITY | X3-008
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 55.4 |  |  | 0.00145 |  |  | 0.12623 |  | 1 | CAPACITY
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0 |  |  | 0.0014 |  |  | 0 |  | 1 | NEWENERGY | Y1-079
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.0014 |  |  | 0 |  | 1 | CAPACITY | Y1-079
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0 |  |  | 0.00137 |  |  | 0 |  | 1 | NEWENERGY | X3-066
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 2.28 | 1.83 |  |  | 0.00137 |  |  | 0 |  | 1 | CAPACITY | X3-066
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 57.24 |  |  | 0.00133 |  |  | 0.10478 |  | 1 | CAPACITY
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 45.76 |  |  | 0.00133 |  |  | 0.08446 |  | 1 | CAPACITY
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 44.16 |  |  | 0.00133 |  |  | 0.04435 |  | 1 | CAPACITY | DELAWARE CITY
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.00133 |  |  | 0 |  | 1 | NEWENERGY | AB1-142
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.00133 |  |  | 0 |  | 1 | NEWENERGY | AB1-141
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 14.29 |  |  | 0.00133 |  |  | 0.08446 |  | 1 | CAPACITY
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.00133 |  |  | 0 |  | 1 | CAPACITY | AB1-142
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.00133 |  |  | 0 |  | 1 | CAPACITY | AB1-141
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 19.11 |  |  | 0.0013 |  |  | 0.12623 |  | 1 | CAPACITY
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00113 |  |  | 0 |  | 1 | NEWENERGY | AB2-179
233931 | AB2-179 C | 0.38 | 235 | 75 | 0 | 38 | 30.51 |  |  | 0.00113 |  |  | 0 |  | 1 | CAPACITY | AB2-179
925112 | AB2-168 E | 34.5 | 235 | 75 | 0 | 5.2 | 0 |  |  | 0.00081 |  |  | 0 |  | 1 | NEWENERGY | AB2-168
925111 | AB2-168 C | 34.5 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.00081 |  |  | 0 |  | 1 | CAPACITY | AB2-168
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.09 |  |  | 0.00079 |  |  | 0 |  | 1 | CAPACITY
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 369.31 |  |  | 0.00064 |  |  | 0.04435 |  | 1 | CAPACITY | Y1-065
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00064 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00064 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200055 | ROCKSP 4 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00064 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 4
200054 | ROCKSP 3 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00064 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 3
200052 | ROCKSP 1 | 18 | 225 | 57 | 145.7 | 167.5 | 145.91 |  |  | 0.00064 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 1
200053 | ROCKSP 2 | 18 | 225 | 57 | 144.9 | 166.5 | 145.04 |  |  | 0.00064 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 2
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 13.81 |  |  | 0.0005 |  |  | 0.08446 |  | 1 | CAPACITY
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 18.47 |  |  | 0.00047 |  |  | 0.08446 |  | 1 | CAPACITY
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 18.39 |  |  | 0.00047 |  |  | 0.08446 |  | 1 | CAPACITY
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1034.24 |  |  | 0.00031 |  |  | 0.01494 |  | 1 | CAPACITY
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 306.69 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA2
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 154.95 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | DELTA
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | DELTA
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00031 |  |  | 0 |  | 1 | CAPACITY | DELTA
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 139.7 |  |  | 0.0003 |  |  | 0.10478 |  | 1 | CAPACITY
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1049.33 |  |  | 0.0003 |  |  | 0.01494 |  | 1 | CAPACITY
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00029 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 69.05 |  |  | 0.00029 |  |  | 0.10478 |  | 1 | CAPACITY
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 11.4 |  |  | 0.00029 |  |  | 0.08446 |  | 1 | CAPACITY
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 256.27 |  |  | 9e-05 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | 9e-05 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 134.08 |  |  | 9e-05 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | 9e-05 |  |  | 0.04435 |  | 1 | CAPACITY | HUNTERSTOWN
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | 6e-05 |  |  | 0.0316 |  | 1 | CAPACITY
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | 6e-05 |  |  | 0.0316 |  | 1 | CAPACITY
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | 6e-05 |  |  | 0.0316 |  | 1 | CAPACITY
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | 6e-05 |  |  | 0.0316 |  | 1 | CAPACITY
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 246 |  |  | 5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 102.85 |  |  | 5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 45.76 |  |  | 5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | ENERGY
226895 | WOAKV2-037 E | 69 | 233 | 65 | 0 | 4.5 | 0 |  |  | 5e-05 |  |  | 0 |  | 1 | ENERGY
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 10.68 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | 6e-05 |  |  | 0 |  | 1 | ENERGY
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.49 |  |  | 5e-05 |  |  | 0 |  | 1 | CAPACITY
220904 | CRANE G2 | 20 | 232 | 12 | 60 | 195 | 0 |  |  | 5e-05 |  |  | 0.10478 |  | 1 | NEW
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 695.27 |  |  | 5e-05 |  |  | 0.01494 |  | 1 | CAPACITY
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 675.85 |  |  | 5e-05 |  |  | 0.01494 |  | 1 | CAPACITY
910861 | X3-087 C | 230 | 233 | 58 | 0 | 744 | 597.33 |  |  | 4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 516 |  |  | 5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 512.95 |  |  | 5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 497.29 |  |  | 4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 492.39 |  |  | 4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 477.7 |  |  | 5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 469.91 |  |  | 5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 318.73 |  |  | 5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 272.01 |  |  | 4e-05 |  |  | 0 |  | 1 | CAPACITY | WALDORF
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 330 | 264.94 |  |  | 4e-05 |  |  | 0 |  | 1 | CAPACITY | X4-035
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | 4e-05 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | 4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | WALDORF
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | 4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | X4-035
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | 4e-05 |  |  | 0 |  | 1 | CAPACITY | X4-035
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 140.6 | 112.88 |  |  | 4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | 4e-05 |  |  | 0.10478 |  | 1 | ENERGY
917371 | Z2-060 | 230 | 233 | 58 | 0 | 116 | 93.13 |  |  | 4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 91.2 |  |  | 4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 83.5 |  |  | 4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 0 |  |  | 5e-05 |  |  | 0 |  | 1 | NEWENERGY | AC2-101
920642 | AA2-170 E | 230 | 233 | 58 | 0 | 19.1 | 0 |  |  | 4e-05 |  |  | 0.04435 |  | 1 | NEW | AA2-170
920641 | AA2-170 C | 230 | 233 | 58 | 0 | 92 | 73.86 |  |  | 4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-170
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 0 |  |  | 5e-05 |  |  | 0 |  | 1 | NEWENERGY | AC2-120
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
227024 | SMECOCT | 13.8 | 238 | 57 | 30 | 80.2 | 64.39 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 64.23 |  |  | 4e-05 |  |  | 0 |  | 1 | CAPACITY | PANDA
220905 | CRANE GT | 4.16 | 232 | 55 | 0 | 14 | 0 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | NEW
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 41.75 |  |  | 4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | ENERGY
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | 4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | PANDA
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | 4e-05 |  |  | 0 |  | 1 | CAPACITY | PANDA
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.5 | 24.49 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 30 | 24.08 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 19.59 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 14.45 |  |  | 5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | 4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | 4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
226915 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 9.92 |  |  | 5e-05 |  |  | 0 |  | 1 | CAPACITY | AC2-101
226912 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 8.39 |  |  | 5e-05 |  |  | 0 |  | 1 | CAPACITY | AC2-120
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0 |  |  | 5e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-157
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.69 |  |  | 5e-05 |  |  | 0 |  | 1 | CAPACITY
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.21 |  |  | 4e-05 |  |  | 0 |  | 1 | CAPACITY
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.76 |  |  | 5e-05 |  |  | 0 |  | 1 | CAPACITY
925011 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.64 |  |  | 5e-05 |  |  | 0 |  | 1 | CAPACITY | AB2-157
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 0 |  |  | 3e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-129
924771 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 0 |  |  | 3e-05 |  |  | 0 |  | 1 | NEW | AB2-129
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | 3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | 3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 41.75 |  |  | 3e-05 |  |  | 0.10478 |  | 1 | CAPACITY
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 14.45 |  |  | 3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0 |  |  | 4e-05 |  |  | 0 |  | 1 | NEWENERGY | AA2-072
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 245.67 |  |  | 3e-05 |  |  | 0 |  | 1 | CAPACITY | X4-039
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 201.52 |  |  | 2e-05 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | 3e-05 |  |  | 0 |  | 1 | CAPACITY | X4-039
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | 3e-05 |  |  | 0.04435 |  | 1 | CAPACITY | X4-039
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | 2e-05 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | 2e-05 |  |  | 0.04435 |  | 1 | CAPACITY | POSSUM POINT
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | 2e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | 2e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 28.74 |  |  | 2e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 28.66 |  |  | 2e-05 |  |  | 0.10478 |  | 1 | CAPACITY
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | 2e-05 |  |  | 0 |  | 1 | NEWENERGY | AC2-072
314088 | 6VANDORN | 230 | 345 | 2 | 7 | 21 | 16.86 |  |  | 2e-05 |  |  | 0 |  | 1 | CAPACITY
932521 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | 2e-05 |  |  | 0 |  | 1 | CAPACITY | AC2-072
313821 | 6PACIFIC | 230 | 345 | 75 | 0 | 0.09 | 0 |  |  | 2e-05 |  |  | 0 |  | 1 | NEWENERGY
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 761.83 |  |  | 1e-05 |  |  | 0.01494 |  | 1 | CAPACITY
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 761.51 |  |  | 1e-05 |  |  | 0.01494 |  | 1 | CAPACITY
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 2
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 1
315033 | 1BIRCHWDA | 18 | 345 | 13 | 85 | 238 | 191.08 |  |  | 2e-05 |  |  | 0.10478 |  | 1 | CAPACITY
926737 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-158 1
926738 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-158 2
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | 2e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | 2e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 128.94 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 128.86 |  |  | 2e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 128.54 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 128.3 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 152.3 | 122.28 |  |  | 2e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | 2e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | 2e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 120.19 |  |  | 2e-05 |  |  | 0.10478 |  | 1 | CAPACITY
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-158
316149 | AD1-046 E | 230 | 345 | 75 | 0 | 20.5 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AD1-044
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | W4-102
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 0 |  |  | 2e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-029
925021 | AB2-158 C | 230 | 345 | 75 | 0 | 61 | 48.97 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AB2-158
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
235002 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0 |  |  | 2e-05 |  |  | 0 |  | 1 | NEW | AC1-039
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-097
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0 |  |  | 2e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-039
923213 | AB1-125 E OP | 34.5 | 201 | 75 | 0 | 9.3 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | 2e-05 |  |  | 0 |  | 1 | NEWENERGY | W1-116
237799 | 01AA2-159 C | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
923202 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
920562 | AA2-159 E | 34.5 | 201 | 75 | 0 | 7.3 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
923192 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-118
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AE1-124
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0 |  |  | 2e-05 |  |  | 0 |  | 1 | NEWENERGY | AC2-136
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-096
316148 | AD1-046 C | 230 | 345 | 75 | 0 | 30.7 | 24.65 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AD1-044
923212 | AB1-125 C OP | 34.5 | 201 | 75 | 0 | 5.7 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
923872 | AB2-027 E | 34.5 | 201 | 75 | 0 | 5.5 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-027
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0 |  |  | 2e-05 |  |  | 0 |  | 1 | NEWENERGY | AA1-109
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AA1-092
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AA1-095
235006 | AB2-027 C | 34.5 | 201 | 75 | 0 | 3.3 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEW | AB2-027
938961 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AE1-124
314078 | 3REMNGTN | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | 2e-05 |  |  | 0 |  | 1 | CAPACITY | AB2-029
314766 | 6LOUISA | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY
314190 | 6WESTMOR | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-118
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 6.98 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 6.42 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AA1-092
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | W4-102
933251 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 4.41 |  |  | 2e-05 |  |  | 0 |  | 1 | CAPACITY | AC2-136
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 4.27 |  |  | 2e-05 |  |  | 0 |  | 1 | CAPACITY | W1-116
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 3.61 |  |  | 2e-05 |  |  | 0 |  | 1 | CAPACITY | AA1-109
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 0.68 | 0 |  |  | 2e-05 |  |  | 0 |  | 1 | NEWENERGY
930521 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 2.49 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AB1-096
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 2.33 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AA1-095
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 2.09 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 1.61 |  |  | 2e-05 |  |  | 0 |  | 1 | CAPACITY
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.88 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEW | AC1-107
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEW | AC1-107
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | 1e-05 |  |  | 0.04435 |  | 1 | NEW | AC1-107
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | Z1-036
901082 | W1-029 E | 230 | 345 | 74 | 0 | 261 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | W1-029
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY | K11
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 678.09 |  |  | 0 |  |  | 0.01494 |  | 1 | CAPACITY
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 677.21 |  |  | 0 |  |  | 0.01494 |  | 1 | CAPACITY
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 788.9 | 633.38 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 480.11 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 452.01 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 443.98 |  |  | -1e-05 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM2
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 440.13 |  |  | -1e-05 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM1
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 422.86 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 419.81 |  |  | -1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 404.48 |  |  | -1e-05 |  |  | 0.0316 |  | 1 | CAPACITY
926785 | AC1-164 E | 0.44 | 345 | 75 | 0 | 99.2 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-164
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 403.68 |  |  | -1e-05 |  |  | 0.0316 |  | 1 | CAPACITY
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 403.27 |  |  | -1e-05 |  |  | 0.0316 |  | 1 | CAPACITY
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 403.2 |  |  | -1e-05 |  |  | 0.0316 |  | 1 | CAPACITY
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -1e-05 |  |  | 0.0316 |  | 1 | CAPACITY
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -1e-05 |  |  | 0.0316 |  | 1 | CAPACITY
316114 | AB2-068 ST | 22 | 345 | 58 | 0 | 492 | 395.01 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AB2-068
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.5 | 354.46 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 350.93 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
923262 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY | T157
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 322.35 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315616 | AA1-038 C | 230 | 345 | 74 | 0 | 76.6 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEW | AA1-038
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-134
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | 0 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-086
918232 | AA1-038 E | 230 | 345 | 74 | 0 | 66.7 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY | AA1-038
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AA2-088
316113 | AB2-068 CT2 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316112 | AB2-068 CT1 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | 1e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-068
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | 1e-05 |  |  | 0.04435 |  | 1 | CAPACITY | WARREN COUNTY CC
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | 0 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNSWICK COUNTY
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEW | AB2-015
314860 | 4E MILL | 138 | 345 | 2 | 0 | 50 | 0 |  |  | -1e-05 |  |  | 0.10478 |  | 1 | ENERGY
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-160
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY | Z2-088
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 198.31 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-190
923991 | AB2-040 C O1 | 115 | 345 | 75 | 0 | 44 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEW | AB2-040
926784 | AC1-164 C | 0.44 | 345 | 75 | 0 | 220.8 | 177.27 |  |  | 1e-05 |  |  | 0 |  | 1 | NEW | AC1-164
315085 | 1SPRUNCC | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | NEW
315086 | 1SPRUNCD | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | NEW
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-015
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | ENERGY
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-174
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | 0 |  |  | 0.04435 |  | 1 | CAPACITY | BEAR GARDEN
314189 | 6PAPERMILL | 230 | 345 | 1 | 12 | 37 | 0 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | ENERGY
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AA1-139
923992 | AB2-040 E O1 | 115 | 345 | 75 | 0 | 36 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-040
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | 0 |  |  | 0.04435 |  | 1 | CAPACITY | FLUVANNA
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | 0 |  |  | 0.10478 |  | 1 | ENERGY
925122 | AB2-169 E | 115 | 345 | 75 | 0 | 35 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-169
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-059
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 136.49 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 126.85 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-065
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-161
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-043
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 104.93 |  |  | 1e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 7
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-060
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 103.25 |  |  | 1e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 8
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 101.16 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
314525 | 6KINGFORK | 230 | 345 | 75 | 0 | 24.3 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AA2-178
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AA1-065
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AA1-063A
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-081
314550 | 6HICKORY | 230 | 345 | 75 | 0 | 22.93 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AA2-053
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 89.92 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AB2-190
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 88.96 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | 0 |  |  | 0.07484 |  | 1 | CAPACITY
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | 0 |  |  | 0.07484 |  | 1 | CAPACITY
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 87.83 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | 1e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 5
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | 1e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 6
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 86.31 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
919702 | AA2-057 E OP | 115 | 345 | 75 | 0 | 21.1 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AA2-057
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AC1-054
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AD1-085
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 69.77 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 69.69 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 69.05 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-105
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 68.97 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 68.72 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 68.64 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 2
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 1
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | 1e-05 |  |  | 0.04435 |  | 1 | CAPACITY | HOPEWELL HCF
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 63.18 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AA1-139
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 61.9 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 76.6 | 61.5 |  |  | 0 |  |  | 0.04435 |  | 1 | CAPACITY | ROSEMARY
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 57.65 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-134
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 53.15 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 52.99 |  |  | -1e-05 |  |  | 0 |  | 1 | CAPACITY | AB2-059
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | Y1-086
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB1-128
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB1-127
314466 | 6FENTRES | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314632 | 6AYDLETOLD | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
313717 | 6SLIGO L2192 | 230 | 345 | 75 | 0 | 12.34 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314331 | 6POE | 230 | 345 | 75 | 0 | 12.27 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 48.17 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 44.96 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AA2-178
922922 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 44.96 |  |  | -1e-05 |  |  | 0 |  | 1 | CAPACITY | AB1-081
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 44 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AA2-053
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 43.67 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-060
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 53.6 | 43.03 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AA1-065
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | Z1-068
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 53 | 42.55 |  |  | -1e-05 |  |  | 0 |  | 1 | CAPACITY | Z2-088
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 40.87 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AA1-063A
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 40.38 |  |  | 0 |  |  | 0.07484 |  | 1 | CAPACITY
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 40.14 |  |  | 0 |  |  | 0.19858 |  | 1 | CAPACITY
314713 | 3PAMPLIN | 115 | 345 | 75 | 0 | 9.73 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314807 | 3MT JACK | 115 | 345 | 75 | 0 | 9.7 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 38.54 |  |  | 0 |  |  | 0.07484 |  | 1 | CAPACITY
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 47.5 | 38.13 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AD1-060
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AC1-036
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | 1e-05 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 2
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | 1e-05 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 1
316143 | AD1-160 E | 115 | 345 | 75 | 0 | 9.1 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AD1-160
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 36.61 |  |  | -1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
313719 | 3CHESTNUT | 115 | 345 | 75 | 0 | 44.7 | 35.89 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AA2-057
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 35.73 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AC1-054
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | 0 |  |  | 0.08446 |  | 1 | CAPACITY
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | 0 |  |  | 0.08446 |  | 1 | CAPACITY
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 33.72 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-174
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -1e-05 |  |  | 0.07484 |  | 1 | CAPACITY
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -1e-05 |  |  | 0.07484 |  | 1 | CAPACITY
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -1e-05 |  |  | 0.07484 |  | 1 | CAPACITY
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -1e-05 |  |  | 0.07484 |  | 1 | CAPACITY
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -1e-05 |  |  | 0.07484 |  | 1 | CAPACITY
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -1e-05 |  |  | 0.07484 |  | 1 | CAPACITY
925863 | AC1-065 C | 0.39 | 345 | 75 | 0 | 41.8 | 33.56 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-065
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AE1-162
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-077
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-078
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-079
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 32.44 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB1-173
935212 | AD1-156 E | 230 | 345 | 75 | 0 | 7.92 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AD1-156
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AC1-116
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | W1-029
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | Z1-036
925121 | AB2-169 C | 115 | 345 | 75 | 0 | 39 | 31.31 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-169
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 30.67 |  |  | -1e-05 |  |  | 0 |  | 1 | CAPACITY | K11
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 30.51 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AA2-088
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AC2-137
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AC1-147
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 35.9 | 28.82 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-022
316145 | AE1-027 E | 230 | 345 | 75 | 0 | 6.9 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AE1-027
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 27.7 |  |  | -1e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-105
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AD2-030
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AE1-074
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AC2-071
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AC2-196
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-100 2
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-100 1
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AC1-027
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-045
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB1-173
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-024
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-026
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | Z2-030
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AC2-174
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-025
314608 | 3TARBORO | 115 | 345 | 75 | 0 | 6.2 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-112
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AC2-138
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-027
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AD1-063
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | Z2-027
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AD1-157
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 24.41 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-160
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AE1-075
314574 | 6EVERETS | 230 | 345 | 75 | 0 | 5.89 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 23.76 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AD1-144
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AE1-098
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AE1-099
316158 | AD2-164 | 230 | 345 | 57 | 0 | 26.7 | 21.44 |  |  | 0 |  |  | 0.08446 |  | 1 | CAPACITY
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AC2-074
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AD2-215
314578 | 3HORNRTN | 115 | 345 | 75 | 0 | 5.15 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 20.23 |  |  | -1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 20.15 |  |  | -1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 19.99 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | South Anna 1
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | South Anna 2
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 19.27 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
314589 | 3MURPHYS | 115 | 345 | 75 | 0 | 4.66 | 0 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | V4-068
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AA1-067
316147 | AE1-028 E | 230 | 345 | 75 | 0 | 4.4 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AE1-028
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 16.46 |  |  | -1e-05 |  |  | 0 |  | 1 | CAPACITY | T157
314541 | 3WATKINS | 115 | 345 | 1 | 0 | 4 | 0 |  |  | 0 |  |  | 0 |  | 1 | ENERGY
313853 | 3PONTONDP | 115 | 345 | 2 | 0 | 4 | 0 |  |  | 0 |  |  | 0 |  | 1 | ENERGY
314333 | 6POWHATN | 230 | 345 | 75 | 0 | 3.97 | 0 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-026
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 16.06 |  |  | 1e-05 |  |  | 0.12623 |  | 1 | CAPACITY
314579 | 6HORNRTN | 230 | 345 | 75 | 0 | 3.91 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY | AC2-070
933571 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEW | AC2-174
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 15.25 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-161
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 15.17 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-043
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY | Z2-044
314651 | 6WINFALL | 230 | 345 | 75 | 0 | 3.35 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314645 | 6SLIGO L269 | 230 | 345 | 75 | 0 | 3.22 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.3 | 13.09 |  |  | 1e-05 |  |  | 0.12623 |  | 1 | CAPACITY
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 16 | 12.85 |  |  | 0 |  |  | 0.12623 |  | 1 | CAPACITY
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 12.2 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 12.04 |  |  | 0 |  |  | 0.12623 |  | 1 | CAPACITY
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 12.04 |  |  | 1e-05 |  |  | 0.12623 |  | 1 | CAPACITY
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 12.04 |  |  | -1e-05 |  |  | 0.07484 |  | 1 | CAPACITY
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 11.96 |  |  | 1e-05 |  |  | 0.12623 |  | 1 | CAPACITY
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 11.96 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
938551 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AE1-074
932511 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AC2-071
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AD2-030
316144 | AE1-027 C | 230 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AE1-027
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 10.44 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-022
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 10.36 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
314623 | 3WITAKRS | 115 | 345 | 75 | 0 | 2.51 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | CAPACITY | Z2-044
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEW
926661 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 10.12 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AC1-147
314266 | 6NORTHAMPTON | 230 | 345 | 75 | 0 | 2.47 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 9.88 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AD1-085
316258 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AE1-162
938561 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AE1-075
924301 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | 0 |  |  | 0 |  | 1 | NEW | AB2-077
924311 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | 0 |  |  | 0 |  | 1 | NEW | AB2-078
924321 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | 0 |  |  | 0 |  | 1 | NEW | AB2-079
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 9.55 |  |  | 0 |  |  | 0.10478 |  | 1 | CAPACITY
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 9.55 |  |  | -1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
935211 | AD1-156 C | 230 | 345 | 75 | 0 | 11.82 | 9.49 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AD1-156
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 11.4 | 9.15 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AC2-137
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 9.05 |  |  | 0 |  |  | 0.12623 |  | 1 | CAPACITY
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 8.83 |  |  | 1e-05 |  |  | 0.12623 |  | 1 | CAPACITY
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 8.83 |  |  | 0 |  |  | 0.12623 |  | 1 | CAPACITY
314172 | 6DUNNSVL | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY
314375 | 6CORRCTN | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AB2-024
314533 | 6SMITFLD | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314435 | 6SAPONY | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-025
314603 | 3SCOT NK | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314617 | 3TUNIS | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314593 | 3PARMELE | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314187 | 3WAN 176 | 115 | 345 | 75 | 0 | 2.12 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY
314677 | 6BUCKING | 230 | 345 | 75 | 0 | 2.12 | 0 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-045
932541 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AC2-074
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AE1-099
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AE1-098
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 8.03 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY
933731 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 8.03 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AC2-196
316150 | AD2-215 C | 230 | 345 | 76 | 0 | 9.8 | 7.87 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AD2-215
935111 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 7.79 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AD1-144
314491 | 3PENDLTN | 115 | 345 | 75 | 0 | 1.89 | 0 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AC1-027
314241 | 6OLDCHRC | 230 | 345 | 75 | 0 | 1.82 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AB1-027
932501 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 7.39 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AC2-070
934391 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 7.23 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AD1-063
935221 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 7.23 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AD1-157
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | V4-068
925611 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 6.9 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AC1-036
314176 | 6HARMONY | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY
314637 | 6EDENTON | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AA2-059
314568 | 3EARLEYS | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314554 | 3BTLEBRO | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY
314566 | 3CRESWEL | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AB2-099
316146 | AE1-028 C | 230 | 345 | 75 | 0 | 7.6 | 6.1 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AE1-028
235041 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB1-128
235040 | 01AB1-127 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB1-127
942852 | AE2-304 E | 230 | 345 | 75 | 0 | 1.4 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY | AE2-304
316142 | AD1-160 C | 115 | 345 | 75 | 0 | 6.6 | 5.3 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AD1-160
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 6.3 | 5.06 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AC2-138
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 4.98 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY
314559 | 3CAROLNA | 115 | 345 | 75 | 0 | 1.21 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
934362 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 4.58 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY | AD1-060
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 4.41 |  |  | -1e-05 |  |  | 0 |  | 1 | CAPACITY
314648 | 6SUNBURY | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314620 | 6CASHIE | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314551 | 3AHOSKIE | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314626 | 3WOODLND | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314596 | 3POPLR C | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314582 | 3KELFORD | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | Z2-043
314557 | 3BETHELC | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY
314549 | 3TOT1 | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 3.93 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY
926451 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 3.77 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AC1-116
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 3.61 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 3.21 |  |  | 1e-05 |  |  | 0 |  | 1 | CAPACITY
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 3.05 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | Z2-030
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 2.81 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AB2-099
942851 | AE2-304 C | 230 | 345 | 75 | 0 | 3.3 | 2.65 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | AE2-304
314734 | 6CASHSCORNER | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY
314638 | 6ELIZ CT | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | Y1-086
314662 | 6S HERTFORD | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314594 | 6PLYMOTH | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314604 | 3SEABORD | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314762 | 3JAMES R | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314607 | 3TAR RVR | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY
314205 | 3HEARTS | 115 | 345 | 75 | 0 | 0.41 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 1.61 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY
314639 | 6TANGLEW | 230 | 345 | 75 | 0 | 0.32 | 0 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | Z2-027
314545 | 3TOT5 | 115 | 345 | 75 | 0 | 0.32 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY
314177 | 3HAYES89 | 115 | 345 | 75 | 0 | 0.31 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.2 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY | Z1-068
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 1.04 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY
314294 | 6ENON | 230 | 345 | 75 | 0 | 0.23 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY
314629 | 3MARTNCO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314560 | 3CNETO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY
314798 | 3MERCK5 | 115 | 345 | 75 | 0 | 0.16 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.64 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.56 |  |  | 0 |  |  | 0 |  | 1 | CAPACITY
313812 | 6ROCKLANDING | 230 | 345 | 75 | 0 | 0.11 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314453 | 6CHRHLND | 230 | 345 | 75 | 0 | 0.08 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
313828 | 3WHITEMARSH | 115 | 345 | 75 | 0 | 0.05 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY
313826 | 6HYDRAULIC | 230 | 345 | 75 | 0 | 0.04 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314640 | 6KITTY HAWK | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314487 | 3MCLAUGH | 115 | 345 | 75 | 0 | 0.01 | 0 |  |  | 0 |  |  | 0 |  | 1 | NEWENERGY
314222 | 6HANOVER | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY
314213 | 3CARVER | 115 | 345 | 75 | 0 | 0 | 0 |  |  | 1e-05 |  |  | 0 |  | 1 | NEWENERGY
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 1044 |  |  |  | 0
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 68.3 |  |  |  | 0
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 154.95 |  |  | -2e-05 |  |  | 0.0316 |  | 1 | CAPACITY
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 152.54 |  |  | -2e-05 |  |  | 0.0316 |  | 1 | CAPACITY
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 0 |  |  | -2e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-145
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 97.14 |  |  | -2e-05 |  |  | 0.0316 |  | 1 | CAPACITY
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-075
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 59.41 |  |  | -2e-05 |  |  | 0.0316 |  | 1 | CAPACITY
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 57 |  |  | -2e-05 |  |  | 0.0316 |  | 1 | CAPACITY
244012 | 05PINNACLE | 4 | 205 | 1 | 0 | 11 | 0 |  |  | -2e-05 |  |  | 0.10478 |  | 1 | ENERGY
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 42.07 |  |  | -2e-05 |  |  | 0.10478 |  | 1 | CAPACITY
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.9 | 40.06 |  |  | -2e-05 |  |  | 0.07484 |  | 1 | CAPACITY
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 30.75 |  |  | -1e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-075
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 0 |  |  | -1e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-080
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 23.68 |  |  | -1e-05 |  |  | 0.12623 |  | 1 | CAPACITY
926645 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 15.25 |  |  | -2e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-145
926023 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 10.28 |  |  | -1e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-080
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 3.21 |  |  | -2e-05 |  |  | 0 |  | 1 | CAPACITY
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | U2-073 A
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | Y1-006
235520 | 01WVACO_S38 | 13.8 | 201 | 2 | 0 | 60 | 0 |  |  | -2e-05 |  |  | 0 |  | 1 | NEW
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | S14
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | U2-030
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | U2-073 B
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 144.51 |  |  | -2e-05 |  |  | 0.10478 |  | 1 | CAPACITY
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0 |  |  | -2e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-117
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0 |  |  | -2e-05 |  |  | 0 |  | 1 | NEWENERGY | AD1-018
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | -2e-05 |  |  | 0.05 |  | 1 | MTX | AA1-100
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
913034 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEW | Y1-006
242677 | 05INDDRV | 138 | 205 | 64 | 0 | 45 | 36.13 |  |  | -3e-05 |  |  | 0.12623 |  | 1 | CAPACITY
926461 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0 |  |  | -2e-05 |  |  | 0 |  | 1 | NEW | AC1-117
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0 |  |  | -2e-05 |  |  | 0 |  | 1 | NEW | AD1-018
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -3e-05 |  |  | 0.07484 |  | 1 | CAPACITY
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -3e-05 |  |  | 0.07484 |  | 1 | CAPACITY
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | -3e-05 |  |  | 0.07484 |  | 1 | ENERGY
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 25.9 | 20.79 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY | U2-073 A
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | MTX | AD2-205
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 15 | 12.04 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY | U2-073 B
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 14.1 | 11.32 |  |  | -3e-05 |  |  | 0.07484 |  | 1 | CAPACITY
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 11.24 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY | S14
923762 | AB2-010 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-010
923761 | AB2-010 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEW | AB2-010
923772 | AB2-011 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-011
923771 | AB2-011 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEW | AB2-011
270148 | AE1-018 E | 138 | 205 | 75 | 0 | 2.2 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | AE1-018
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 8.59 |  |  | -2e-05 |  |  | 0 |  | 1 | CAPACITY | N47
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.7 | 7.79 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 6.42 |  |  | -2e-05 |  |  | 0 |  | 1 | CAPACITY
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 6.26 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY | U2-030
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 3.29 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY
270147 | AE1-018 C | 138 | 205 | 75 | 0 | 2.8 | 2.25 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY | AE1-018
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 896 |  |  |  | 0
237085 | AD2-192 GEN | 23 | 201 | 57 | 0 | 600 | 0 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | NEW
293798 | W4-005 E | 0.69 | 222 | 74 | 0 | 305.37 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | W4-005
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1396 | 1120.79 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | GVG2
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1371 | 1100.72 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | GVG1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1088.67 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | RKG1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1356 | 1088.67 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | MTG1
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1067.8 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | AMG3
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1043.71 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | RKG2
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 949.78 |  |  | -4e-05 |  |  | 0.01494 |  | 1 | CAPACITY
274656 | BYRON ;1U | 25 | 222 | 45 | 700 | 1168.5 | 938.14 |  |  | -4e-05 |  |  | 0.01494 |  | 1 | CAPACITY
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 926.5 |  |  | -4e-05 |  |  | 0.01494 |  | 1 | CAPACITY
274657 | BYRON ;2U | 25 | 222 | 45 | 700 | 1141.5 | 916.46 |  |  | -4e-05 |  |  | 0.01494 |  | 1 | CAPACITY
274661 | LASCO STA;2U | 25 | 222 | 49 | 150 | 1135.9 | 911.97 |  |  | -4e-05 |  |  | 0.01494 |  | 1 | CAPACITY
274660 | LASCO STA;1U | 25 | 222 | 49 | 150 | 1131.2 | 908.19 |  |  | -4e-05 |  |  | 0.01494 |  | 1 | CAPACITY
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 200 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Q57
918472 | AA1-062 E | 138 | 201 | 74 | 0 | 195 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AA1-062
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | X2-022
274663 | QUAD CITI;2U | 18 | 222 | 48 | 150 | 911.7 | 731.97 |  |  | -4e-05 |  |  | 0.01494 |  | 1 | CAPACITY
274662 | QUAD CITI;1U | 18 | 222 | 48 | 150 | 911.1 | 731.48 |  |  | -4e-05 |  |  | 0.01494 |  | 1 | CAPACITY
274658 | DRESDEN ;2U | 18 | 222 | 48 | 150 | 902.5 | 724.58 |  |  | -4e-05 |  |  | 0.01494 |  | 1 | CAPACITY
274659 | DRESDEN ;3U | 18 | 222 | 48 | 150 | 895.5 | 718.96 |  |  | -4e-05 |  |  | 0.01494 |  | 1 | CAPACITY
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  |  |  | 0
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Z2-087
930042 | AB1-006 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-006
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | U3-002 2
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | V3-007
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | U2-090
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | O50
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 159.7 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | S06
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Q01 3
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  |  |  | 0
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | S27
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | S28
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | O22 2
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 642.29 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 642.29 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | P10
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 589.3 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | ZIMM
293799 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | S36
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | S37
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  |  |  | 0
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 570.03 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AA1-018
235586 | 01HARRN2 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
235587 | 01HARRN3 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
235585 | 01HARRN1 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Q01 4
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 124 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | ENERGY | L05_CE22
253314 | AC1-085 A_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 A
253317 | AC1-085 B_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 B
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 489.98 |  |  | -3e-05 |  |  | 0.10478 |  | 1 | CAPACITY
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | O51 2
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | O51 1
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | N15
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 470.47 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | ZIMM
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AC2-176
927091 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-204
927093 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-204
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 443.18 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 437.96 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 415.88 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 415.88 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 409.46 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
274687 | WILL CNTY;4U | 20 | 222 | 15 | 0 | 510 | 409.46 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | WILL4
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | P36 2
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | P36 1
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | S71
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-089
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | O29 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | P26
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | P59
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | M24
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Q01 21
293516 | O-009 E1 | 0.69 | 222 | 74 | 0 | 82.04 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | O09 1
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 81.6 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | O22 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | P11 2
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | P11 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | P46
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 80 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | T126 3
247943 | T-127 E | 0.74 | 205 | 74 | 0 | 80 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | T127 5
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 80 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | T127 4
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 80 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | T126 2
247903 | 05FR-22G E | 0.69 | 205 | 75 | 0 | 78.8 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Q01 22
247900 | 05FR-11G E | 0.6 | 205 | 75 | 0 | 78.3 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Q01 11
930062 | AB1-014 E | 138 | 212 | 75 | 0 | 77.5 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-014
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 522.66 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Q01 12
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 284.53 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK8
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | W2-048
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 263.34 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK7
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-169
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 62.8 |  |  |  | 0
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 244.87 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | O35
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 240.86 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | K28
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 294 | 236.04 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-079
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 225.6 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | O29 2
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | NQ71
293518 | O-009 E3 | 0.57 | 222 | 74 | 0 | 45.89 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | O09 3
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 45.5 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Z1-073
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AB1-169
916211 | Z1-072 E | 0.6 | 222 | 74 | 0 | 44.8 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Z1-072
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 180.64 |  |  | -3e-05 |  |  | 0.10478 |  | 1 | CAPACITY
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | O29 3
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-150
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | U2-061
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 219 | 175.82 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Z1-079
293517 | O-009 E2 | 0.6 | 222 | 74 | 0 | 41.67 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | O09 2
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 38 |  |  |  | 0
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 2
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
274708 | KENDALL ;3C | 18 | 222 | 58 | 140 | 184.3 | 147.97 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 3
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 146.36 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 2
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 146.36 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 138 | 182.3 | 146.36 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 4
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 144.51 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
247225 | 05FTHLG2 | 18 | 205 | 57 | 120 | 173.8 | 139.54 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247224 | 05FTHLG1 | 18 | 205 | 57 | 120 | 173.7 | 139.46 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 2
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 1
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247231 | 05RIVRG2 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247232 | 05RIVRG3 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247230 | 05RIVRG1 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 136.16 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | NELSON
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 135.12 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | NELSON
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 134.32 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 134.16 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 132.47 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 131.75 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | -3e-05 |  |  | 0.05 |  | 1 | MTX | M24 BAT
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 130.06 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | CORDOVA
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 31.5 |  |  |  | 0
919221 | AA1-146 | 345 | 222 | 58 | 0 | 157 | 126.05 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
292981 | N-007 E | 138 | 201 | 74 | 0 | 30.4 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | N07
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
235801 | 01WM_AA1_062 | 138 | 201 | 74 | 0 | 29 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEW | AA1-062
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | ENERGY
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 127.4 | 102.28 |  |  | -3e-05 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 101.08 |  |  | -3e-05 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | CLIF5
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF2
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | CLIF3
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | CLIF6
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | CLIF1
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | CLIF4
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 99.72 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | KYG1
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 99.47 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | NELSON
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | KYG4
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | KYG2
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | KYG5
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | KYG3
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 98.59 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | NELSON
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 97.87 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Kendall 2
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 97.87 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Kendall 1
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 97.87 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Kendall 4
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 97.87 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Kendall 3
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | K28
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 96.42 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 93.13 |  |  | -3e-05 |  |  | 0.10478 |  | 1 | CAPACITY
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | NQ72
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 115.4 | 92.65 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | EQUISTAR MORRIS
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-048
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 109.5 | 87.91 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 106.7 | 85.67 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 84.78 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 75.6 | 104 | 83.5 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 72.7 | 101.6 | 81.57 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
920072 | AA2-103 E | 138 | 201 | 76 | -20 | 20 | 0 |  |  | -4e-05 |  |  | 0.05 |  | 1 | MTX | AA2-103
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -4e-05 |  |  | 0.05 |  | 1 | MTX | AA2-123
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -4e-05 |  |  | 0.05 |  | 1 | MTX | Z1-108
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -4e-05 |  |  | 0.05 |  | 1 | MTX | Z1-107
276592 | O-012 C | 138 | 222 | 64 | 0 | 20 | 0 |  |  | -4e-05 |  |  | 0.12623 |  | 1 | ENERGY
902531 | W2-040 C | 69 | 209 | 75 | 0 | 20 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEW | W2-040
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 80.93 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 71.2 | 100.6 | 80.77 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 80.69 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 133.1 | 153 | 133.28 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 80.21 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 129.7 | 149.1 | 129.88 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 128.6 | 147.8 | 128.75 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
243415 | 05WWVSTA | 69 | 205 | 61 | 60 | 96 | 77.08 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 67.52 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 65.51 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 81.5 | 65.43 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.8 | 64.87 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 64.31 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 64.23 |  |  | -3e-05 |  |  | 0.07484 |  | 1 | CAPACITY
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 64.23 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 62.14 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
250166 | HLCRST AB114 | 138 | 212 | 75 | 0 | 76 | 61.02 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AB1-014
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-085 B
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-085 A
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 60.94 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 60.78 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 60.7 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 60.53 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | CLIF2
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF3
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF5
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF6
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF1
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF4
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 58.77 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 72.9 | 58.53 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 58.45 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | KYG1
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 72.6 | 58.29 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | KYG4
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | KYG5
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY | KYG2
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | KYG3
251957 | 08MADSN6 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
251953 | 08MADSN2 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
251959 | 08MADSN8 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
251958 | 08MADSN7 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
251955 | 08MADSN4 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
251952 | 08MADSN1 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
251956 | 08MADSN5 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
251954 | 08MADSN3 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 56.84 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 56.2 |  |  | -3e-05 |  |  | 0.07484 |  | 1 | CAPACITY
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 55.4 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEW | AC1-048
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 52.91 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
205910 | AC2-053 E | 0.39 | 227 | 74 | 0 | 12.4 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | AC2-053
902532 | W2-040 E | 69 | 209 | 75 | 0 | 12.4 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | W2-040
251828 | CLNTESP1 | 34.5 | 212 | 76 | 0 | 12 | 0 |  |  | -4e-05 |  |  | 0.05 |  | 1 | MTX | Z1-080
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 48.09 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 47.93 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 46.65 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 46.41 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
926103 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 45.76 |  |  | -4e-05 |  |  | 0.05 |  | 1 | NEW | AC1-089
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 55 | 44.16 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 43.03 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | 0
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -4e-05 |  |  | 0.05 |  | 1 | MTX | Z1-106
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -4e-05 |  |  | 0.05 |  | 1 | MTX | Z1-106
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 40.54 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | MIDDLETOWN COKE
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 37.49 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 36.93 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 36.61 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | W4-005
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Q57
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | O50
205909 | AC2-053 C | 0.39 | 227 | 74 | 0 | 7.6 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEW | AC2-053
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 28.74 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | S28
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 28.18 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | O22 2
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | S37
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | S36
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 27.94 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | S27
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 42.68 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 42.6 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 42.51 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -4e-05 |  |  | 0.05 |  | 1 | MTX | Z1-065
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 24.08 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
925972 | AC1-073 E | 138 | 201 | 74 | 0 | 5.9 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-073
925971 | AC1-073 C | 138 | 201 | 74 | 0 | 5.8 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEW | AC1-073
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 23.36 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Q01 4
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | X3-005
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 20.3 | 27.6 | 22.16 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 22 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | N15
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 21.68 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 26 | 20.87 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | L05_CE22
274889 | BRIGHTSTK;1U | 0.7 | 222 | 74 | 0 | 26 | 20.87 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Z2-087
930041 | AB1-006 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AB1-006
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | V3-007
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 20.87 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | U2-090
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 20.79 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | S06
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 20.63 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Q01 11
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 20.07 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 19.27 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | S71
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | O51 1
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | O51 2
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 17.58 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | O29 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 17.58 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | P26
293513 | O-009 C1 | 0.69 | 222 | 74 | 0 | 20.5 | 16.46 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | O09 1
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 16.22 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | T127 5
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | P11 2
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | P11 1
274891 | OTTER CRK;1U | 0.69 | 222 | 74 | 0 | 19.5 | 15.66 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AA1-018
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 15.58 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | P46
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 14.77 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | O22 1
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.4 | 13.97 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY | K28
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 22.91 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
933594 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 13.57 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AC2-176
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 12.28 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | T126 3
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | P36 2
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | P36 1
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 12.2 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | T126 2
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 12.04 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY | M24
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 11.88 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -3e-05 |  |  | 0.07484 |  | 1 | CAPACITY
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -3e-05 |  |  | 0.07484 |  | 1 | CAPACITY
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 13.3 | 10.68 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Z1-073
276173 | Z2-081 | 138 | 222 | 2 | 0 | 13.3 | 10.68 |  |  | -4e-05 |  |  | 0.12623 |  | 1 | CAPACITY
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 10.6 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | U3-002 1
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 10.44 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Q01 21
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 10.44 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Q01 22
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 10.36 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 10.28 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | U3-002 2
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Q01 3
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Q01 12
904211 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 9.71 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 9.64 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | O29 2
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 9.47 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | T127 4
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 9.39 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | P59
293515 | O-009 C3 | 0.57 | 222 | 74 | 0 | 11.5 | 9.23 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | O09 3
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 8.91 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | O29 3
904201 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 8.51 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
293514 | O-009 C2 | 0.6 | 222 | 74 | 0 | 10.4 | 8.35 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | O09 2
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 10.3 | 8.27 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | O35
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 8.19 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | P10
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | MTX | AB1-055
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | MTX | Y3-100
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | MTX | Y3-099
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 10 | 8.03 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Z1-072
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.6 | 7.71 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 6.5 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | K19
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | V4-073
235000 | N-007 C | 138 | 201 | 74 | 0 | 7.6 | 6.1 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | N07
295108 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 5.7 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | NQ71
931011 | AB1-150 C | 138 | 201 | 74 | 0 | 6.7 | 5.38 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY | AB1-150
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 5.22 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | U2-061
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 5.14 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
247968 | Z2-115 E | 12 | 205 | 74 | 0 | 1.25 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Z2-115
276159 | W4-082 | 138 | 222 | 64 | 0 | 5.8 | 4.66 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 4.41 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY
342550 | 4BAVARIAN LF | 138 | 320 | 2 | 0 | 4.8 | 3.85 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.8 | 3.85 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 2.73 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | X3-005
342070 | 2PINE GROVE | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY
341584 | 2GRIFFIN | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
295110 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 2.57 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | NQ72
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.55 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
341329 | 2COLESBURG | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
342031 | 2PACTOLUS | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.76 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
341200 | 2BROMLEYEK | 69 | 320 | 2 | 0 | 2 | 1.61 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 1.3 | 1.04 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 1 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Z2-115
342442 | 2W GLASGOW | 69 | 320 | 2 | 0 | 1 | 0.8 |  |  | -3e-05 |  |  | 0 |  | 1 | CAPACITY
904721 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.76 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | V4-073
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1402 |  |  |  | 0
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | U2-072
247919 | U2-041 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | U2-041
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1148 | 921.68 |  |  | -4e-05 |  |  | 0.01494 |  | 1 | CAPACITY
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 814.5 |  |  | -4e-05 |  |  | 0.01494 |  | 1 | CAPACITY
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEWENERGY | V4-010
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 634.42 |  |  | -5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 618.28 |  |  | -4e-05 |  |  | 0.10478 |  | 1 | CAPACITY
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 533.66 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-173
893022 | V2-006 E | 138 | 205 | 74 | 0 | 130.5 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | V2-006
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 120.8 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | R49
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AB2-067
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-067
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-044
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | T131
924440 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 389.39 |  |  | -5e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-093
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 94.4 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | R60 3
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | R60 1
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | R60 2
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | V1-011
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEWENERGY | U4-029
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEWENERGY | U4-028
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-116
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AA2-116
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 292.88 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 268.96 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-173
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 267.35 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AA2-116
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 261.89 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY | OREGON
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 318.8 | 255.95 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | RONCO
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 248.73 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY | AB1-107
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 238.45 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -5e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-107
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 201.52 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | X2-052
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -5e-05 |  |  | 0.04435 |  | 1 | CAPACITY | OREGON
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY | OREGON
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 193.49 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | X2-052
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | X2-052
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 225.4 | 180.96 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | U1-059
247530 | 05COVRT3 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 3
247528 | 05COVRT1 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 1
247529 | 05COVRT2 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 2
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 162.9 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247506 | U2-041 C | 345 | 205 | 74 | 0 | 39 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | U2-041
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | WASHINGTON
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | RONCO
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | RONCO
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | DRESDEN
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -4e-05 |  |  | 0.04435 |  | 1 | CAPACITY | WATERFORD
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AC2-067
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 120.19 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 109.19 |  |  | -5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 106.94 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
247533 | 05COVRT6 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Covert 3
247531 | 05COVRT4 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Covert 1
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEW | V4-010
247532 | 05COVRT5 | 16.5 | 205 | 58 | 90 | 131.2 | 105.33 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Covert 2
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.66 | 96.07 |  |  | -5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEWENERGY
893021 | V2-006 C | 138 | 205 | 74 | 0 | 19.5 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | V2-006
927184 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -4e-05 |  |  | 0.05 |  | 1 | MTX | AC1-212
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-165
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-166
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | W1-056
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 65.03 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-068
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-069
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 64.23 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 63.43 |  |  | -4e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | V3-028
208904 | HOLT 696 | 13.2 | 229 | 60 | 23 | 58.4 | 46.89 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
208903 | HOLT 695 | 13.2 | 229 | 60 | 26 | 53.2 | 42.71 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | U1-059
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 31.31 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | U2-072
247549 | V3-028 C | 345 | 205 | 75 | 0 | 7.6 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | V3-028
930262 | AB1-065 E | 34.5 | 201 | 75 | 0 | 6.8 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-069
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-068
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-165
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-166
932312 | AC2-045 E | 69 | 205 | 75 | 0 | 6.2 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AC2-045
247521 | T131 | 0.69 | 205 | 74 | 22.4 | 30 | 24.08 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | T131
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 21.28 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AC2-067
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -5e-05 |  |  | 0.07484 |  | 1 | CAPACITY
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -5e-05 |  |  | 0.07484 |  | 1 | CAPACITY
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 18.39 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | R49
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 17.66 |  |  | -5e-05 |  |  | 0.08446 |  | 1 | CAPACITY
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -4e-05 |  |  | 0.07484 |  | 1 | CAPACITY
235013 | 01AB1-065 C | 34.5 | 201 | 75 | 0 | 4.1 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | MTX
932311 | AC2-045 C | 69 | 205 | 75 | 0 | 3.8 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEW | AC2-045
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 15.25 |  |  | -5e-05 |  |  | 0.07484 |  | 1 | CAPACITY
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 13.25 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | R60 3
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | R60 1
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | R60 2
919535 | V4-027 E | 0 | 229 | 75 | 0 | 3.1 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | V4-027
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 10.68 |  |  | -5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
247607 | V1-011 C | 34.5 | 205 | 74 | 0 | 13 | 10.44 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | V1-011
247552 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -5e-05 |  |  | 0 |  | 1 | NEW | U4-029
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -5e-05 |  |  | 0 |  | 1 | NEW | U4-028
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 10.19 |  |  | -5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -4e-05 |  |  | 0.12623 |  | 1 | CAPACITY
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -4e-05 |  |  | 0.12623 |  | 1 | CAPACITY
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Z2-113
294740 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | ENERGY
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 8.83 |  |  | -5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 8.03 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
926865 | AC1-173 C | 0.65 | 205 | 75 | 0 | 9.9 | 7.95 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-173
903052 | W2-094 E | 115 | 227 | 75 | 0 | 1.9 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEWENERGY | W2-094
AC1-212 | BATTERY_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | 0
247969 | Z2-116 E | 138 | 205 | 76 | 0 | 1.3 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | Z2-116
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 5.14 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 4.82 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 4.66 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
205911 | 27W2-094 | 115 | 227 | 75 | 0 | 1.1 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEWENERGY | W2-094
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 3.93 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | V4-027
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.61 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
245413 | 05S FULTHA | 69 | 205 | 65 | 0 | 0.85 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | ENERGY
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 3.13 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
208474 | KINZ 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
247604 | X1-042 | 12 | 205 | 64 | 0 | 3 | 2.41 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.8 | 2.25 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 2.09 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.93 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | W1-056
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 1.85 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Z2-113
927183 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.53 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-212
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.5 | 1.2 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 1.04 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | Z2-116
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEW | AB1-069
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEW | AB1-069
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -5e-05 |  |  | 0.04435 |  | 1 | NEW | AB1-069
237082 | AA2-121 | 345 | 201 | 58 | 0 | 830 | 666.37 |  |  | -6e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-121
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 503.47 |  |  | -6e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AVON LAKE
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 498.09 |  |  | -6e-05 |  |  | 0.10478 |  | 1 | CAPACITY
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 780.51 |  |  | -5e-05 |  |  | 0.01494 |  | 1 | CAPACITY
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -6e-05 |  |  | 0.10478 |  | 1 | CAPACITY
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -6e-05 |  |  | 0.10478 |  | 1 | CAPACITY
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 364.2 | 292.4 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY | FREMONT
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 272 | 218.38 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -6e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Y2-050
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 170 | 136.49 |  |  | -5e-05 |  |  | 0.04435 |  | 1 | CAPACITY | FREMONT
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 166.4 | 133.6 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY | FREMONT
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 91.93 |  |  | -6e-05 |  |  | 0.07484 |  | 1 | CAPACITY
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 62.22 |  |  | -6e-05 |  |  | 0.08446 |  | 1 | CAPACITY
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 61.42 |  |  | -6e-05 |  |  | 0.07484 |  | 1 | CAPACITY
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -6e-05 |  |  | 0.08446 |  | 1 | CAPACITY
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -6e-05 |  |  | 0.08446 |  | 1 | CAPACITY
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 60.86 |  |  | -6e-05 |  |  | 0.08446 |  | 1 | CAPACITY
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 60.29 |  |  | -6e-05 |  |  | 0.08446 |  | 1 | CAPACITY
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 60 | 48.17 |  |  | -6e-05 |  |  | 0.08446 |  | 1 | CAPACITY
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 41.03 |  |  | -6e-05 |  |  | 0.12623 |  | 1 | CAPACITY
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 39.82 |  |  | -6e-05 |  |  | 0.12623 |  | 1 | CAPACITY
936011 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 16.06 |  |  | -5e-05 |  |  | 0.10478 |  | 1 | CAPACITY
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 19.5 | 15.66 |  |  | -6e-05 |  |  | 0.08446 |  | 1 | CAPACITY
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 11.24 |  |  | -6e-05 |  |  | 0.12623 |  | 1 | CAPACITY
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 8.03 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 7.95 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 4.41 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY | N32
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 3.21 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 1.85 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY
253900 | 15BVRVL1 | 22 | 215 | 44 | 843.9 | 970 | 844.97 |  |  | -6e-05 |  |  | 0.01494 |  | 1 | CAPACITY
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -6e-05 |  |  | 0.10478 |  | 1 | CAPACITY
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -6e-05 |  |  | 0.10478 |  | 1 | CAPACITY
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 783.39 |  |  | -6e-05 |  |  | 0.01494 |  | 1 | CAPACITY
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 455.62 |  |  | -6e-05 |  |  | 0.10478 |  | 1 | CAPACITY
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 329.17 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | AA1-044
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 261.73 |  |  | -7e-05 |  |  | 0 |  | 1 | CAPACITY | T-174
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | AA1-123
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -7e-05 |  |  | 0.04435 |  | 1 | CAPACITY | T-174
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -7e-05 |  |  | 0 |  | 1 | CAPACITY | T-174
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 300.6 | 241.34 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | Z2-028
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -6e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-044
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | AA1-044
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 233.87 |  |  | -6e-05 |  |  | 0.10478 |  | 1 | CAPACITY
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -6e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-028
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | Z2-028
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -6e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-123
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | AA1-123
239024 | 02NWCAG5 | 16.5 | 202 | 58 | 23 | 141 | 113.2 |  |  | -7e-05 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 81.57 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 77.88 |  |  | -6e-05 |  |  | 0.07484 |  | 1 | CAPACITY
253970 | 15BI2 | 13.8 | 215 | 58 | 60 | 96.2 | 77.24 |  |  | -6e-05 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
239022 | 02NWCAG3 | 14.4 | 202 | 58 | 20 | 92.3 | 74.11 |  |  | -7e-05 |  |  | 0.04435 |  | 1 | CAPACITY | NEW CASTLE
239023 | 02NWCAG4 | 14.4 | 202 | 58 | 20 | 92 | 73.86 |  |  | -7e-05 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | -6e-05 |  |  | 0.10478 |  | 1 | ENERGY
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 0 |  |  | -7e-05 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 51.78 |  |  | -6e-05 |  |  | 0.07484 |  | 1 | CAPACITY
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 51.38 |  |  | -6e-05 |  |  | 0.07484 |  | 1 | CAPACITY
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | Y3-103
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.7 | 39.1 |  |  | -6e-05 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0 |  |  | -6e-05 |  |  | 0 |  | 1 | NEWENERGY | W1-045
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0 |  |  | -6e-05 |  |  | 0 |  | 1 | NEWENERGY | AC2-168
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -6e-05 |  |  | 0.04435 |  | 1 | CAPACITY | Y3-103
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | Y3-103
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 24.6 | 19.75 |  |  | -6e-05 |  |  | 0.12623 |  | 1 | CAPACITY
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 21 | 16.86 |  |  | -6e-05 |  |  | 0.12623 |  | 1 | CAPACITY
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 16.46 |  |  | -7e-05 |  |  | 0.12623 |  | 1 | CAPACITY
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 14.53 |  |  | -6e-05 |  |  | 0.08446 |  | 1 | CAPACITY
208769 | SISO | 12.5 | 229 | 2 | 0 | 2.48 | 0 |  |  | -7e-05 |  |  | 0 |  | 1 | ENERGY
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 0 |  |  | -7e-05 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
933531 | AC2-168 C | 138 | 215 | 75 | 0 | 7.55 | 6.06 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | AC2-168
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.5 |  |  | -7e-05 |  |  | 0 |  | 1 | CAPACITY
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.13 | 4.12 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | W1-045
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 3.21 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY
208876 | WLAN | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -7e-05 |  |  | 0 |  | 1 | CAPACITY
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 2.01 |  |  | -7e-05 |  |  | 0 |  | 1 | CAPACITY
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 1.37 |  |  | -7e-05 |  |  | 0 |  | 1 | CAPACITY | K20
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1086.27 |  |  | -7e-05 |  |  | 0.01494 |  | 1 | CAPACITY
920571 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 411.86 |  |  | -7e-05 |  |  | 0.04435 |  | 1 | NEW | AA2-161
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 19.6 | 15.74 |  |  | -8e-05 |  |  | 0.08446 |  | 1 | CAPACITY
209030 | FRFA O01 | 12.5 | 229 | 2 | 0 | 3.2 | 0 |  |  | -8e-05 |  |  | 0 |  | 1 | NEW
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.82 |  |  | -7e-05 |  |  | 0 |  | 1 | CAPACITY
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 3.05 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 0.4 | 0.32 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY | V3-051
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 353.26 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -8e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-076
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY | AA1-076
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 140 | 182.2 | 146.28 |  |  | -9e-05 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 118.7 | 175.2 | 140.66 |  |  | -9e-05 |  |  | 0.04435 |  | 1 | CAPACITY | AE SPRINGDALE
913142 | Y1-033 E OP1 | 115 | 226 | 74 | 0 | 34.02 | 0 |  |  | -8e-05 |  |  | 0 |  | 1 | NEWENERGY | Y1-033
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 118.7 | 172.2 | 138.25 |  |  | -9e-05 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -9e-05 |  |  | 0.08446 |  | 1 | CAPACITY
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -9e-05 |  |  | 0.08446 |  | 1 | CAPACITY
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 39.5 | 31.71 |  |  | -8e-05 |  |  | 0.08446 |  | 1 | CAPACITY
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 28.1 |  |  | -9e-05 |  |  | 0.10478 |  | 1 | CAPACITY
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 4.01 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY | Y1-033
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 0 |  |  | -0.0001 |  |  | 0 |  | 1 | NEWENERGY | K23
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 0 |  |  | -0.0001 |  |  | 0 |  | 1 | NEWENERGY | L13
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 0 |  |  | -0.0001 |  |  | 0 |  | 1 | NEWENERGY | O48
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | -0.0001 |  |  | 0.05 |  | 1 | MTX
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | -0.0001 |  |  | 0.05 |  | 1 | MTX
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 38.7 | 31.07 |  |  | -0.0001 |  |  | 0.08446 |  | 1 | CAPACITY
204555 | 27QUEEN ST | 115 | 227 | 74 | 0 | 5 | 0 |  |  | -0.0001 |  |  | 0 |  | 1 | NEWENERGY
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 0 |  |  | -0.0001 |  |  | 0 |  | 1 | NEWENERGY | R40
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 5.54 |  |  | -0.0001 |  |  | 0 |  | 1 | CAPACITY
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 5.06 |  |  | -0.0001 |  |  | 0 |  | 1 | CAPACITY | O48
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 4.74 |  |  | -0.0001 |  |  | 0 |  | 1 | CAPACITY | L13
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 5.1 | 4.09 |  |  | -0.0001 |  |  | 0 |  | 1 | CAPACITY | K23
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 853.3 | 685.08 |  |  | -0.0001 |  |  | 0.10478 |  | 1 | CAPACITY | Keys1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 853.1 | 684.92 |  |  | -0.0001 |  |  | 0.10478 |  | 1 | CAPACITY | Keys2
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 682.91 |  |  | -0.0001 |  |  | 0.10478 |  | 1 | CAPACITY | Cone1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 682.43 |  |  | -0.0001 |  |  | 0.10478 |  | 1 | CAPACITY | Cone2
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 400 | 321.14 |  |  | -0.0001 |  |  | 0.04435 |  | 1 | CAPACITY | AD2-114
235619 | 01SBEND1 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.0001 |  |  | 0.08446 |  | 1 | CAPACITY
235622 | 01SBEND4 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.0001 |  |  | 0.08446 |  | 1 | CAPACITY
235621 | 01SBEND3 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.0001 |  |  | 0.08446 |  | 1 | CAPACITY
235620 | 01SBEND2 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.0001 |  |  | 0.08446 |  | 1 | CAPACITY
204638 | 27CAT TRAC | 13.2 | 227 | 58 | 0 | 32.3 | 25.93 |  |  | -0.0001 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 24.08 |  |  | -0.0001 |  |  | 0.10478 |  | 1 | CAPACITY
204706 | 27CAT TRC2 | 13.2 | 227 | 58 | 0 | 13.9 | 11.16 |  |  | -0.0001 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 6.1 |  |  | -0.0001 |  |  | 0 |  | 1 | CAPACITY
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00011 |  |  | 0 |  | 1 | CAPACITY
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00012 |  |  | 0 |  | 1 | NEWENERGY | P60
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 23.2 | 0 |  |  | -0.00012 |  |  | 0 |  | 1 | NEWENERGY | K13
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 68.24 |  |  | -0.00012 |  |  | 0.10478 |  | 1 | CAPACITY
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00012 |  |  | 0.08446 |  | 1 | CAPACITY
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 42.95 |  |  | -0.00012 |  |  | 0.08446 |  | 1 | CAPACITY
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00012 |  |  | 0.08446 |  | 1 | CAPACITY
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 42.95 |  |  | -0.00012 |  |  | 0.08446 |  | 1 | CAPACITY
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00012 |  |  | 0.08446 |  | 1 | CAPACITY
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 24.24 |  |  | -0.00012 |  |  | 0.07484 |  | 1 | CAPACITY
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 16.55 |  |  | -0.00012 |  |  | 0.07484 |  | 1 | CAPACITY
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00012 |  |  | 0.12623 |  | 1 | CAPACITY
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 6.82 |  |  | -0.00012 |  |  | 0 |  | 1 | CAPACITY | P60
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 5.46 |  |  | -0.00011 |  |  | 0 |  | 1 | CAPACITY
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.02 |  |  | -0.00012 |  |  | 0 |  | 1 | CAPACITY
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 2.57 |  |  | -0.00012 |  |  | 0 |  | 1 | CAPACITY | K13
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00012 |  |  | 0 |  | 1 | CAPACITY
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.45 |  |  | -0.00011 |  |  | 0 |  | 1 | CAPACITY
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.72 |  |  | -0.00011 |  |  | 0 |  | 1 | CAPACITY | K22
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 497.77 |  |  | -0.00013 |  |  | 0.10478 |  | 1 | CAPACITY
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 422.06 |  |  | -0.00012 |  |  | 0.10478 |  | 1 | CAPACITY
903644 | W3-099 E OP1 | 230 | 226 | 74 | 0 | 87 | 0 |  |  | -0.00012 |  |  | 0 |  | 1 | NEWENERGY | W3-099
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 60 | 0 |  |  | -0.00013 |  |  | 0 |  | 1 | NEWENERGY | R32
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 52 | 0 |  |  | -0.00013 |  |  | 0 |  | 1 | NEWENERGY | O18
200805 | 26COLVER13 | 13.2 | 226 | 12 | 77 | 110 | 88.31 |  |  | -0.00013 |  |  | 0.10478 |  | 1 | CAPACITY
201144 | W3-099 C OP1 | 230 | 226 | 74 | 0 | 13 | 0 |  |  | -0.00012 |  |  | 0 |  | 1 | NEW | W3-099
200809 | 26SITHE | 138 | 226 | 15 | 0 | 36 | 28.9 |  |  | -0.00013 |  |  | 0.10478 |  | 1 | CAPACITY
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 10.44 |  |  | -0.00012 |  |  | 0.12623 |  | 1 | CAPACITY
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 10.19 |  |  | -0.00013 |  |  | 0 |  | 1 | CAPACITY | R32
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00012 |  |  | 0.12623 |  | 1 | CAPACITY
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00013 |  |  | 0 |  | 1 | CAPACITY | O18
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 521.86 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | CAPACITY
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 492.95 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | CAPACITY
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 0 |  |  | -0.00014 |  |  | 0 |  | 1 | NEWENERGY | N39
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00014 |  |  | 0 |  | 1 | NEWENERGY | O38
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 48 | 0 |  |  | -0.00014 |  |  | 0 |  | 1 | NEWENERGY | Q53
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 0 |  |  | -0.00013 |  |  | 0 |  | 1 | NEWENERGY | V3-030
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | N39
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.4 | 7.55 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | O38
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 5.14 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | Q53
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 4.25 |  |  | -0.00013 |  |  | 0 |  | 1 | CAPACITY | V3-030
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 57 | 45.76 |  |  | -0.00015 |  |  | 0.08446 |  | 1 | CAPACITY
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 601.34 |  |  | -0.00016 |  |  | 0.10478 |  | 1 | CAPACITY
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 293.93 |  |  | -0.00016 |  |  | 0.10478 |  | 1 | CAPACITY | Bris2
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 248.4 |  |  | -0.00016 |  |  | 0.10478 |  | 1 | CAPACITY | Bris1
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 187.87 |  |  | -0.00016 |  |  | 0.0316 |  | 1 | CAPACITY
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 177.43 |  |  | -0.00016 |  |  | 0.0316 |  | 1 | CAPACITY
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 40 | 0 |  |  | -0.00015 |  |  | 0 |  | 1 | NEWENERGY | Q36
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 26.13 |  |  | -0.00016 |  |  | 0.07484 |  | 1 | CAPACITY
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | -0.00016 |  |  | 0 |  | 1 | ENERGY
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 6.66 |  |  | -0.00015 |  |  | 0 |  | 1 | CAPACITY | Q36
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 16.86 |  |  | -0.00016 |  |  | 0.07484 |  | 1 | CAPACITY
200722 | 26SHAWVL 2 | 18 | 226 | 12 | 62 | 124.7 | 100.12 |  |  | -0.00018 |  |  | 0.10478 |  | 1 | CAPACITY
200715 | 26SHAWVL 1 | 18 | 226 | 12 | 62 | 122 | 97.95 |  |  | -0.00018 |  |  | 0.10478 |  | 1 | CAPACITY
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 33.96 |  |  | -0.00017 |  |  | 0.10478 |  | 1 | CAPACITY
208947 | WSHO CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00018 |  |  | 0.08446 |  | 1 | CAPACITY
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4.82 |  |  | -0.00017 |  |  | 0 |  | 1 | CAPACITY
200665 | 26SHAWVL 3 | 22 | 226 | 12 | 120 | 174.2 | 139.86 |  |  | -0.00018 |  |  | 0.10478 |  | 1 | CAPACITY
200666 | 26SHAWVL 4 | 22 | 226 | 12 | 120 | 171 | 137.29 |  |  | -0.00018 |  |  | 0.10478 |  | 1 | CAPACITY
236828 | 01GRAYMONT | 46 | 201 | 2 | 0 | 4 | 0 |  |  | -0.00019 |  |  | 0 |  | 1 | ENERGY
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | -0.00019 |  |  | 0 |  | 1 | MTX | AC1-025
208942 | HARR CT | 12.5 | 229 | 55 | 0 | 42 | 33.72 |  |  | -0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 9.64 |  |  | -0.0002 |  |  | 0.12623 |  | 1 | CAPACITY
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 8.19 |  |  | -0.0002 |  |  | 0.10478 |  | 1 | CAPACITY
210319 | WCAR 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.0002 |  |  | 0 |  | 1 | CAPACITY
208348 | EELI | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00019 |  |  | 0 |  | 1 | CAPACITY
210022 | LING 2 | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.0002 |  |  | 0 |  | 1 | CAPACITY
922932 | AB1-082 OP | 46 | 201 | 55 | 0 | 19.9 | 0 |  |  | -0.0002 |  |  | 0.08446 |  | 1 | NEW
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 24.08 |  |  | -0.0002 |  |  | 0.10478 |  | 1 | CAPACITY
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 0 |  |  | -0.00022 |  |  | 0 |  | 1 | NEWENERGY | Z1-069
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | -0.00023 |  |  | 0.12623 |  | 1 | ENERGY
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00022 |  |  | 0 |  | 1 | CAPACITY | Z1-069
208885 | WNHO | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00023 |  |  | 0 |  | 1 | CAPACITY
208697 | PRIN B34 | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00023 |  |  | 0 |  | 1 | CAPACITY
204663 | 27AES GEN2 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00026 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204664 | 27AES GEN3 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00026 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204662 | 27AES GEN1 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00026 |  |  | 0.04435 |  | 1 | CAPACITY | IRONWOOD
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | -0.00025 |  |  | 0 |  | 1 | ENERGY
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.61 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 19 | 15.25 |  |  | -0.00028 |  |  | 0.08446 |  | 1 | CAPACITY
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | -0.00028 |  |  | 0 |  | 1 | ENERGY
208580 | MGTN 2 | 12.5 | 229 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00028 |  |  | 0 |  | 1 | CAPACITY
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 0 |  |  | -0.00028 |  |  | 0 |  | 1 | NEWENERGY | P47
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00029 |  |  | 0 |  | 1 | NEWENERGY | K02
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.8 | 12.69 |  |  | -0.00028 |  |  | 0 |  | 1 | CAPACITY | P47
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 17.18 |  |  | -0.0003 |  |  | 0.12623 |  | 1 | CAPACITY
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 16.86 |  |  | -0.0003 |  |  | 0.12623 |  | 1 | CAPACITY
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 16.86 |  |  | -0.0003 |  |  | 0.12623 |  | 1 | CAPACITY
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | -0.00031 |  |  | 0.07484 |  | 1 | CAPACITY
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | -0.00031 |  |  | 0.07484 |  | 1 | CAPACITY
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 77.07 |  |  | -0.00031 |  |  | 0.07484 |  | 1 | CAPACITY
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | -0.00031 |  |  | 0.07484 |  | 1 | CAPACITY
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | -0.00031 |  |  | 0.07484 |  | 1 | CAPACITY
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 38.54 |  |  | -0.00031 |  |  | 0.07484 |  | 1 | CAPACITY
920341 | AA2-132 | 34.5 | 226 | 55 | 0 | 19.9 | 0 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | NEW
919201 | AA1-144 OP | 230 | 226 | 58 | 0 | 163 | 130.87 |  |  | -0.00034 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-144
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00034 |  |  | 0.04435 |  | 1 | CAPACITY | X1-109
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00034 |  |  | 0 |  | 1 | CAPACITY | X1-109
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.04 |  |  | -0.00034 |  |  | 0 |  | 1 | CAPACITY
203932 | AA2-133 GEN | 13.8 | 226 | 55 | 0 | 19.89 | 0 |  |  | -0.00037 |  |  | 0.08446 |  | 1 | NEW
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 389.39 |  |  | -0.00038 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-115
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 30.1 | 24.17 |  |  | -0.00038 |  |  | 0.08446 |  | 1 | CAPACITY
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 4.82 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 6 | 4.82 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | P28
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 317.93 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | Hummel
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | NEW
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 194.29 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | Hummel
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.0004 |  |  | 0.04435 |  | 1 | CAPACITY | Hummel
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | Hummel
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 47.37 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 17.58 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | P28
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 17.18 |  |  | -0.0004 |  |  | 0.12623 |  | 1 | CAPACITY
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 64.23 |  |  | -0.00042 |  |  | 0.10478 |  | 1 | CAPACITY
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 152.86 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 152.86 |  |  | -0.00043 |  |  | 0.04435 |  | 1 | CAPACITY | ONTELAUNEE
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 139.94 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 361.29 |  |  | -0.00043 |  |  | 0.10478 |  | 1 | CAPACITY
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 148.77 |  |  | -0.00043 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC1
209018 | SUNBIPCT | 12.5 | 229 | 55 | 0 | 36 | 28.9 |  |  | -0.00045 |  |  | 0.08446 |  | 1 | CAPACITY
212345 | PENS | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 18.3 | 14.69 |  |  | -0.00045 |  |  | 0.12623 |  | 1 | CAPACITY
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 11.24 |  |  | -0.00047 |  |  | 0.08446 |  | 1 | CAPACITY
212435 | SMIL | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00048 |  |  | 0.04435 |  | 1 | CAPACITY | MOXIE PATRIOT
208948 | WILL CT | 12.5 | 229 | 55 | 0 | 27.4 | 22 |  |  | -0.00047 |  |  | 0.08446 |  | 1 | CAPACITY
212005 | ALWD | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 608.97 |  |  | -0.00048 |  |  | 0.10478 |  | 1 | CAPACITY
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 608.49 |  |  | -0.00048 |  |  | 0.10478 |  | 1 | CAPACITY
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 34.28 |  |  | -0.00049 |  |  | 0.10478 |  | 1 | CAPACITY
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 26.09 |  |  | -0.00049 |  |  | 0.10478 |  | 1 | CAPACITY
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 6.42 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 4.9 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1090.36 |  |  | -0.00051 |  |  | 0.01494 |  | 1 | CAPACITY
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 69.05 |  |  | -0.00051 |  |  | 0.10478 |  | 1 | CAPACITY
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 65.83 |  |  | -0.00051 |  |  | 0.10478 |  | 1 | CAPACITY
208941 | FISH CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00051 |  |  | 0.08446 |  | 1 | CAPACITY
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.4 | 9.15 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | Q27
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.81 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | N14
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00051 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-046
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | Z2-046
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1091.76 |  |  | -0.00053 |  |  | 0.01494 |  | 1 | CAPACITY
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.00054 |  |  | 0.05 |  | 1 | MTX | AB1-182
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 39.1 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 38.86 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 35.57 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 23.44 |  |  | -0.00053 |  |  | 0.04435 |  | 1 | CAPACITY | HUNLOCK
208944 | JENK CT | 12.5 | 229 | 55 | 0 | 28 | 22.48 |  |  | -0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 S
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY | W2-071
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.65 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | L18
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | AB1-025 S
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.85 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | W2-071
211375 | BEAC | 69 | 229 | 2 | 0 | 20 | 0 |  |  | -0.00055 |  |  | 0.10478 |  | 1 | ENERGY
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 47.77 |  |  | -0.00055 |  |  | 0.08446 |  | 1 | CAPACITY
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 47.21 |  |  | -0.00055 |  |  | 0.08446 |  | 1 | CAPACITY
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 23.76 |  |  | -0.00055 |  |  | 0.08446 |  | 1 | CAPACITY
208943 | HARW CT | 12.5 | 229 | 55 | 0 | 27.2 | 21.84 |  |  | -0.00055 |  |  | 0.08446 |  | 1 | CAPACITY
211374 | AVOC | 12.5 | 229 | 2 | 0 | 17.4 | 13.97 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY
211591 | HARW | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00055 |  |  | 0 |  | 1 | CAPACITY
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00055 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G2
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00055 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G3
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00055 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G1
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 0 |  |  | -0.00055 |  |  | 0 |  | 1 | NEWENERGY | AC1-071
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | -0.00055 |  |  | 0.05 |  | 1 | MTX | Z2-107
209009 | PEIP 2 | 13.8 | 229 | 56 | 0 | 43.7 | 35.08 |  |  | -0.00055 |  |  | 0.08446 |  | 1 | CAPACITY
209010 | PEIP 1 | 13.8 | 229 | 29 | 0 | 26.7 | 21.43 |  |  | -0.00055 |  |  | 0.10478 |  | 1 | CAPACITY
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 7.23 |  |  | -0.00055 |  |  | 0 |  | 1 | CAPACITY | K21
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 7.02 |  |  | -0.00055 |  |  | 0 |  | 1 | NEW | AC1-071
209003 | KSTN IPP | 13.8 | 229 | 65 | 0 | 4.9 | 3.93 |  |  | -0.00055 |  |  | 0 |  | 1 | CAPACITY
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | -0.00056 |  |  | 0 |  | 1 | ENERGY
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00057 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00057 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00057 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00057 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00057 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200044 | BETH CT1 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00057 |  |  | 0.04435 |  | 1 | CAPACITY | BETH1234
200048 | BETH CT5 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00057 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0 |  |  | -0.00058 |  |  | 0 |  | 1 | NEWENERGY | W2-056
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0 |  |  | -0.00058 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 N
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 3.36 |  |  | -0.00058 |  |  | 0 |  | 1 | CAPACITY | W2-056
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00058 |  |  | 0 |  | 1 | CAPACITY | AB1-025 N
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 900.89 |  |  | -0.00059 |  |  | 0.01494 |  | 1 | CAPACITY
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 0 |  |  | -0.0006 |  |  | 0 |  | 1 | NEWENERGY | AA2-017
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 0 |  |  | -0.0006 |  |  | 0 |  | 1 | NEW | AA2-017
209007 | NOEN IPP | 13.8 | 229 | 12 | 80 | 111.4 | 89.44 |  |  | -0.00061 |  |  | 0.10478 |  | 1 | CAPACITY
208940 | ALLE CT | 12.5 | 229 | 55 | 0 | 56 | 44.96 |  |  | -0.0006 |  |  | 0.08446 |  | 1 | CAPACITY
900003 | DEANS E | 500 | 231 | 74 | 0 | 1779.4 | 0 |  |  | -0.00063 |  |  | 0 |  | 1 | NEWENERGY | OSW_DEANS
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 120 |  |  |  | -0.0006
211065 | PSPA IPP | 13.8 | 229 | 75 | 0 | 18.4 | 6.74 |  |  | -0.00062 |  |  | 0 |  | 1 | NEWENERGY | U4-014
200006 | DEANS C | 500 | 231 | 74 | 0 | 762.6 | 762.6 |  |  | -0.00063 |  |  | 0 |  | 1 | CAPACITY | OSW_DEANS
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00063 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
208920 | WLPK | 12.5 | 229 | 60 | 0 | 40.9 | 32.84 |  |  | -0.00064 |  |  | 0.07484 |  | 1 | CAPACITY
208946 | MACR CT | 12.5 | 229 | 55 | 0 | 72 | 57.81 |  |  | -0.00066 |  |  | 0.08446 |  | 1 | CAPACITY
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00068 |  |  | 0.10478 |  | 1 | CAPACITY
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00068 |  |  | 0.10478 |  | 1 | CAPACITY
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 192.53 |  |  | -0.00068 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 160.57 |  |  | -0.00068 |  |  | 0.04435 |  | 1 | CAPACITY | LOWER MT BETHEL
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 160.57 |  |  | -0.00068 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.33 |  |  | -0.00068 |  |  | 0 |  | 1 | CAPACITY
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 152 | 122.03 |  |  | -0.0007 |  |  | 0.08446 |  | 1 | CAPACITY
206341 | 28GIL 8 | 13.8 | 228 | 58 | 69.9 | 90 | 72.26 |  |  | -0.0007 |  |  | 0.04435 |  | 1 | CAPACITY | GILBERT
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 87 | 100 | 87.11 |  |  | -0.0007 |  |  | 0 |  | 1 | CAPACITY | GILBERT
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 85.3 | 98 | 85.37 |  |  | -0.0007 |  |  | 0 |  | 1 | CAPACITY | GILBERT
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 20 | 16.06 |  |  | -0.0007 |  |  | 0.08446 |  | 1 | CAPACITY
207402 | 28AA2-082 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.00072 |  |  | 0.05 |  | 1 | MTX | AA2-082
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00071 |  |  | 0 |  | 1 | NEWENERGY | W4-073
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00071 |  |  | 0 |  | 1 | NEWENERGY | W1-127
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.00071 |  |  | 0 |  | 1 | CAPACITY
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0 |  |  | -0.00071 |  |  | 0 |  | 1 | NEWENERGY | U2-059
925462 | AC1-018 E | 34.5 | 228 | 75 | 0 | 0.9 | 0 |  |  | -0.00071 |  |  | 0 |  | 1 | NEWENERGY | AC1-018
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 4 | 3.21 |  |  | -0.00071 |  |  | 0 |  | 1 | CAPACITY
925461 | AC1-018 C | 34.5 | 228 | 75 | 0 | 0.5 | 0 |  |  | -0.00071 |  |  | 0 |  | 1 | NEW | AC1-018
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00071 |  |  | 0 |  | 1 | CAPACITY | W1-127
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00071 |  |  | 0 |  | 1 | CAPACITY | U2-059
204651 | 27PORT CT | 13.8 | 227 | 56 | 4 | 35 | 28.1 |  |  | -0.00073 |  |  | 0.08446 |  | 1 | CAPACITY
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0 |  |  | -0.00072 |  |  | 0 |  | 1 | NEWENERGY | AD2-070
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00072 |  |  | 0 |  | 1 | NEWENERGY | W4-097
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00072 |  |  | 0 |  | 1 | CAPACITY | AD2-070
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00072 |  |  | 0 |  | 1 | CAPACITY | W4-097
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 134 | 107.58 |  |  | -0.00073 |  |  | 0.08446 |  | 1 | CAPACITY
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | W3-077
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 5.7 | 4.58 |  |  | -0.00074 |  |  | 0 |  | 1 | CAPACITY | W3-077
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.00074 |  |  | 0 |  | 1 | CAPACITY | W2-091
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00075 |  |  | 0.0316 |  | 1 | CAPACITY
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00075 |  |  | 0.0316 |  | 1 | CAPACITY
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00075 |  |  | 0.0316 |  | 1 | CAPACITY
206747 | 28DSM_X3-029 | 34.5 | 228 | 29 | 0 | 11.15 | 0 |  |  | -0.00076 |  |  | 0.10478 |  | 1 | ENERGY
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | -0.00076 |  |  | 0.08446 |  | 1 | ENERGY
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | NEWENERGY | Y2-018
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 0 |  |  | -0.00078 |  |  | 0 |  | 1 | NEWENERGY | W3-044
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00078 |  |  | 0 |  | 1 | CAPACITY | W3-044
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 898.96 |  |  | -0.00078 |  |  | 0.01494 |  | 1 | CAPACITY
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00078 |  |  | 0 |  | 1 | NEWENERGY | W4-046
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 1.93 |  |  | -0.00078 |  |  | 0 |  | 1 | CAPACITY | W4-046
933322 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | -0.0008 |  |  | 0 |  | 1 | MTX | AC2-144
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.00081 |  |  | 0 |  | 1 | NEWENERGY | V4-001
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.61 |  |  | -0.00081 |  |  | 0 |  | 1 | CAPACITY | V4-001
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | NEWENERGY | W4-064
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | W4-064
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | -0.00084 |  |  | 0.05 |  | 1 | MTX | AA2-061
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00084 |  |  | 0 |  | 1 | NEWENERGY | X1-012
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0 |  |  | -0.00085 |  |  | 0 |  | 1 | NEWENERGY | W3-106
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | -0.00084 |  |  | 0.05 |  | 1 | MTX | AA2-060
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0 |  |  | -0.00085 |  |  | 0 |  | 1 | NEWENERGY | W3-110
206742 | 28SUX_V3-011 | 34.5 | 228 | 64 | 0 | 2 | 0 |  |  | -0.00084 |  |  | 0 |  | 1 | CAPACITY
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 2.97 |  |  | -0.00084 |  |  | 0 |  | 1 | CAPACITY | X1-012
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 2.29 |  |  | -0.00085 |  |  | 0 |  | 1 | CAPACITY | W3-110
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0 |  |  | -0.00086 |  |  | 0 |  | 1 | NEWENERGY | AC2-175
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0 |  |  | -0.00086 |  |  | 0 |  | 1 | NEWENERGY | AE1-081
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 2.99 |  |  | -0.00085 |  |  | 0 |  | 1 | CAPACITY | Y1-020
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.77 |  |  | -0.00086 |  |  | 0 |  | 1 | CAPACITY | AE1-081
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.00088 |  |  | 0.08446 |  | 1 | CAPACITY
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.00088 |  |  | 0 |  | 1 | NEWENERGY | W2-016
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.00088 |  |  | 0 |  | 1 | CAPACITY | W2-016
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0 |  |  | -0.0009 |  |  | 0 |  | 1 | NEWENERGY | X2-089
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.61 |  |  | -0.0009 |  |  | 0 |  | 1 | CAPACITY | X2-089
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  |  |  | -0.0009
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 309 | 248.08 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.00092 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC2
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.00092 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218344 | TOSCO_G6 | 18 | 231 | 2 | 90 | 180 | 144.51 |  |  | -0.00092 |  |  | 0.04435 |  | 1 | CAPACITY | TOSCO
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | -0.00092 |  |  | 0.08446 |  | 1 | CAPACITY
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | -0.00092 |  |  | 0.08446 |  | 1 | CAPACITY
933332 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | -0.00091 |  |  | 0 |  | 1 | MTX | AC2-145
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 538.72 |  |  | -0.00092 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-116
219001 | SEWAREN7GT | 25 | 231 | 58 | 101.5 | 324.6 | 260.61 |  |  | -0.00092 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-089
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 309 | 248.08 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
219002 | SEWAREN7ST | 18 | 231 | 58 | 96.3 | 216.4 | 173.74 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY | Z2-089
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 180 | 144.51 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | -0.00092 |  |  | 0.04435 |  | 1 | ENERGY | Z2-089
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | -0.00092 |  |  | 0 |  | 1 | ENERGY | Z2-089
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -0.00092 |  |  | 0.08446 |  | 1 | CAPACITY
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -0.00092 |  |  | 0.08446 |  | 1 | CAPACITY
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 30.03 |  |  | -0.00092 |  |  | 0.10478 |  | 1 | CAPACITY
213798 | MERCK 3 | 13.8 | 230 | 2 | 13 | 35 | 28.1 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY
213797 | MERCK 2 | 13.8 | 230 | 2 | 4 | 25 | 20.07 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0 |  |  | -0.00092 |  |  | 0 |  | 1 | NEWENERGY | AB1-139
217825 | UMD_NJ | 26 | 231 | 2 | 0 | 10.5 | 8.43 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 5.3 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | W2-080
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0 |  |  | -0.00092 |  |  | 0 |  | 1 | NEWENERGY | AE1-041
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | W1-101
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 3.29 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY
930901 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 2.01 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY | AB1-139
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0 |  |  | -0.00092 |  |  | 0 |  | 1 | NEWENERGY | W2-052
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | W2-080
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.43 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | W1-101
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY | W2-052
938281 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY | AE1-041
900004 | SMITHBRG E | 500 | 228 | 74 | 0 | 820.4 | 0 |  |  | -0.00094 |  |  | 0 |  | 1 | NEWENERGY | OSW_SMITHB
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 207.94 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 202.48 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.00093 |  |  | 0.04435 |  | 1 | CAPACITY | DELANCY STREET
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 169.24 |  |  | -0.00093 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN1
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 143.63 |  |  | -0.00093 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN2
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 143.63 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 76.11 |  |  | -0.00093 |  |  | 0.08446 |  | 1 | CAPACITY
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.00093 |  |  | 0.08446 |  | 1 | CAPACITY
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.00093 |  |  | 0.08446 |  | 1 | CAPACITY
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.00093 |  |  | 0.08446 |  | 1 | CAPACITY
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.00093 |  |  | 0.08446 |  | 1 | CAPACITY
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
218092 | PRIMEENG_G | 26.4 | 231 | 29 | 10 | 70.3 | 56.44 |  |  | -0.00093 |  |  | 0.10478 |  | 1 | CAPACITY
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 70.56 |  |  | -0.00093 |  |  | 0.08446 |  | 1 | CAPACITY
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.00093 |  |  | 0.04435 |  | 1 | CAPACITY | NEWARK BAY
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 27.46 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.00093 |  |  | 0.10478 |  | 1 | CAPACITY
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.00093 |  |  | 0.10478 |  | 1 | CAPACITY
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | V2-025
217831 | PB_NUTCLIF | 26 | 231 | 2 | 0 | 10.7 | 8.59 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY
217850 | MONTCLAIR_U | 26 | 231 | 2 | 0 | 10.6 | 8.51 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | W4-059
934302 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | AD1-054
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.74 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | AB1-021
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | X1-072
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | V3-067
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.85 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | V3-065
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | V3-066
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | V3-068
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | X1-072
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | AB1-021
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.23 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | V3-067
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.18 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | W4-059
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.17 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | V3-065
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | V3-068
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | V3-066
200017 | SMITHBRG C | 500 | 228 | 74 | 0 | 327.6 | 327.6 |  |  | -0.00094 |  |  | 0 |  | 1 | CAPACITY | OSW_SMITHB
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0 |  |  | -0.00094 |  |  | 0 |  | 1 | NEWENERGY | X2-087
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.00094 |  |  | 0 |  | 1 | CAPACITY | X2-087
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | W3-029
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | W3-003
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEW | AE1-156
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | NEWENERGY | X2-075
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | AE1-156
937512 | AD2-210 E | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | MTX | AD2-210
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | W1-132
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | V4-069
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | V4-070
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | W2-061
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY | W3-029
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 1.83 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | X2-075
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY | V4-070
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY | V4-069
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY | W2-061
218455 | CINNBAY_CGEN | 26.4 | 231 | 75 | 0 | 9 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | NEWENERGY
924132 | NEWROADSO E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | NEWENERGY | AB2-057
217199 | EDGEBORO_2E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | NEWENERGY | V3-059
217198 | EDGEBORO_1E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | NEWENERGY | V3-058
924131 | NEWROADSO C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | AB2-057
218781 | BRIS_MYERS | 26 | 231 | 2 | 0 | 3 | 2.41 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | NEWENERGY | V3-070
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | NEWENERGY | X1-095
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | V3-070
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | X1-095
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | W2-050
213893 | PHLISST1 | 20 | 230 | 58 | 184 | 267 | 214.36 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00103 |  |  | 0.04435 |  | 1 | CAPACITY | PHILLIPS ISLAND
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | V3-024
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | V2-009 2
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | W3-124
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | V2-009 1
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | X2-088
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | V3-024
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 1.52 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | V2-009 2
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.87 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | W3-124
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | V2-009 1
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.72 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | X2-088
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 22.48 |  |  | -0.00108 |  |  | 0.10478 |  | 1 | CAPACITY
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0 |  |  | -0.0011 |  |  | 0 |  | 1 | NEWENERGY | V2-009 3
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0 |  |  | -0.0011 |  |  | 0 |  | 1 | NEWENERGY | V2-009 4
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 1.92 |  |  | -0.0011 |  |  | 0 |  | 1 | CAPACITY | V2-009 3
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 1.15 |  |  | -0.0011 |  |  | 0 |  | 1 | CAPACITY | V2-009 4
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0 |  |  | -0.00113 |  |  | 0 |  | 1 | NEWENERGY | W2-036
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00113 |  |  | 0 |  | 1 | CAPACITY | W2-036
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0 |  |  | -0.00116 |  |  | 0 |  | 1 | NEWENERGY | V4-005
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00116 |  |  | 0 |  | 1 | CAPACITY | V4-005
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0 |  |  | -0.00124 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0 |  |  | -0.00124 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
932032 | AC2-009 E | 13.2 | 231 | 75 | -0.5 | 0.49 | 0 |  |  | -0.00124 |  |  | 0 |  | 1 | NEWENERGY | AC2-009
932031 | AC2-009 C | 13.2 | 231 | 75 | -0.1 | 0.1 | 0 |  |  | -0.00124 |  |  | 0 |  | 1 | NEW | AC2-009
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00124 |  |  | 0 |  | 1 | CAPACITY | AA2-058
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 35.24 |  |  | -0.00125 |  |  | 0.10478 |  | 1 | CAPACITY
218780 | PRINCENTON_U | 26 | 231 | 2 | 0 | 31.56 | 25.34 |  |  | -0.00124 |  |  | 0 |  | 1 | CAPACITY
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0 |  |  | -0.00124 |  |  | 0 |  | 1 | NEWENERGY | Z1-096
219622 | TRENT_BIOGAS | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.00124 |  |  | 0 |  | 1 | CAPACITY
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 2.39 |  |  | -0.00124 |  |  | 0 |  | 1 | CAPACITY | Z1-096
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 31.31 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00127 |  |  | 0.10478 |  | 1 | CAPACITY
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00127 |  |  | 0.10478 |  | 1 | CAPACITY
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 238 | 191.08 |  |  | -0.00127 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00127 |  |  | 0.04435 |  | 1 | CAPACITY | LIBERTY EDDY
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00127 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 27.3 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00128 |  |  | 0.08446 |  | 1 | CAPACITY
219650 | TRENT_COLLEG | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.00128 |  |  | 0 |  | 1 | CAPACITY
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0 |  |  | -0.00128 |  |  | 0 |  | 1 | NEWENERGY | W4-058
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.22 |  |  | -0.00128 |  |  | 0 |  | 1 | CAPACITY | W4-058
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0 |  |  | -0.00129 |  |  | 0 |  | 1 | NEWENERGY | Y1-075
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.00129 |  |  | 0 |  | 1 | CAPACITY | Y1-075
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 130.87 |  |  | -0.00132 |  |  | 0.04435 |  | 1 | CAPACITY | GRAYS FERRY
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.00133 |  |  | 0.08446 |  | 1 | CAPACITY
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0 |  |  | -0.00134 |  |  | 0 |  | 1 | NEWENERGY | W1-121 Z
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY | W1-121 Z
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.46 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.00135 |  |  | 0.08446 |  | 1 | CAPACITY
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.00135 |  |  | 0.08446 |  | 1 | CAPACITY
219123 | BCRR_COGEN | 13.8 | 231 | 64 | 0 | 6 | 0 |  |  | -0.00144 |  |  | 0.12623 |  | 1 | CAPACITY
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY | T20
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.00151 |  |  | 0.08446 |  | 1 | CAPACITY
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.00151 |  |  | 0.08446 |  | 1 | CAPACITY
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 260.3 | 208.98 |  |  | -0.00154 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 205.69 |  |  | -0.00154 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | -0.00154 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | -0.00154 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill B
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | -0.00154 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | -0.00154 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill A
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 0 |  |  | -0.00155 |  |  | 0 |  | 1 | NEWENERGY | W3-080
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.00155 |  |  | 0.08446 |  | 1 | CAPACITY
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.00155 |  |  | 0.08446 |  | 1 | CAPACITY
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.00155 |  |  | 0.08446 |  | 1 | CAPACITY
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.00155 |  |  | 0.08446 |  | 1 | CAPACITY
925442 | AC1-016 E | 26.4 | 231 | 75 | 0 | 5.45 | 0 |  |  | -0.00155 |  |  | 0 |  | 1 | NEWENERGY | AC1-016
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | -0.00155 |  |  | 0 |  | 1 | NEWENERGY | W2-102
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | -0.00155 |  |  | 0 |  | 1 | NEWENERGY | W4-103
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -0.00155 |  |  | 0 |  | 1 | NEWENERGY | Y3-026
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00155 |  |  | 0 |  | 1 | CAPACITY | Y3-026
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 2.97 |  |  | -0.00155 |  |  | 0 |  | 1 | CAPACITY | W3-080
925441 | AC1-016 C | 26.4 | 231 | 75 | 0 | 3.34 | 2.68 |  |  | -0.00155 |  |  | 0 |  | 1 | CAPACITY | AC1-016
219685 | NATIONAL_GYP | 26 | 231 | 2 | 0 | 2.8 | 2.25 |  |  | -0.00155 |  |  | 0 |  | 1 | CAPACITY
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.00155 |  |  | 0 |  | 1 | CAPACITY | W4-103
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.00155 |  |  | 0 |  | 1 | CAPACITY | W2-102
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00156 |  |  | 0.08446 |  | 1 | CAPACITY
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00156 |  |  | 0.08446 |  | 1 | CAPACITY
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00156 |  |  | 0.08446 |  | 1 | CAPACITY
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00156 |  |  | 0.08446 |  | 1 | CAPACITY
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00156 |  |  | 0.08446 |  | 1 | CAPACITY
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00156 |  |  | 0.08446 |  | 1 | CAPACITY
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00156 |  |  | 0.08446 |  | 1 | CAPACITY
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 38.54 |  |  | -0.00156 |  |  | 0.08446 |  | 1 | CAPACITY
214030 | WAYNEJCT | 13.8 | 230 | 2 | 0 | 8.8 | 7.07 |  |  | -0.00157 |  |  | 0 |  | 1 | CAPACITY
228203 | P06 | 13.8 | 234 | 57 | 80.6 | 92.7 | 80.75 |  |  | -0.00177 |  |  | 0.08446 |  | 1 | CAPACITY
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0 |  |  | -0.00177 |  |  | 0 |  | 1 | NEWENERGY | AC1-017
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0 |  |  | -0.00177 |  |  | 0 |  | 1 | NEWENERGY | X1-070
925451 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 1.12 |  |  | -0.00177 |  |  | 0 |  | 1 | CAPACITY | AC1-017
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.96 |  |  | -0.00177 |  |  | 0 |  | 1 | CAPACITY | X1-070
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  |  |  | -0.0019
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 245.67 |  |  | -0.00189 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.00189 |  |  | 0.04435 |  | 1 | CAPACITY | RARITAN RIVER
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.00189 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
207435 | AD1-113 CT2 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.00189 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207434 | AD1-113 CT1 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.00189 |  |  | 0.04435 |  | 1 | NEW | RARITAN RIVER
207441 | AD1-113 ST | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.00189 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 97.1 | 111.6 | 97.21 |  |  | -0.00189 |  |  | 0.08446 |  | 1 | CAPACITY
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 90.9 | 104.5 | 91.03 |  |  | -0.00189 |  |  | 0.08446 |  | 1 | CAPACITY
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0 |  |  | -0.00191 |  |  | 0 |  | 1 | NEWENERGY | Y3-087
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 1.84 |  |  | -0.00191 |  |  | 0 |  | 1 | CAPACITY | Y3-087
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0 |  |  | -0.00196 |  |  | 0 |  | 1 | NEWENERGY | X3-075
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.00198 |  |  | 0.08446 |  | 1 | CAPACITY
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.00198 |  |  | 0.08446 |  | 1 | CAPACITY
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0 |  |  | -0.00198 |  |  | 0 |  | 1 | NEWENERGY | W2-078
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.00198 |  |  | 0 |  | 1 | NEWENERGY | W1-113
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00198 |  |  | 0 |  | 1 | CAPACITY | W2-078
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 2.25 |  |  | -0.00198 |  |  | 0 |  | 1 | CAPACITY | W1-113
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 199.11 |  |  | -0.00199 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.00199 |  |  | 0.04435 |  | 1 | CAPACITY | RED OAK
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 141.3 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 43.63 |  |  | -0.00206 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 46.17 |  |  | -0.00206 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 66.1 | 98 | 78.68 |  |  | -0.00207 |  |  | 0.08446 |  | 1 | CAPACITY
206327 | 28S RIV G1 | 13.8 | 228 | 57 | 86.9 | 99.9 | 87.02 |  |  | -0.00207 |  |  | 0.08446 |  | 1 | CAPACITY
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 87.02 |  |  | -0.00207 |  |  | 0.08446 |  | 1 | CAPACITY
207419 | AB2-139 E | 34.5 | 228 | 76 | 0 | 0.21 | 0 |  |  | -0.00208 |  |  | 0 |  | 1 | ENERGY | AB2-139
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEWENERGY | AC1-030
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0 |  |  | -0.00208 |  |  | 0 |  | 1 | NEWENERGY | X1-071
925561 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | AC1-030
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.28 |  |  | -0.00208 |  |  | 0 |  | 1 | CAPACITY | X1-071
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | MTX | Z1-082
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AC1-207
207420 | AC1-207 C | 34.5 | 228 | 75 | 0 | 4.9 | 3.93 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AC1-207
219647 | COOPERSOLA E | 13.2 | 231 | 75 | 0 | 0.4 | 0 |  |  | -0.00223 |  |  | 0 |  | 1 | NEWENERGY | AB1-063
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00226 |  |  | 0 |  | 1 | NEWENERGY | W1-032
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00226 |  |  | 0 |  | 1 | CAPACITY | W1-032
901032 | W1-024E OP1 | 34.5 | 228 | 0 | 0 | 0 | 0 |  |  | -0.00226 |  |  | 0 |  | 1 | NEW
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00226 |  |  | 0 |  | 1 | CAPACITY | W1-024
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00229 |  |  | 0 |  | 1 | NEWENERGY | W4-060
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.00229 |  |  | 0 |  | 1 | CAPACITY | W4-060
219913 | PENNSAU2 E | 26.4 | 231 | 75 | 0 | 8.2 | 0 |  |  | -0.00237 |  |  | 0 |  | 1 | NEWENERGY | AD2-042
219915 | CINNAMSOL E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.00237 |  |  | 0 |  | 1 | NEWENERGY | AD2-027
219912 | PENNSAU2 C | 26.4 | 231 | 75 | 0 | 5 | 0 |  |  | -0.00237 |  |  | 0 |  | 1 | NEW | AD2-042
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.63 | 3.72 |  |  | -0.00237 |  |  | 0 |  | 1 | CAPACITY
219914 | CINNAMSOL C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00237 |  |  | 0 |  | 1 | CAPACITY | AD2-027
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.4 |  |  | -0.00237 |  |  | 0 |  | 1 | CAPACITY
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00241 |  |  | 0 |  | 1 | NEWENERGY | X1-085
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00241 |  |  | 0 |  | 1 | CAPACITY | X1-085
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.00257 |  |  | 0.05 |  | 1 | MTX
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0 |  |  | -0.00265 |  |  | 0 |  | 1 | NEWENERGY | W1-112
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00265 |  |  | 0 |  | 1 | CAPACITY | W1-112
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 64.31 |  |  | -0.00266 |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 52.35 |  |  | -0.00266 |  |  | 0.04435 |  | 1 | CAPACITY | CAMDEN COGEN TECH
925391 | AC1-010 C | 26.4 | 231 | 75 | 0 | 6 | 0 |  |  | -0.00266 |  |  | 0 |  | 1 | NEW | AC1-010
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 19.27 |  |  | -0.00266 |  |  | 0.10478 |  | 1 | CAPACITY
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -0.00266 |  |  | 0 |  | 1 | NEWENERGY | AC1-010
219765 | PARADISE E | 26.4 | 231 | 75 | 0 | 3.2 | 0 |  |  | -0.00266 |  |  | 0 |  | 1 | NEWENERGY | U4-036
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.3 | 9.07 |  |  | -0.00266 |  |  | 0.10478 |  | 1 | CAPACITY
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | -0.00266 |  |  | 0 |  | 1 | MTX | X2-013
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00266 |  |  | 0 |  | 1 | CAPACITY | U4-036
206201 | 28JERSVGEN | 34.5 | 228 | 2 | 0 | 2 | 1.61 |  |  | -0.00276 |  |  | 0 |  | 1 | CAPACITY
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0 |  |  | -0.00281 |  |  | 0 |  | 1 | NEWENERGY | W2-019
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 1.85 |  |  | -0.00281 |  |  | 0 |  | 1 | CAPACITY | W2-019
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.00288 |  |  | 0 |  | 1 | NEWENERGY | W4-025
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00288 |  |  | 0 |  | 1 | NEWENERGY | W1-129
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.00288 |  |  | 0 |  | 1 | CAPACITY | W4-025
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00288 |  |  | 0 |  | 1 | CAPACITY | W1-129
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00291 |  |  | 0 |  | 1 | NEWENERGY | X4-015
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00291 |  |  | 0 |  | 1 | CAPACITY | X4-015
920732 | AA2-184 E | 34.5 | 228 | 75 | 0 | 20 | 0 |  |  | -0.00294 |  |  | 0 |  | 1 | NEWENERGY | AA2-184
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00296 |  |  | 0 |  | 1 | NEWENERGY | W2-082
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00297 |  |  | 0 |  | 1 | NEWENERGY | W1-124
921743 | AA2-049 E | 34.5 | 228 | 76 | -3 | 3 | 0 |  |  | -0.00297 |  |  | 0 |  | 1 | MTX | AA2-049
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.00297 |  |  | 0 |  | 1 | CAPACITY | W1-124
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00296 |  |  | 0 |  | 1 | CAPACITY | W2-082
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0 |  |  | -0.00297 |  |  | 0 |  | 1 | NEWENERGY | X1-037
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 3.37 |  |  | -0.00297 |  |  | 0 |  | 1 | CAPACITY | X1-037
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.00311 |  |  | 0 |  | 1 | NEWENERGY | X4-031
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0 |  |  | -0.00334 |  |  | 0 |  | 1 | NEWENERGY | Z2-102
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 3.97 |  |  | -0.00334 |  |  | 0 |  | 1 | CAPACITY | Z2-102
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.00335 |  |  | 0 |  | 1 | NEWENERGY | W1-120
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.00335 |  |  | 0 |  | 1 | NEWENERGY | W1-119
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.00335 |  |  | 0 |  | 1 | CAPACITY | W1-119
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.00335 |  |  | 0 |  | 1 | CAPACITY | W1-120
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -0.00352 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -0.00353 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 33.72 |  |  | -0.00352 |  |  | 0.04435 |  | 1 | CAPACITY | EAGLE POINT
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 24.08 |  |  | -0.00352 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00361 |  |  | 0 |  | 1 | NEWENERGY | Y2-081
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.00361 |  |  | 0 |  | 1 | CAPACITY | Y2-081
919662 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 |  |  | -0.00369 |  |  | 0.05 |  | 1 | MTX | AA2-048
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY | W3-079
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.00369 |  |  | 0 |  | 1 | CAPACITY | W3-079
900005 | 28LARRABEE E | 230 | 228 | 74 | 0 | 840 | 0 |  |  | -0.00379 |  |  | 0 |  | 1 | NEWENERGY | OSW_LARRAB
206294 | 28LARRABEE C | 230 | 228 | 74 | 0 | 360 | 360 |  |  | -0.00379 |  |  | 0 |  | 1 | CAPACITY | OSW_LARRAB
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY | Y2-051
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00384 |  |  | 0 |  | 1 | CAPACITY | Y2-051
923463 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | AB1-163
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 60.21 |  |  | -0.00429 |  |  | 0.10478 |  | 1 | CAPACITY
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.00477 |  |  | 0.08446 |  | 1 | CAPACITY
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.00477 |  |  | 0.08446 |  | 1 | CAPACITY
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 61.6 | 88.4 | 70.97 |  |  | -0.00477 |  |  | 0.04435 |  | 1 | CAPACITY | LAKEWOOD
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 61.2 | 88.3 | 70.89 |  |  | -0.00477 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 76.92 |  |  | -0.00477 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
923293 | AB1-138 E | 34.5 | 228 | 75 | 0 | 6 | 0 |  |  | -0.00506 |  |  | 0 |  | 1 | NEWENERGY | AB1-138
206280 | 28LAKEHURS | 34.5 | 228 | 64 | 0 | 13.8 | 11.08 |  |  | -0.00506 |  |  | 0.08446 |  | 1 | CAPACITY
923292 | AB1-138 C | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.00506 |  |  | 0 |  | 1 | CAPACITY | AB1-138
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 74.48 |  |  | -0.00515 |  |  | 0.08446 |  | 1 | CAPACITY
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 192.69 |  |  | -0.00579 |  |  | 0.10478 |  | 1 | CAPACITY
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 58.9 | 47.29 |  |  | -0.00585 |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 58.9 | 47.29 |  |  | -0.00585 |  |  | 0.04435 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 175.82 |  |  | -0.00587 |  |  | 0.10478 |  | 1 | CAPACITY
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 271.13 |  |  | -0.00594 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | -0.00594 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | -0.00594 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
228712 | V2-041E | 13.2 | 234 | 75 | 2.5 | 2.48 | 0 |  |  | -0.00598 |  |  | 0 |  | 1 | NEWENERGY | V2-041
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00598 |  |  | 0 |  | 1 | CAPACITY | V2-041
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 73.09 |  |  | -0.006 |  |  | 0.08446 |  | 1 | CAPACITY
228343 | QUINTN#1 | 12.9 | 234 | 64 | 0 | 1.7 | 0 |  |  | -0.00645 |  |  | 0 |  | 1 | CAPACITY
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 55.49 |  |  | -0.00646 |  |  | 0.08446 |  | 1 | CAPACITY
228471 | VALERO1 | 13.8 | 234 | 2 | 19.1 | 22 | 19.16 |  |  | -0.00647 |  |  | 0 |  | 1 | CAPACITY
228472 | VALERO2 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | -0.00647 |  |  | 0 |  | 1 | CAPACITY
228484 | VALERO4 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | -0.00647 |  |  | 0 |  | 1 | CAPACITY
228473 | VALERO3 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | -0.00647 |  |  | 0 |  | 1 | CAPACITY
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | -0.00648 |  |  | 0 |  | 1 | ENERGY
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.6 | 39.8 | 34.67 |  |  | -0.00675 |  |  | 0.08446 |  | 1 | CAPACITY
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 32.75 |  |  | -0.00675 |  |  | 0.08446 |  | 1 | CAPACITY
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 4.8 | 0 |  |  | -0.00675 |  |  | 0 |  | 1 | NEW
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0 |  |  | -0.00677 |  |  | 0 |  | 1 | NEWENERGY | V4-054
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00677 |  |  | 0 |  | 1 | CAPACITY | V4-054
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 48.35 |  |  | -0.00688 |  |  | 0.08446 |  | 1 | CAPACITY
228357 | V2-046E | 12.9 | 234 | 75 | 12.9 | 12.9 | 0 |  |  | -0.00709 |  |  | 0 |  | 1 | NEWENERGY | V2-046
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 6.26 |  |  | -0.00709 |  |  | 0 |  | 1 | CAPACITY | V2-046
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.5 | 18.87 |  |  | -0.00735 |  |  | 0.08446 |  | 1 | CAPACITY
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 49.65 |  |  | -0.00755 |  |  | 0.10478 |  | 1 | CAPACITY
900002 | 28OYSTER E | 230 | 228 | 74 | 0 | 586.7 | 0 |  |  | -0.0093 |  |  | 0 |  | 1 | NEWENERGY | OSW_OYSCK
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 27.3 |  |  | -0.0093 |  |  | 0.12623 |  | 1 | CAPACITY
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 27 |  |  | -0.0093 |  |  | 0.12623 |  | 1 | CAPACITY
206302 | 28OYSTER C | 230 | 228 | 74 | 0 | 229.3 | 229.3 |  |  | -0.0093 |  |  | 0 |  | 1 | CAPACITY | OSW_OYSCK
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.61 |  |  | -0.01627 |  |  | 0 |  | 1 | CAPACITY
900001 | BLE E | 138 | 234 | 74 | 0 | 310.6 | 0 |  |  | -0.02547 |  |  | 0 |  | 1 | NEWENERGY | OSW_BLE
228110 | BLE C | 138 | 234 | 74 | 0 | 121.4 | 121.4 |  |  | -0.02547 |  |  | 0 |  | 1 | CAPACITY | OSW_BLE
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0 |  |  | -0.06791 |  |  | 0 |  | 1 | NEWENERGY | W2-030
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 2.93 |  |  | -0.06791 |  |  | 0 |  | 1 | CAPACITY | W2-030
228721 | V2-035E | 12.9 | 234 | 75 | 1.2 | 1.2 | 0 |  |  | -0.0968 |  |  | 0 |  | 1 | NEWENERGY | V2-035
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.61 |  |  | -0.0968 |  |  | 0 |  | 1 | CAPACITY | V2-035
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0 |  |  | -0.1182 |  |  | 0 |  | 1 | NEWENERGY | AB1-001
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.7 |  |  | -0.1182 |  |  | 0 |  | 1 | CAPACITY | AB1-001
227801 | ONTC&DCT | 13.8 | 234 | 56 | 38.6 | 38.6 | 0 |  |  | -0.12189 |  |  | 0.08446 |  | 1 | NEW
228014 | PVILLEG | 0.48 | 234 | 65 | 1.7 | 3 | 1.04 |  |  | -0.14379 |  |  | 0 |  | 1 | CAPACITY
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0 |  |  | -0.21792 |  |  | 0 |  | 1 | NEWENERGY | W1-130
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 2.57 |  |  | -0.21792 |  |  | 0 |  | 1 | CAPACITY | W1-130

## FG 28-GD-S2-S8
****** PJM Generator Deliverability Detailed Report ****** POWER-GEM [TARA Ver 2001.1a PJMGD RC3 64-bit - Wed Aug 18 16:47:36 2021]
FG Index | 8 | Monitored Facility:206302 28OYSTER C 230 206297 28MANITOU 230 1 / Contingency:JC-P2-3-JCC-230-234OD[Breaker]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
817 | 104.47 | 102.07 | AC | 114.21 | 723.12 | 1.27 | 17.94 | -3.05 | 853.49 | 833.9 | 0.001715 | 0 | 12817.4 | 0 | 10597.7 | 0.07728 | 2219.67 | 2219.72 | -0.05 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited?
900002 | 28OYSTER E | 230 | 228 | 74 | 0 | 586.7 | 0 | 586.7 | FiftyFifty | 0.68993 | 404.7848 |  | 0 | 0.7635 | 1 | NEWENERGY | OSW_OYSCK
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 27.3 | 34 | FiftyFifty | 0.68993 | 4.6246 |  | 0.12623 | 0.8738 | 1 | CAPACITY
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 27 | 31 | FiftyFifty | 0.68993 | 2.757 |  | 0.12623 | 0.7635 | 1 | CAPACITY
206302 | 28OYSTER C | 230 | 228 | 74 | 0 | 229.3 | 229.3 | 229.3 | FiftyFifty | 0.68993 |  |  | 0 | 0.7635 | 1 | CAPACITY | OSW_OYSCK
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0 | 1.43 | FiftyFifty | 0.27446 | 0.3925 |  | 0 | 0.7635 | 1 | NEWENERGY | AB1-001
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.7 | 0.87 | FiftyFifty | 0.27446 | 0.0469 |  | 0 | 0.7635 | 1 | CAPACITY | AB1-001
900000 | CARDIFF E | 230 | 234 | 74 | 0 | 1235 | 0 | 1235 | FiftyFifty | 0.20271 | 250.345 |  | 0 | 0.7635 | 1 | NEWENERGY | OSW_CARDIF
227900 | CARDIFF C | 230 | 234 | 74 | 0 | 275 | 275 | 275 | FiftyFifty | 0.20271 |  |  | 0 | 0.7635 | 1 | CAPACITY | OSW_CARDIF
227928 | V4-067E | 12.9 | 234 | 75 | 1.6 | 1.6 | 0 | 1.6 | FiftyFifty | 0.18965 | 0.3034 |  | 0 | 0.7635 | 1 | NEWENERGY | V4-067
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.79 | 0.98 | FiftyFifty | 0.18965 | 0.0368 |  | 0 | 0.7635 | 1 | CAPACITY | V4-067
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0 | 1.2 | FiftyFifty | 0.18962 | 0.2275 |  | 0 | 0.7635 | 1 | NEWENERGY | AB2-122
924701 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.56 | 0.7 | FiftyFifty | 0.18962 | 0.026 |  | 0 | 0.7635 | 1 | CAPACITY | AB2-122
228014 | PVILLEG | 0.48 | 234 | 65 | 1.7 | 3 | 1.04 | 3 | FiftyFifty | 0.18592 | 0.3637 |  | 0 | 0.7635 | 1 | CAPACITY
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 | 7.8 | FiftyFifty | 0.18441 | 1.4384 |  | 0.12623 | 0.6671 | 1 | ENERGY
227801 | ONTC&DCT | 13.8 | 234 | 56 | 38.6 | 38.6 | 0 | 38.6 | FiftyFifty | 0.1843 | 7.1139 |  | 0.08446 | 0.6108 | 1 | NEW
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 | 5.5 | FiftyFifty | 0.1843 | 1.0136 |  | 0.10478 | 0.5468 | 1 | ENERGY
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0 | 6 | FiftyFifty | 0.18057 | 1.0834 |  | 0 | 0.5468 | 1 | NEWENERGY | W2-030
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 2.93 | 3.65 | FiftyFifty | 0.18057 | 0.1296 |  | 0 | 0.5468 | 1 | CAPACITY | W2-030
900001 | BLE E | 138 | 234 | 74 | 0 | 310.6 | 0 | 310.6 | FiftyFifty | 0.15211 | 47.2465 |  | 0 | 0.5468 | 1 | NEWENERGY | OSW_BLE
228110 | BLE C | 138 | 234 | 74 | 0 | 121.4 | 121.4 | 121.4 | FiftyFifty | 0.15211 |  |  | 0 | 0.5468 | 1 | CAPACITY | OSW_BLE
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.61 | 2 | FiftyFifty | 0.13191 | 0.052 |  | 0 | 0.5468 | 1 | CAPACITY
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 74.48 | 85.5 | FiftyFifty | 0.10263 | 1.131 |  | 0.08446 | 0.5006 | 1 | CAPACITY
228712 | V2-041E | 13.2 | 234 | 75 | 2.5 | 2.48 | 0 | 2.11 | Adder/OL | 0.1004 | 0.2116 | 0.0036 | 0 |  | 1 | NEWENERGY | V2-041
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0 | 4.84 | Adder/OL | 0.09368 | 0.4539 | 0.0083 | 0 |  | 1 | NEWENERGY | W1-130
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  | 105 | LTF/CMTX NF | 0.04268 | 4.481 | -0.1801
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  | 673 | LTF/CMTX NF | 0.01776 | 11.9539 | -1.1544
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  | 55.3 | CLTF | 0.01159 | 0.6407 | -0.0949
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.6 |  | 173.6 | CLTF | 0.00098 | 0.1703 | -0.2978
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 0.00098 | 0.0547 | -0.0955
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 0.00098 | 0.0536 | -0.0937
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  | 258.3 | CLTF | 0.00095 | 0.2462 | -0.4431
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  | 210 | CLTF | 0.00089 | 0.1875 | -0.3602
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 0.00084 | 0.0422 | -0.0859
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 0.00085 | 0.0421 | -0.0853
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  | 35 | CLTF | 0.00073 | 0.0257 | -0.06
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  | 57.8 | CLTF | 0.00068 | 0.0392 | -0.0991
919662 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 | -7 | Adder/NFTWR/OL | -0.08697 | 0.6088 | -0.012 | 0.05 |  | 1 | MTX NFTWR | AA2-048
228203 | P06 | 13.8 | 234 | 57 | 80.6 | 92.7 | 80.75 |  |  | 0.10096 |  |  | 0.08446 |  | 1 | CAPACITY
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 1.22 |  |  | 0.1004 |  |  | 0 |  | 1 | CAPACITY | V2-041
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 73.09 |  |  | 0.09692 |  |  | 0.08446 |  | 1 | CAPACITY
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 2.57 |  |  | 0.09368 |  |  | 0 |  | 1 | CAPACITY | W1-130
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 48.35 |  |  | 0.08659 |  |  | 0.08446 |  | 1 | CAPACITY
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.5 | 18.87 |  |  | 0.0836 |  |  | 0.08446 |  | 1 | CAPACITY
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 49.65 |  |  | 0.08204 |  |  | 0.10478 |  | 1 | CAPACITY
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0 |  |  | 0.07517 |  |  | 0 |  | 1 | NEWENERGY | V4-054
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 3.05 |  |  | 0.07517 |  |  | 0 |  | 1 | CAPACITY | V4-054
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 4.8 | 0 |  |  | 0.07516 |  |  | 0 |  | 1 | NEW
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.6 | 39.8 | 34.67 |  |  | 0.07505 |  |  | 0.08446 |  | 1 | CAPACITY
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 32.75 |  |  | 0.07505 |  |  | 0.08446 |  | 1 | CAPACITY
228721 | V2-035E | 12.9 | 234 | 75 | 1.2 | 1.2 | 0 |  |  | 0.06608 |  |  | 0 |  | 1 | NEWENERGY | V2-035
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.61 |  |  | 0.06608 |  |  | 0 |  | 1 | CAPACITY | V2-035
228343 | QUINTN#1 | 12.9 | 234 | 64 | 0 | 1.7 | 0 |  |  | 0.05958 |  |  | 0 |  | 1 | CAPACITY
228357 | V2-046E | 12.9 | 234 | 75 | 12.9 | 12.9 | 0 |  |  | 0.05184 |  |  | 0 |  | 1 | NEWENERGY | V2-046
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 6.26 |  |  | 0.05184 |  |  | 0 |  | 1 | CAPACITY | V2-046
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 192.69 |  |  | 0.05112 |  |  | 0.10478 |  | 1 | CAPACITY
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 58.9 | 47.29 |  |  | 0.04027 |  |  | 0.04435 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 58.9 | 47.29 |  |  | 0.04027 |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 175.82 |  |  | 0.03655 |  |  | 0.10478 |  | 1 | CAPACITY
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | 0.03314 |  |  | 0 |  | 1 | ENERGY
228471 | VALERO1 | 13.8 | 234 | 2 | 19.1 | 22 | 19.16 |  |  | 0.03276 |  |  | 0 |  | 1 | CAPACITY
228473 | VALERO3 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.03276 |  |  | 0 |  | 1 | CAPACITY
228484 | VALERO4 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.03276 |  |  | 0 |  | 1 | CAPACITY
228472 | VALERO2 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.03276 |  |  | 0 |  | 1 | CAPACITY
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 55.49 |  |  | 0.03118 |  |  | 0.08446 |  | 1 | CAPACITY
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 271.13 |  |  | 0.02399 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.02399 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.02399 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 998.11 |  |  | 0.01988 |  |  | 0.01494 |  | 1 | CAPACITY
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 992.1 |  |  | 0.01988 |  |  | 0.01494 |  | 1 | CAPACITY
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | 0.01988 |  |  | 0.08446 |  | 1 | ENERGY
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1026.43 |  |  | 0.01974 |  |  | 0.01494 |  | 1 | CAPACITY
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 60.21 |  |  | 0.01892 |  |  | 0.10478 |  | 1 | CAPACITY
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0 |  |  | 0.01748 |  |  | 0 |  | 1 | NEWENERGY | Y2-081
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | 0.01748 |  |  | 0 |  | 1 | CAPACITY | Y2-081
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | 0.01724 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 33.72 |  |  | 0.01723 |  |  | 0.04435 |  | 1 | CAPACITY | EAGLE POINT
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 24.08 |  |  | 0.01723 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | 0.01721 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0 |  |  | 0.01672 |  |  | 0 |  | 1 | NEWENERGY | Y3-087
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 1.84 |  |  | 0.01672 |  |  | 0 |  | 1 | CAPACITY | Y3-087
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0 |  |  | 0.01564 |  |  | 0 |  | 1 | NEWENERGY | X3-075
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | 0.015 |  |  | 0 |  | 1 | MTX | Z1-082
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 64.31 |  |  | 0.0148 |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 52.35 |  |  | 0.0148 |  |  | 0.04435 |  | 1 | CAPACITY | CAMDEN COGEN TECH
925391 | AC1-010 C | 26.4 | 231 | 75 | 0 | 6 | 0 |  |  | 0.0148 |  |  | 0 |  | 1 | NEW | AC1-010
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 19.27 |  |  | 0.0148 |  |  | 0.10478 |  | 1 | CAPACITY
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | 0.0148 |  |  | 0 |  | 1 | NEWENERGY | AC1-010
219765 | PARADISE E | 26.4 | 231 | 75 | 0 | 3.2 | 0 |  |  | 0.0148 |  |  | 0 |  | 1 | NEWENERGY | U4-036
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.3 | 9.07 |  |  | 0.0148 |  |  | 0.10478 |  | 1 | CAPACITY
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | 0.0148 |  |  | 0 |  | 1 | MTX | X2-013
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | 0.0148 |  |  | 0 |  | 1 | CAPACITY | U4-036
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | 0.0148 |  |  | 0.04435 |  | 1 | NEW | AA2-069
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 154.95 |  |  | 0.0148 |  |  | 0.04435 |  | 1 | CAPACITY | Garrison
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 93.29 |  |  | 0.0148 |  |  | 0 |  | 1 | CAPACITY | Garrison
232901 | NORTHST | 69 | 235 | 56 | 5 | 46 | 36.93 |  |  | 0.0148 |  |  | 0.08446 |  | 1 | CAPACITY
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 12.2 |  |  | 0.0148 |  |  | 0.10478 |  | 1 | CAPACITY
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 39.34 |  |  | 0.01467 |  |  | 0.08446 |  | 1 | CAPACITY
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 38.54 |  |  | 0.01467 |  |  | 0.08446 |  | 1 | CAPACITY
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 0 |  |  | 0.01426 |  |  | 0 |  | 1 | NEWENERGY | AB1-056
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 330.7 |  |  | 0.01426 |  |  | 0.10478 |  | 1 | CAPACITY
930201 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 51.71 |  |  | 0.01426 |  |  | 0 |  | 1 | CAPACITY | AB1-056
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 152.54 |  |  | 0.01426 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01426 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC2
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01426 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01426 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
232920 | IR10 | 13.2 | 235 | 55 | 12.6 | 16.1 | 12.93 |  |  | 0.01425 |  |  | 0.08446 |  | 1 | CAPACITY
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0 |  |  | 0.01424 |  |  | 0 |  | 1 | NEWENERGY | AB1-137
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 3.37 |  |  | 0.01424 |  |  | 0 |  | 1 | CAPACITY | AB1-137
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | 0.01423 |  |  | 0.10478 |  | 1 | ENERGY
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.01422 |  |  | 0 |  | 1 | NEWENERGY | Z2-077
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.01422 |  |  | 0 |  | 1 | NEWENERGY | Z2-076
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.01422 |  |  | 0 |  | 1 | CAPACITY | Z2-077
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.01422 |  |  | 0 |  | 1 | CAPACITY | Z2-076
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.41 |  |  | 0.01422 |  |  | 0 |  | 1 | CAPACITY
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.05 |  |  | 0.01418 |  |  | 0 |  | 1 | CAPACITY
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.01418 |  |  | 0.08446 |  | 1 | CAPACITY
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.01418 |  |  | 0.08446 |  | 1 | CAPACITY
917082 | CHERRYDALE E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01412 |  |  | 0 |  | 1 | NEWENERGY | Z2-012
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01412 |  |  | 0 |  | 1 | NEWENERGY | W1-003
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01412 |  |  | 0 |  | 1 | NEWENERGY | W1-006
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01412 |  |  | 0 |  | 1 | NEWENERGY | W1-004
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01412 |  |  | 0 |  | 1 | NEWENERGY | W1-005
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232915 | OH NUG4 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 39.03 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 38.94 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 38.68 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 26.05 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.01412 |  |  | 0 |  | 1 | CAPACITY | W1-003
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.01412 |  |  | 0 |  | 1 | CAPACITY | W1-004
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.01412 |  |  | 0 |  | 1 | CAPACITY | W1-005
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.01412 |  |  | 0 |  | 1 | CAPACITY | W1-006
232905 | BAYVIEW1 | 24.9 | 235 | 65 | 0 | 12.5 | 10.04 |  |  | 0.01412 |  |  | 0.12623 |  | 1 | CAPACITY
917081 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.01412 |  |  | 0 |  | 1 | CAPACITY | Z2-012
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 0 |  |  | 0.01409 |  |  | 0 |  | 1 | NEWENERGY | AA1-102
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 45.76 |  |  | 0.01409 |  |  | 0 |  | 1 | CAPACITY | AA1-102
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0 |  |  | 0.0141 |  |  | 0 |  | 1 | NEWENERGY | X1-032
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 8.03 |  |  | 0.01409 |  |  | 0 |  | 1 | CAPACITY
293670 | O-025 C | 25 | 235 | 64 | 0 | 6 | 4.82 |  |  | 0.0141 |  |  | 0 |  | 1 | CAPACITY
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0 |  |  | 0.01407 |  |  | 0 |  | 1 | NEWENERGY | Y3-058
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 5.7 | 4.58 |  |  | 0.01407 |  |  | 0 |  | 1 | CAPACITY | Y3-058
232919 | VN10 | 13.2 | 235 | 55 | 12.4 | 14.3 | 12.46 |  |  | 0.01397 |  |  | 0 |  | 1 | CAPACITY
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 122.84 |  |  | 0.01394 |  |  | 0.10478 |  | 1 | CAPACITY
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0 |  |  | 0.01394 |  |  | 0 |  | 1 | NEWENERGY | Y1-080
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 1.03 |  |  | 0.01394 |  |  | 0 |  | 1 | CAPACITY | Y1-080
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01386 |  |  | 0 |  | 1 | NEWENERGY | X3-008
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.01386 |  |  | 0 |  | 1 | CAPACITY | X3-008
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 55.4 |  |  | 0.01358 |  |  | 0.12623 |  | 1 | CAPACITY
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0 |  |  | 0.01341 |  |  | 0 |  | 1 | NEWENERGY | Y1-079
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.01341 |  |  | 0 |  | 1 | CAPACITY | Y1-079
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 57.24 |  |  | 0.01335 |  |  | 0.10478 |  | 1 | CAPACITY
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 45.76 |  |  | 0.01335 |  |  | 0.08446 |  | 1 | CAPACITY
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 44.16 |  |  | 0.01335 |  |  | 0.04435 |  | 1 | CAPACITY | DELAWARE CITY
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 14.29 |  |  | 0.01335 |  |  | 0.08446 |  | 1 | CAPACITY
219647 | COOPERSOLA E | 13.2 | 231 | 75 | 0 | 0.4 | 0 |  |  | 0.01333 |  |  | 0 |  | 1 | NEWENERGY | AB1-063
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0 |  |  | 0.01331 |  |  | 0 |  | 1 | NEWENERGY | X3-066
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 2.28 | 1.83 |  |  | 0.01331 |  |  | 0 |  | 1 | CAPACITY | X3-066
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 19.11 |  |  | 0.01331 |  |  | 0.12623 |  | 1 | CAPACITY
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.0132 |  |  | 0 |  | 1 | NEWENERGY | AB1-142
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.0132 |  |  | 0 |  | 1 | NEWENERGY | AB1-141
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.0132 |  |  | 0 |  | 1 | CAPACITY | AB1-142
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.0132 |  |  | 0 |  | 1 | CAPACITY | AB1-141
219913 | PENNSAU2 E | 26.4 | 231 | 75 | 0 | 8.2 | 0 |  |  | 0.01259 |  |  | 0 |  | 1 | NEWENERGY | AD2-042
219915 | CINNAMSOL E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | 0.01259 |  |  | 0 |  | 1 | NEWENERGY | AD2-027
219912 | PENNSAU2 C | 26.4 | 231 | 75 | 0 | 5 | 0 |  |  | 0.01259 |  |  | 0 |  | 1 | NEW | AD2-042
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.63 | 3.72 |  |  | 0.01259 |  |  | 0 |  | 1 | CAPACITY
219914 | CINNAMSOL C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | 0.01259 |  |  | 0 |  | 1 | CAPACITY | AD2-027
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.4 |  |  | 0.01259 |  |  | 0 |  | 1 | CAPACITY
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01255 |  |  | 0 |  | 1 | NEWENERGY | AB2-179
233931 | AB2-179 C | 0.38 | 235 | 75 | 0 | 38 | 30.51 |  |  | 0.01255 |  |  | 0 |  | 1 | CAPACITY | AB2-179
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.09 |  |  | 0.01216 |  |  | 0 |  | 1 | CAPACITY
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 18.47 |  |  | 0.01184 |  |  | 0.08446 |  | 1 | CAPACITY
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 18.39 |  |  | 0.01184 |  |  | 0.08446 |  | 1 | CAPACITY
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 13.81 |  |  | 0.01181 |  |  | 0.08446 |  | 1 | CAPACITY
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 139.7 |  |  | 0.01161 |  |  | 0.10478 |  | 1 | CAPACITY
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01161 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01161 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01158 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 69.05 |  |  | 0.01158 |  |  | 0.10478 |  | 1 | CAPACITY
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 11.4 |  |  | 0.01158 |  |  | 0.08446 |  | 1 | CAPACITY
925112 | AB2-168 E | 34.5 | 235 | 75 | 0 | 5.2 | 0 |  |  | 0.01149 |  |  | 0 |  | 1 | NEWENERGY | AB2-168
925111 | AB2-168 C | 34.5 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.01149 |  |  | 0 |  | 1 | CAPACITY | AB2-168
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 361.29 |  |  | 0.0107 |  |  | 0.10478 |  | 1 | CAPACITY
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 148.77 |  |  | 0.0107 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC1
213893 | PHLISST1 | 20 | 230 | 58 | 184 | 267 | 214.36 |  |  | 0.00993 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.00993 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.00993 |  |  | 0.04435 |  | 1 | CAPACITY | PHILLIPS ISLAND
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.00993 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.5 | 0 |  |  | 0.00955 |  |  | 0 |  | 1 | NEWENERGY | AC1-030
925561 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | 0.00955 |  |  | 0 |  | 1 | CAPACITY | AC1-030
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0 |  |  | 0.00952 |  |  | 0 |  | 1 | NEWENERGY | X1-071
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.28 |  |  | 0.00952 |  |  | 0 |  | 1 | CAPACITY | X1-071
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | 0.00924 |  |  | 0.08446 |  | 1 | CAPACITY
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | 0.00924 |  |  | 0.08446 |  | 1 | CAPACITY
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 31.31 |  |  | 0.00796 |  |  | 0.08446 |  | 1 | CAPACITY
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | 0.00795 |  |  | 0.08446 |  | 1 | CAPACITY
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | 0.00795 |  |  | 0.08446 |  | 1 | CAPACITY
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | 0.00783 |  |  | 0.10478 |  | 1 | CAPACITY
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | 0.00781 |  |  | 0.10478 |  | 1 | CAPACITY
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 27.3 |  |  | 0.00782 |  |  | 0.08446 |  | 1 | CAPACITY
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | 0.00777 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 238 | 191.08 |  |  | 0.00777 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | 0.00777 |  |  | 0.04435 |  | 1 | CAPACITY | LIBERTY EDDY
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | 0.0077 |  |  | 0.08446 |  | 1 | CAPACITY
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | 0.00724 |  |  | 0.08446 |  | 1 | CAPACITY
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0 |  |  | 0.00683 |  |  | 0 |  | 1 | NEWENERGY | W2-071
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.85 |  |  | 0.00683 |  |  | 0 |  | 1 | CAPACITY | W2-071
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 130.87 |  |  | 0.00642 |  |  | 0.04435 |  | 1 | CAPACITY | GRAYS FERRY
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | 0.0064 |  |  | 0.08446 |  | 1 | CAPACITY
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | 0.00639 |  |  | 0.08446 |  | 1 | CAPACITY
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | 0.00639 |  |  | 0.08446 |  | 1 | CAPACITY
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0 |  |  | 0.00619 |  |  | 0 |  | 1 | NEWENERGY | AC1-017
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0 |  |  | 0.00619 |  |  | 0 |  | 1 | NEWENERGY | X1-070
925451 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 1.12 |  |  | 0.00619 |  |  | 0 |  | 1 | CAPACITY | AC1-017
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.96 |  |  | 0.00619 |  |  | 0 |  | 1 | CAPACITY | X1-070
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | 0.00605 |  |  | 0.08446 |  | 1 | CAPACITY
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | 0.00605 |  |  | 0.08446 |  | 1 | CAPACITY
214030 | WAYNEJCT | 13.8 | 230 | 2 | 0 | 8.8 | 7.07 |  |  | 0.00603 |  |  | 0 |  | 1 | CAPACITY
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0 |  |  | 0.00582 |  |  | 0 |  | 1 | NEWENERGY | Y1-075
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 0.00582 |  |  | 0 |  | 1 | CAPACITY | Y1-075
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0 |  |  | 0.0057 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 S
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 0.0057 |  |  | 0 |  | 1 | CAPACITY | AB1-025 S
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 77.07 |  |  | 0.00533 |  |  | 0.07484 |  | 1 | CAPACITY
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | 0.00533 |  |  | 0.07484 |  | 1 | CAPACITY
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | 0.00533 |  |  | 0.07484 |  | 1 | CAPACITY
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 38.54 |  |  | 0.00533 |  |  | 0.07484 |  | 1 | CAPACITY
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | 0.00533 |  |  | 0.07484 |  | 1 | CAPACITY
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | 0.00533 |  |  | 0.07484 |  | 1 | CAPACITY
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 369.31 |  |  | 0.00524 |  |  | 0.04435 |  | 1 | CAPACITY | Y1-065
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00524 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00524 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200055 | ROCKSP 4 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00524 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 4
200054 | ROCKSP 3 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00524 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 3
200052 | ROCKSP 1 | 18 | 225 | 57 | 145.7 | 167.5 | 145.91 |  |  | 0.00524 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 1
200053 | ROCKSP 2 | 18 | 225 | 57 | 144.9 | 166.5 | 145.04 |  |  | 0.00524 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 2
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | 0.00483 |  |  | 0 |  | 1 | ENERGY
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0 |  |  | 0.00464 |  |  | 0 |  | 1 | NEWENERGY | V4-005
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.88 |  |  | 0.00464 |  |  | 0 |  | 1 | CAPACITY | V4-005
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 0 |  |  | 0.00374 |  |  | 0 |  | 1 | NEWENERGY | W3-080
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.00374 |  |  | 0.08446 |  | 1 | CAPACITY
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.00374 |  |  | 0.08446 |  | 1 | CAPACITY
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.00374 |  |  | 0.08446 |  | 1 | CAPACITY
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.00374 |  |  | 0.08446 |  | 1 | CAPACITY
925442 | AC1-016 E | 26.4 | 231 | 75 | 0 | 5.45 | 0 |  |  | 0.00374 |  |  | 0 |  | 1 | NEWENERGY | AC1-016
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | 0.00374 |  |  | 0 |  | 1 | NEWENERGY | W2-102
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | 0.00374 |  |  | 0 |  | 1 | NEWENERGY | W4-103
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | 0.00374 |  |  | 0 |  | 1 | NEWENERGY | Y3-026
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | 0.00374 |  |  | 0 |  | 1 | CAPACITY | Y3-026
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 2.97 |  |  | 0.00374 |  |  | 0 |  | 1 | CAPACITY | W3-080
925441 | AC1-016 C | 26.4 | 231 | 75 | 0 | 3.34 | 2.68 |  |  | 0.00374 |  |  | 0 |  | 1 | CAPACITY | AC1-016
219685 | NATIONAL_GYP | 26 | 231 | 2 | 0 | 2.8 | 2.25 |  |  | 0.00374 |  |  | 0 |  | 1 | CAPACITY
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | 0.00374 |  |  | 0 |  | 1 | CAPACITY | W4-103
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | 0.00374 |  |  | 0 |  | 1 | CAPACITY | W2-102
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 38.54 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | 0.00327 |  |  | 0.0316 |  | 1 | CAPACITY
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | 0.00326 |  |  | 0.0316 |  | 1 | CAPACITY
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | 0.00327 |  |  | 0.0316 |  | 1 | CAPACITY
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | 0.00326 |  |  | 0.0316 |  | 1 | CAPACITY
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 260.3 | 208.98 |  |  | 0.00317 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | 0.00317 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill B
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | 0.00317 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 205.69 |  |  | 0.00317 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | 0.00317 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill A
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | 0.00317 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1034.24 |  |  | 0.00295 |  |  | 0.01494 |  | 1 | CAPACITY
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 306.69 |  |  | 0.00294 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00294 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA2
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 154.95 |  |  | 0.00294 |  |  | 0 |  | 1 | CAPACITY | DELTA
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00294 |  |  | 0 |  | 1 | CAPACITY | DELTA
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00294 |  |  | 0 |  | 1 | CAPACITY | DELTA
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1049.33 |  |  | 0.00285 |  |  | 0.01494 |  | 1 | CAPACITY
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 22.48 |  |  | 0.00233 |  |  | 0.10478 |  | 1 | CAPACITY
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0 |  |  | 0.00078 |  |  | 0 |  | 1 | NEWENERGY | AA2-072
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 140.6 | 112.88 |  |  | 0.00072 |  |  | 0.08446 |  | 1 | CAPACITY
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 91.2 |  |  | 0.00072 |  |  | 0.08446 |  | 1 | CAPACITY
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 83.5 |  |  | 0.00072 |  |  | 0.08446 |  | 1 | CAPACITY
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 41.75 |  |  | 0.00072 |  |  | 0.08446 |  | 1 | CAPACITY
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.21 |  |  | 0.00072 |  |  | 0 |  | 1 | CAPACITY
220904 | CRANE G2 | 20 | 232 | 12 | 60 | 195 | 0 |  |  | 0.00064 |  |  | 0.10478 |  | 1 | NEW
220905 | CRANE GT | 4.16 | 232 | 55 | 0 | 14 | 0 |  |  | 0.00064 |  |  | 0.08446 |  | 1 | NEW
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | 0.00061 |  |  | 0 |  | 1 | ENERGY
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 256.27 |  |  | 0.00061 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | 0.00061 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | 0.00061 |  |  | 0.04435 |  | 1 | CAPACITY | HUNTERSTOWN
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 134.08 |  |  | 0.00061 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.5 | 24.49 |  |  | 0.00059 |  |  | 0.08446 |  | 1 | CAPACITY
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 30 | 24.08 |  |  | 0.00059 |  |  | 0.08446 |  | 1 | CAPACITY
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 45.76 |  |  | 0.00058 |  |  | 0.10478 |  | 1 | CAPACITY
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 246 |  |  | 0.00056 |  |  | 0.10478 |  | 1 | CAPACITY
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 102.85 |  |  | 0.00056 |  |  | 0.10478 |  | 1 | CAPACITY
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | 0.00056 |  |  | 0.08446 |  | 1 | ENERGY
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 10.68 |  |  | 0.00056 |  |  | 0.08446 |  | 1 | CAPACITY
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 516 |  |  | 0.00054 |  |  | 0.10478 |  | 1 | CAPACITY
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 512.95 |  |  | 0.00054 |  |  | 0.10478 |  | 1 | CAPACITY
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 318.73 |  |  | 0.00054 |  |  | 0.10478 |  | 1 | CAPACITY
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.49 |  |  | 0.0004 |  |  | 0 |  | 1 | CAPACITY
226895 | WOAKV2-037 E | 69 | 233 | 65 | 0 | 4.5 | 0 |  |  | 0.00033 |  |  | 0 |  | 1 | ENERGY
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 695.27 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 675.85 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | ENERGY
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.76 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0 |  |  | 0.00025 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 N
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0 |  |  | 0.00025 |  |  | 0 |  | 1 | NEWENERGY | AB2-157
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.69 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY | AB1-025 N
925011 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.64 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY | AB2-157
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 477.7 |  |  | 0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 469.91 |  |  | 0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
227024 | SMECOCT | 13.8 | 238 | 57 | 30 | 80.2 | 64.39 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 19.59 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 14.45 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 497.29 |  |  | 0.00022 |  |  | 0.10478 |  | 1 | CAPACITY
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 492.39 |  |  | 0.00022 |  |  | 0.10478 |  | 1 | CAPACITY
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 0 |  |  | 0.00022 |  |  | 0 |  | 1 | NEWENERGY | AC2-101
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 0 |  |  | 0.00022 |  |  | 0 |  | 1 | NEWENERGY | AC2-120
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
226915 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 9.92 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY | AC2-101
226912 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 8.39 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY | AC2-120
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 272.01 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | 0.00022 |  |  | 0.04435 |  | 1 | CAPACITY | WALDORF
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY | WALDORF
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0 |  |  | 0.0002 |  |  | 0 |  | 1 | NEWENERGY | W2-056
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 3.36 |  |  | 0.0002 |  |  | 0 |  | 1 | CAPACITY | W2-056
910861 | X3-087 C | 230 | 233 | 58 | 0 | 744 | 597.33 |  |  | 0.00017 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
917371 | Z2-060 | 230 | 233 | 58 | 0 | 116 | 93.13 |  |  | 0.00017 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
920642 | AA2-170 E | 230 | 233 | 58 | 0 | 19.1 | 0 |  |  | 0.00017 |  |  | 0.04435 |  | 1 | NEW | AA2-170
920641 | AA2-170 C | 230 | 233 | 58 | 0 | 92 | 73.86 |  |  | 0.00017 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-170
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 64.23 |  |  | 0.00017 |  |  | 0 |  | 1 | CAPACITY | PANDA
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | 0.00017 |  |  | 0 |  | 1 | CAPACITY | PANDA
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | 0.00017 |  |  | 0.04435 |  | 1 | CAPACITY | PANDA
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 330 | 264.94 |  |  | 0.00016 |  |  | 0 |  | 1 | CAPACITY | X4-035
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | 0.00016 |  |  | 0 |  | 1 | CAPACITY | X4-035
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | 0.00016 |  |  | 0.04435 |  | 1 | CAPACITY | X4-035
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | 0.00014 |  |  | 0.10478 |  | 1 | ENERGY
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | 3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | 3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 41.75 |  |  | 3e-05 |  |  | 0.10478 |  | 1 | CAPACITY
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 14.45 |  |  | 3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-129
924771 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEW | AB2-129
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -8e-05 |  |  | 0.08446 |  | 1 | CAPACITY
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 1.04 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY | T20
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 245.67 |  |  | -0.0001 |  |  | 0 |  | 1 | CAPACITY | X4-039
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.0001 |  |  | 0.04435 |  | 1 | CAPACITY | X4-039
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.0001 |  |  | 0 |  | 1 | CAPACITY | X4-039
313821 | 6PACIFIC | 230 | 345 | 75 | 0 | 0.09 | 0 |  |  | -0.00011 |  |  | 0 |  | 1 | NEWENERGY
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 201.52 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00014 |  |  | 0.04435 |  | 1 | CAPACITY | POSSUM POINT
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 28.74 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | CAPACITY
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 28.66 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | CAPACITY
314088 | 6VANDORN | 230 | 345 | 2 | 7 | 21 | 16.86 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | CAPACITY
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | CAPACITY
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00017 |  |  | 0 |  | 1 | NEWENERGY | AC2-072
932521 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00017 |  |  | 0 |  | 1 | CAPACITY | AC2-072
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 0.68 | 0 |  |  | -0.00019 |  |  | 0 |  | 1 | NEWENERGY
235002 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0 |  |  | -0.0002 |  |  | 0 |  | 1 | NEW | AC1-039
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0 |  |  | -0.0002 |  |  | 0 |  | 1 | NEWENERGY | AC1-039
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0 |  |  | -0.0002 |  |  | 0 |  | 1 | NEWENERGY | AA1-109
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 3.61 |  |  | -0.0002 |  |  | 0 |  | 1 | CAPACITY | AA1-109
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.00021 |  |  | 0 |  | 1 | NEWENERGY | W1-116
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 4.27 |  |  | -0.00021 |  |  | 0 |  | 1 | CAPACITY | W1-116
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 1.61 |  |  | -0.00021 |  |  | 0 |  | 1 | CAPACITY
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 152.3 | 122.28 |  |  | -0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 120.19 |  |  | -0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 128.86 |  |  | -0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00023 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 0 |  |  | -0.00024 |  |  | 0 |  | 1 | NEWENERGY | AB2-029
923213 | AB1-125 E OP | 34.5 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.00023 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
923202 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.00023 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0 |  |  | -0.00023 |  |  | 0 |  | 1 | NEWENERGY | AB1-096
923212 | AB1-125 C OP | 34.5 | 201 | 75 | 0 | 5.7 | 0 |  |  | -0.00023 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
314078 | 3REMNGTN | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00024 |  |  | 0 |  | 1 | CAPACITY | AB2-029
930521 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00023 |  |  | 0 |  | 1 | CAPACITY | AB1-096
315033 | 1BIRCHWDA | 18 | 345 | 13 | 85 | 238 | 191.08 |  |  | -0.00024 |  |  | 0.10478 |  | 1 | CAPACITY
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.00025 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 2
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.00025 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 1
926737 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | AC1-158 1
926738 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | AC1-158 2
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 6.98 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 128.94 |  |  | -0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 128.54 |  |  | -0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 128.3 |  |  | -0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0 |  |  | -0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC2-136
933251 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 4.41 |  |  | -0.00026 |  |  | 0 |  | 1 | CAPACITY | AC2-136
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 761.83 |  |  | -0.00027 |  |  | 0.01494 |  | 1 | CAPACITY
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 761.51 |  |  | -0.00027 |  |  | 0.01494 |  | 1 | CAPACITY
923872 | AB2-027 E | 34.5 | 201 | 75 | 0 | 5.5 | 0 |  |  | -0.00028 |  |  | 0 |  | 1 | NEWENERGY | AB2-027
235006 | AB2-027 C | 34.5 | 201 | 75 | 0 | 3.3 | 0 |  |  | -0.00028 |  |  | 0 |  | 1 | NEW | AB2-027
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00028 |  |  | 0 |  | 1 | CAPACITY
316149 | AD1-046 E | 230 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00029 |  |  | 0 |  | 1 | NEWENERGY | AD1-044
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | W4-102
237799 | 01AA2-159 C | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
920562 | AA2-159 E | 34.5 | 201 | 75 | 0 | 7.3 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00029 |  |  | 0 |  | 1 | NEWENERGY | AE1-124
316148 | AD1-046 C | 230 | 345 | 75 | 0 | 30.7 | 24.65 |  |  | -0.00029 |  |  | 0 |  | 1 | CAPACITY | AD1-044
938961 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00029 |  |  | 0 |  | 1 | CAPACITY | AE1-124
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY | W4-102
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-158
925021 | AB2-158 C | 230 | 345 | 75 | 0 | 61 | 48.97 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY | AB2-158
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-097
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC1-118
314766 | 6LOUISA | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY
314190 | 6WESTMOR | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | CAPACITY | AC1-118
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 2.09 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.88 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 136.49 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
923192 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | AA1-095
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 2.33 |  |  | -0.00031 |  |  | 0 |  | 1 | CAPACITY | AA1-095
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.00033 |  |  | 0.08446 |  | 1 | CAPACITY
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.00033 |  |  | 0.08446 |  | 1 | CAPACITY
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 126.85 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00033 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 6
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00033 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 5
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 61.9 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00032 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00032 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 2
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00033 |  |  | 0 |  | 1 | NEWENERGY | AC2-138
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 19.99 |  |  | -0.00033 |  |  | 0.10478 |  | 1 | CAPACITY
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00032 |  |  | 0 |  | 1 | CAPACITY | South Anna 2
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00032 |  |  | 0 |  | 1 | CAPACITY | South Anna 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 19.27 |  |  | -0.00033 |  |  | 0.10478 |  | 1 | CAPACITY
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 6.3 | 5.06 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | AC2-138
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0 |  |  | -0.00033 |  |  | 0 |  | 1 | NEWENERGY | AA1-092
314172 | 6DUNNSVL | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00033 |  |  | 0 |  | 1 | NEWENERGY
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 6.42 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | AA1-092
314734 | 6CASHSCORNER | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00034 |  |  | 0 |  | 1 | NEWENERGY
314222 | 6HANOVER | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00034 |  |  | 0 |  | 1 | NEWENERGY
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AC1-112
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AB1-027
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AC2-070
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 8.83 |  |  | -0.00036 |  |  | 0.12623 |  | 1 | CAPACITY
314241 | 6OLDCHRC | 230 | 345 | 75 | 0 | 1.82 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AB1-027
932501 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 7.39 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AC2-070
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 3.21 |  |  | -0.00035 |  |  | 0 |  | 1 | CAPACITY
314213 | 3CARVER | 115 | 345 | 75 | 0 | 0 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEW | AC1-107
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00036 |  |  | 0.04435 |  | 1 | NEW | AC1-107
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEW | AC1-107
926785 | AC1-164 E | 0.44 | 345 | 75 | 0 | 99.2 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AC1-164
316114 | AB2-068 ST | 22 | 345 | 58 | 0 | 492 | 395.01 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316113 | AB2-068 CT2 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316112 | AB2-068 CT1 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00036 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-068
926784 | AC1-164 C | 0.44 | 345 | 75 | 0 | 220.8 | 177.27 |  |  | -0.00036 |  |  | 0 |  | 1 | NEW | AC1-164
315085 | 1SPRUNCC | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00037 |  |  | 0.10478 |  | 1 | NEW
315086 | 1SPRUNCD | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00037 |  |  | 0.10478 |  | 1 | NEW
314189 | 6PAPERMILL | 230 | 345 | 1 | 12 | 37 | 0 |  |  | -0.00036 |  |  | 0.10478 |  | 1 | ENERGY
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AC1-065
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 104.93 |  |  | -0.00037 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 7
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 103.25 |  |  | -0.00037 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 8
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 69.05 |  |  | -0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 68.97 |  |  | -0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 68.72 |  |  | -0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 68.64 |  |  | -0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 53.15 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 48.17 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7
925863 | AC1-065 C | 0.39 | 345 | 75 | 0 | 41.8 | 33.56 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AC1-065
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AC2-137
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AD2-030
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | AE1-074
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AB2-024
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AD1-063
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 16.06 |  |  | -0.00036 |  |  | 0.12623 |  | 1 | CAPACITY
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.3 | 13.09 |  |  | -0.00036 |  |  | 0.12623 |  | 1 | CAPACITY
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 11.96 |  |  | -0.00037 |  |  | 0.12623 |  | 1 | CAPACITY
938551 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | AE1-074
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AD2-030
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 11.4 | 9.15 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AC2-137
314375 | 6CORRCTN | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AB2-024
314187 | 3WAN 176 | 115 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY
934391 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AD1-063
314176 | 6HARMONY | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 4.98 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY
314294 | 6ENON | 230 | 345 | 75 | 0 | 0.23 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | -0.00038 |  |  | 0.10478 |  | 1 | ENERGY
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 106.94 |  |  | -0.00038 |  |  | 0.07484 |  | 1 | CAPACITY
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 101.16 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00038 |  |  | 0.04435 |  | 1 | CAPACITY | HOPEWELL HCF
208904 | HOLT 696 | 13.2 | 229 | 60 | 23 | 58.4 | 46.89 |  |  | -0.00038 |  |  | 0.07484 |  | 1 | CAPACITY
208903 | HOLT 695 | 13.2 | 229 | 60 | 26 | 53.2 | 42.71 |  |  | -0.00038 |  |  | 0.07484 |  | 1 | CAPACITY
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00038 |  |  | 0.10478 |  | 1 | CAPACITY
919535 | V4-027 E | 0 | 229 | 75 | 0 | 3.1 | 0 |  |  | -0.00038 |  |  | 0 |  | 1 | NEWENERGY | V4-027
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 3.93 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY | V4-027
208474 | KINZ 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY
314177 | 3HAYES89 | 115 | 345 | 75 | 0 | 0.31 | 0 |  |  | -0.00038 |  |  | 0 |  | 1 | NEWENERGY
313828 | 3WHITEMARSH | 115 | 345 | 75 | 0 | 0.05 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 788.9 | 633.38 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 422.86 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY | AB2-134
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00039 |  |  | 0.04435 |  | 1 | CAPACITY | WARREN COUNTY CC
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY | AB2-160
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY | AB2-190
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 89.92 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | AB2-190
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 57.65 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | AB2-134
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 24.41 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | AB2-160
316158 | AD2-164 | 230 | 345 | 57 | 0 | 26.7 | 21.44 |  |  | -0.00039 |  |  | 0.08446 |  | 1 | CAPACITY
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 12.04 |  |  | -0.00039 |  |  | 0.12623 |  | 1 | CAPACITY
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 8.03 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY
313812 | 6ROCKLANDING | 230 | 345 | 75 | 0 | 0.11 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 678.09 |  |  | -0.00039 |  |  | 0.01494 |  | 1 | CAPACITY
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 677.21 |  |  | -0.00039 |  |  | 0.01494 |  | 1 | CAPACITY
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AB2-161
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 69.77 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 69.69 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
314331 | 6POE | 230 | 345 | 75 | 0 | 12.27 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AD1-060
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AE1-162
935212 | AD1-156 E | 230 | 345 | 75 | 0 | 7.92 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AD1-156
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 23.76 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AB2-161
316258 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AE1-162
935211 | AD1-156 C | 230 | 345 | 75 | 0 | 11.82 | 9.49 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AD1-156
314533 | 6SMITFLD | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY
934362 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 4.58 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AD1-060
314525 | 6KINGFORK | 230 | 345 | 75 | 0 | 24.3 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
314550 | 6HICKORY | 230 | 345 | 75 | 0 | 22.93 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 88.96 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 87.83 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 86.31 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
314466 | 6FENTRES | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | Z1-068
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AC1-147
316145 | AE1-027 E | 230 | 345 | 75 | 0 | 6.9 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AE1-027
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AC2-196
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AC1-027
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AB2-026
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AE1-075
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AD1-144
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AD2-215
316147 | AE1-028 E | 230 | 345 | 75 | 0 | 4.4 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AE1-028
314333 | 6POWHATN | 230 | 345 | 75 | 0 | 3.97 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AB2-026
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 12.2 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 11.96 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
316144 | AE1-027 C | 230 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AE1-027
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 10.36 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
926661 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 10.12 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AC1-147
938561 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AE1-075
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 9.55 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 9.05 |  |  | -0.0004 |  |  | 0.12623 |  | 1 | CAPACITY
933731 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 8.03 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AC2-196
316150 | AD2-215 C | 230 | 345 | 76 | 0 | 9.8 | 7.87 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AD2-215
935111 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 7.79 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AD1-144
314491 | 3PENDLTN | 115 | 345 | 75 | 0 | 1.89 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AC1-027
316146 | AE1-028 C | 230 | 345 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AE1-028
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.2 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | Z1-068
314453 | 6CHRHLND | 230 | 345 | 75 | 0 | 0.08 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY
314487 | 3MCLAUGH | 115 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AA1-139
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 63.18 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AA1-139
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | Y1-086
314632 | 6AYDLETOLD | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
313717 | 6SLIGO L2192 | 230 | 345 | 75 | 0 | 12.34 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | AB2-022
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | Z2-030
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AC2-174
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | Z2-027
933571 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEW | AC2-174
314645 | 6SLIGO L269 | 230 | 345 | 75 | 0 | 3.22 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 12.04 |  |  | -0.00041 |  |  | 0.12623 |  | 1 | CAPACITY
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 10.44 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | AB2-022
314648 | 6SUNBURY | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 3.93 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | Z2-030
314638 | 6ELIZ CT | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | Y1-086
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 1.61 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY
314639 | 6TANGLEW | 230 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | Z2-027
314640 | 6KITTY HAWK | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
901082 | W1-029 E | 230 | 345 | 74 | 0 | 261 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | W1-029
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | W1-029
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY | AB2-025
314651 | 6WINFALL | 230 | 345 | 75 | 0 | 3.35 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY
314435 | 6SAPONY | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY | AB2-025
942852 | AE2-304 E | 230 | 345 | 75 | 0 | 1.4 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY | AE2-304
942851 | AE2-304 C | 230 | 345 | 75 | 0 | 3.3 | 2.65 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY | AE2-304
314662 | 6S HERTFORD | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.56 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY | Z1-036
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | -0.00044 |  |  | 0.10478 |  | 1 | ENERGY
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY | Z1-036
314637 | 6EDENTON | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00044 |  |  | 0 |  | 1 | NEWENERGY | AA2-059
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 480.11 |  |  | -0.00044 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 452.01 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00044 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00044 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-086
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00044 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00045 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNSWICK COUNTY
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 0 |  |  | -0.00044 |  |  | 0 |  | 1 | NEW | AB2-015
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 0 |  |  | -0.00044 |  |  | 0 |  | 1 | NEWENERGY | AB2-015
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00045 |  |  | 0 |  | 1 | NEWENERGY | AA2-178
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | AA2-178
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00045 |  |  | 0.10478 |  | 1 | CAPACITY
314541 | 3WATKINS | 115 | 345 | 1 | 0 | 4 | 0 |  |  | -0.00045 |  |  | 0 |  | 1 | ENERGY
314566 | 3CRESWEL | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00045 |  |  | 0 |  | 1 | NEWENERGY
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 322.35 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AA2-088
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 198.31 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00046 |  |  | 0.04435 |  | 1 | CAPACITY | BEAR GARDEN
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00046 |  |  | 0.04435 |  | 1 | CAPACITY | FLUVANNA
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 30.51 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AA2-088
314594 | 6PLYMOTH | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 2
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AB1-128
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AB1-127
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AC1-116
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AC2-071
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AB2-100 2
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AB2-100 1
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AB2-045
314589 | 3MURPHYS | 115 | 345 | 75 | 0 | 4.66 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | V4-068
932511 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AC2-071
314677 | 6BUCKING | 230 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AB2-045
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | V4-068
235041 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AB1-128
235040 | 01AB1-127 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AB1-127
314620 | 6CASHIE | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY
926451 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 3.77 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AC1-116
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY
313826 | 6HYDRAULIC | 230 | 345 | 75 | 0 | 0.04 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AB2-174
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AA1-065
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AA1-063A
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 53.6 | 43.03 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AA1-065
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 40.87 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | AA1-063A
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 40.14 |  |  | -0.00047 |  |  | 0.19858 |  | 1 | CAPACITY
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 33.72 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | AB2-174
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEW
314617 | 3TUNIS | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY
314568 | 3EARLEYS | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AB2-099
314551 | 3AHOSKIE | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY
314626 | 3WOODLND | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AB2-099
314604 | 3SEABORD | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.5 | 354.46 |  |  | -0.00049 |  |  | 0.10478 |  | 1 | CAPACITY
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 350.93 |  |  | -0.00049 |  |  | 0.10478 |  | 1 | CAPACITY
923262 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
923991 | AB2-040 C O1 | 115 | 345 | 75 | 0 | 44 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEW | AB2-040
923992 | AB2-040 E O1 | 115 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AB2-040
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
925122 | AB2-169 E | 115 | 345 | 75 | 0 | 35 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AB2-169
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AA2-053
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.00048 |  |  | 0.07484 |  | 1 | CAPACITY
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.00048 |  |  | 0.07484 |  | 1 | CAPACITY
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 76.6 | 61.5 |  |  | -0.00049 |  |  | 0.04435 |  | 1 | CAPACITY | ROSEMARY
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 44 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AA2-053
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 40.38 |  |  | -0.00049 |  |  | 0.07484 |  | 1 | CAPACITY
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 38.54 |  |  | -0.00049 |  |  | 0.07484 |  | 1 | CAPACITY
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 47.5 | 38.13 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 32.44 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | AB1-173
925121 | AB2-169 C | 115 | 345 | 75 | 0 | 39 | 31.31 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AB2-169
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 35.9 | 28.82 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AB1-173
314579 | 6HORNRTN | 230 | 345 | 75 | 0 | 3.91 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
314266 | 6NORTHAMPTON | 230 | 345 | 75 | 0 | 2.47 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 8.83 |  |  | -0.00049 |  |  | 0.12623 |  | 1 | CAPACITY
314559 | 3CAROLNA | 115 | 345 | 75 | 0 | 1.21 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
314596 | 3POPLR C | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
314582 | 3KELFORD | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | Z2-043
314762 | 3JAMES R | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AD1-085
314713 | 3PAMPLIN | 115 | 345 | 75 | 0 | 9.73 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY
314807 | 3MT JACK | 115 | 345 | 75 | 0 | 9.7 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
316143 | AD1-160 E | 115 | 345 | 75 | 0 | 9.1 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | AD1-160
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | AD1-157
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AC2-074
314578 | 3HORNRTN | 115 | 345 | 75 | 0 | 5.15 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
313853 | 3PONTONDP | 115 | 345 | 2 | 0 | 4 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | ENERGY
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 16 | 12.85 |  |  | -0.0005 |  |  | 0.12623 |  | 1 | CAPACITY
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 9.88 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AD1-085
314603 | 3SCOT NK | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY
932541 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AC2-074
935221 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | AD1-157
316142 | AD1-160 C | 115 | 345 | 75 | 0 | 6.6 | 5.3 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | AD1-160
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 1.04 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.64 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY | AC1-036
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00051 |  |  | 0.08446 |  | 1 | CAPACITY
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00051 |  |  | 0.08446 |  | 1 | CAPACITY
314593 | 3PARMELE | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY
925611 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 6.9 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | AC1-036
314629 | 3MARTNCO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY
314798 | 3MERCK5 | 115 | 345 | 75 | 0 | 0.16 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY | AC1-054
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 35.73 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | AC1-054
314574 | 6EVERETS | 230 | 345 | 75 | 0 | 5.89 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY | AE1-099
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY | AE1-098
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AA1-067
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | AE1-099
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | AE1-098
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AB2-043
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AB2-060
919702 | AA2-057 E OP | 115 | 345 | 75 | 0 | 21.1 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AA2-057
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 43.67 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | AB2-060
313719 | 3CHESTNUT | 115 | 345 | 75 | 0 | 44.7 | 35.89 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | AA2-057
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AB2-077
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AB2-078
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AB2-079
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 15.17 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | AB2-043
924301 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00052 |  |  | 0 |  | 1 | NEW | AB2-077
924321 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00052 |  |  | 0 |  | 1 | NEW | AB2-079
924311 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00052 |  |  | 0 |  | 1 | NEW | AB2-078
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY | Z2-088
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 53 | 42.55 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | Z2-088
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
314608 | 3TARBORO | 115 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY | Z2-044
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 12.04 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
314623 | 3WITAKRS | 115 | 345 | 75 | 0 | 2.51 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | Z2-044
314549 | 3TOT1 | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY
314557 | 3BETHELC | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY
314607 | 3TAR RVR | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY
314545 | 3TOT5 | 115 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY
314560 | 3CNETO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY | AB2-059
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY | AB1-081
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 52.99 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | AB2-059
922922 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | AB1-081
314554 | 3BTLEBRO | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY
314205 | 3HEARTS | 115 | 345 | 75 | 0 | 0.41 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 0 |  |  | -0.00055 |  |  | 0 |  | 1 | NEWENERGY | T157
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 0 |  |  | -0.00055 |  |  | 0 |  | 1 | NEWENERGY | AC1-105
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 36.61 |  |  | -0.00055 |  |  | 0.10478 |  | 1 | CAPACITY
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 27.7 |  |  | -0.00055 |  |  | 0 |  | 1 | CAPACITY | AC1-105
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 16.46 |  |  | -0.00055 |  |  | 0 |  | 1 | CAPACITY | T157
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 404.48 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 403.68 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 403.27 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 403.2 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315616 | AA1-038 C | 230 | 345 | 74 | 0 | 76.6 | 0 |  |  | -0.00057 |  |  | 0 |  | 1 | NEW | AA1-038
918232 | AA1-038 E | 230 | 345 | 74 | 0 | 66.7 | 0 |  |  | -0.00057 |  |  | 0 |  | 1 | NEWENERGY | AA1-038
314860 | 4E MILL | 138 | 345 | 2 | 0 | 50 | 0 |  |  | -0.00057 |  |  | 0.10478 |  | 1 | ENERGY
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 20.23 |  |  | -0.00057 |  |  | 0.10478 |  | 1 | CAPACITY
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 20.15 |  |  | -0.00057 |  |  | 0.10478 |  | 1 | CAPACITY
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00057 |  |  | 0 |  | 1 | CAPACITY
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 0 |  |  | -0.00058 |  |  | 0 |  | 1 | NEWENERGY | K11
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 30.67 |  |  | -0.00058 |  |  | 0 |  | 1 | CAPACITY | K11
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 443.98 |  |  | -0.00059 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM2
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 440.13 |  |  | -0.00059 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 419.81 |  |  | -0.00059 |  |  | 0.10478 |  | 1 | CAPACITY
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 9.55 |  |  | -0.00059 |  |  | 0.08446 |  | 1 | CAPACITY
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 0 |  |  | -0.00062 |  |  | 0 |  | 1 | NEWENERGY | AC1-075
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 30.75 |  |  | -0.00062 |  |  | 0 |  | 1 | CAPACITY | AC1-075
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 0 |  |  | -0.00062 |  |  | 0 |  | 1 | NEWENERGY | AC1-080
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 23.68 |  |  | -0.00062 |  |  | 0.12623 |  | 1 | CAPACITY
926023 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 10.28 |  |  | -0.00062 |  |  | 0 |  | 1 | CAPACITY | AC1-080
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 68.3 |  |  |  | -0.0006
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 91.93 |  |  | -0.00064 |  |  | 0.07484 |  | 1 | CAPACITY
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 61.42 |  |  | -0.00064 |  |  | 0.07484 |  | 1 | CAPACITY
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.00065 |  |  | 0.08446 |  | 1 | CAPACITY
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 77.88 |  |  | -0.00068 |  |  | 0.07484 |  | 1 | CAPACITY
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 51.78 |  |  | -0.00068 |  |  | 0.07484 |  | 1 | CAPACITY
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 51.38 |  |  | -0.00068 |  |  | 0.07484 |  | 1 | CAPACITY
244012 | 05PINNACLE | 4 | 205 | 1 | 0 | 11 | 0 |  |  | -0.00069 |  |  | 0.10478 |  | 1 | ENERGY
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 42.07 |  |  | -0.00069 |  |  | 0.10478 |  | 1 | CAPACITY
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 0 |  |  | -0.0007 |  |  | 0 |  | 1 | NEWENERGY | AC1-145
926645 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.0007 |  |  | 0 |  | 1 | CAPACITY | AC1-145
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.9 | 40.06 |  |  | -0.00071 |  |  | 0.07484 |  | 1 | CAPACITY
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 1044 |  |  |  | -0.0007
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 154.95 |  |  | -0.00072 |  |  | 0.0316 |  | 1 | CAPACITY
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 152.54 |  |  | -0.00072 |  |  | 0.0316 |  | 1 | CAPACITY
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 97.14 |  |  | -0.00072 |  |  | 0.0316 |  | 1 | CAPACITY
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 59.41 |  |  | -0.00072 |  |  | 0.0316 |  | 1 | CAPACITY
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 57 |  |  | -0.00072 |  |  | 0.0316 |  | 1 | CAPACITY
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 3.21 |  |  | -0.00073 |  |  | 0 |  | 1 | CAPACITY
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | AC1-048
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEW | AC1-048
205910 | AC2-053 E | 0.39 | 227 | 74 | 0 | 12.4 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | AC2-053
205909 | AC2-053 C | 0.39 | 227 | 74 | 0 | 7.6 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEW | AC2-053
208876 | WLAN | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00074 |  |  | 0 |  | 1 | CAPACITY
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 144.51 |  |  | -0.00077 |  |  | 0.10478 |  | 1 | CAPACITY
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | NEWENERGY | AC1-117
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | -0.00077 |  |  | 0.05 |  | 1 | MTX | AA1-100
926461 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | NEW | AC1-117
208769 | SISO | 12.5 | 229 | 2 | 0 | 2.48 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | ENERGY
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 6.42 |  |  | -0.00077 |  |  | 0 |  | 1 | CAPACITY
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.0008 |  |  | 0 |  | 1 | NEWENERGY | AD1-018
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.0008 |  |  | 0 |  | 1 | NEW | AD1-018
235520 | 01WVACO_S38 | 13.8 | 201 | 2 | 0 | 60 | 0 |  |  | -0.00081 |  |  | 0 |  | 1 | NEW
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00081 |  |  | 0.07484 |  | 1 | CAPACITY
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00081 |  |  | 0.07484 |  | 1 | CAPACITY
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 8.59 |  |  | -0.0008 |  |  | 0 |  | 1 | CAPACITY | N47
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 0 |  |  | -0.00082 |  |  | 0 |  | 1 | NEWENERGY | U2-073 A
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 0 |  |  | -0.00082 |  |  | 0 |  | 1 | NEWENERGY | U2-073 B
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 25.9 | 20.79 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY | U2-073 A
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY | U2-073 B
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 3.29 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY
270148 | AE1-018 E | 138 | 205 | 75 | 0 | 2.2 | 0 |  |  | -0.00082 |  |  | 0 |  | 1 | NEWENERGY | AE1-018
270147 | AE1-018 C | 138 | 205 | 75 | 0 | 2.8 | 2.25 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY | AE1-018
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | NEWENERGY | S14
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 11.24 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | S14
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 0 |  |  | -0.00084 |  |  | 0 |  | 1 | NEWENERGY | Y1-006
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 0 |  |  | -0.00085 |  |  | 0 |  | 1 | NEWENERGY | U2-030
913034 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 0 |  |  | -0.00084 |  |  | 0 |  | 1 | NEW | Y1-006
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | -0.00084 |  |  | 0.07484 |  | 1 | ENERGY
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00084 |  |  | 0 |  | 1 | MTX | AD2-205
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 14.1 | 11.32 |  |  | -0.00084 |  |  | 0.07484 |  | 1 | CAPACITY
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.7 | 7.79 |  |  | -0.00084 |  |  | 0 |  | 1 | CAPACITY
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 6.26 |  |  | -0.00085 |  |  | 0 |  | 1 | CAPACITY | U2-030
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00087 |  |  | 0.08446 |  | 1 | CAPACITY
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00087 |  |  | 0.08446 |  | 1 | CAPACITY
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00087 |  |  | 0.08446 |  | 1 | CAPACITY
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00088 |  |  | 0.08446 |  | 1 | CAPACITY
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00088 |  |  | 0.08446 |  | 1 | CAPACITY
242677 | 05INDDRV | 138 | 205 | 64 | 0 | 45 | 36.13 |  |  | -0.00087 |  |  | 0.12623 |  | 1 | CAPACITY
923772 | AB2-011 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00088 |  |  | 0 |  | 1 | NEWENERGY | AB2-011
923762 | AB2-010 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00088 |  |  | 0 |  | 1 | NEWENERGY | AB2-010
923761 | AB2-010 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00088 |  |  | 0 |  | 1 | NEW | AB2-010
923771 | AB2-011 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00088 |  |  | 0 |  | 1 | NEW | AB2-011
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  |  |  | -0.0009
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 489.98 |  |  | -0.00089 |  |  | 0.10478 |  | 1 | CAPACITY
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 127.4 | 102.28 |  |  | -0.00089 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 101.08 |  |  | -0.00089 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 106.7 | 85.67 |  |  | -0.00089 |  |  | 0 |  | 1 | CAPACITY
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 84.78 |  |  | -0.00089 |  |  | 0 |  | 1 | CAPACITY
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  |  |  | -0.0009
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 38 |  |  |  | -0.0009
903052 | W2-094 E | 115 | 227 | 75 | 0 | 1.9 | 0 |  |  | -0.0009 |  |  | 0 |  | 1 | NEWENERGY | W2-094
205911 | 27W2-094 | 115 | 227 | 75 | 0 | 1.1 | 0 |  |  | -0.0009 |  |  | 0 |  | 1 | NEWENERGY | W2-094
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 0 |  |  | -0.00091 |  |  | 0 |  | 1 | NEWENERGY | K28
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 0 |  |  | -0.00091 |  |  | 0 |  | 1 | NEWENERGY | K28
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.4 | 13.97 |  |  | -0.00091 |  |  | 0 |  | 1 | CAPACITY | K28
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 1.3 | 1.04 |  |  | -0.00091 |  |  | 0 |  | 1 | CAPACITY
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 896 |  |  |  | -0.0009
209030 | FRFA O01 | 12.5 | 229 | 2 | 0 | 3.2 | 0 |  |  | -0.00092 |  |  | 0 |  | 1 | NEW
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 0.4 | 0.32 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY | V3-051
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 180.64 |  |  | -0.00093 |  |  | 0.10478 |  | 1 | CAPACITY
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 93.13 |  |  | -0.00093 |  |  | 0.10478 |  | 1 | CAPACITY
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 64.23 |  |  | -0.00093 |  |  | 0.07484 |  | 1 | CAPACITY
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 56.2 |  |  | -0.00094 |  |  | 0.07484 |  | 1 | CAPACITY
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00094 |  |  | 0.07484 |  | 1 | CAPACITY
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00094 |  |  | 0 |  | 1 | CAPACITY
342070 | 2PINE GROVE | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00094 |  |  | 0 |  | 1 | CAPACITY
342442 | 2W GLASGOW | 69 | 320 | 2 | 0 | 1 | 0.8 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | NEWENERGY | M24
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | NEWENERGY | AB1-150
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | -0.00095 |  |  | 0.05 |  | 1 | MTX | M24 BAT
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | M24
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00094 |  |  | 0.07484 |  | 1 | CAPACITY
931011 | AB1-150 C | 138 | 201 | 74 | 0 | 6.7 | 5.38 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | AB1-150
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 244.87 |  |  | -0.00096 |  |  | 0.10478 |  | 1 | CAPACITY
247225 | 05FTHLG2 | 18 | 205 | 57 | 120 | 173.8 | 139.54 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247224 | 05FTHLG1 | 18 | 205 | 57 | 120 | 173.7 | 139.46 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247231 | 05RIVRG2 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247230 | 05RIVRG1 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247232 | 05RIVRG3 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.55 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1067.8 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY | AMG3
918472 | AA1-062 E | 138 | 201 | 74 | 0 | 195 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | AA1-062
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 642.29 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 642.29 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | P59
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | NEWENERGY | U2-061
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00097 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 2
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00097 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
292981 | N-007 E | 138 | 201 | 74 | 0 | 30.4 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | N07
235801 | 01WM_AA1_062 | 138 | 201 | 74 | 0 | 29 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEW | AA1-062
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 109.5 | 87.91 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
920072 | AA2-103 E | 138 | 201 | 76 | -20 | 20 | 0 |  |  | -0.00096 |  |  | 0.05 |  | 1 | MTX | AA2-103
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 60.94 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 60.78 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 60.7 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 60.53 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 72.9 | 58.53 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 72.6 | 58.29 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
925972 | AC1-073 E | 138 | 201 | 74 | 0 | 5.9 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | AC1-073
925971 | AC1-073 C | 138 | 201 | 74 | 0 | 5.8 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEW | AC1-073
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 11.88 |  |  | -0.00097 |  |  | 0.07484 |  | 1 | CAPACITY
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 9.39 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY | P59
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | MTX | AB1-055
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY | K19
235000 | N-007 C | 138 | 201 | 74 | 0 | 7.6 | 6.1 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY | N07
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 5.22 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | U2-061
341329 | 2COLESBURG | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  |  |  | -0.001
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 62.8 |  |  |  | -0.001
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 55 | 44.16 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | -0.001
342031 | 2PACTOLUS | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY
237085 | AD2-192 GEN | 23 | 201 | 57 | 0 | 600 | 0 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | NEW
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1396 | 1120.79 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | GVG2
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1371 | 1100.72 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | GVG1
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | X2-022
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 570.03 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | W2-048
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 52.91 |  |  | -0.00099 |  |  | 0.07484 |  | 1 | CAPACITY
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 19.5 | 15.66 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
341584 | 2GRIFFIN | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY
341200 | 2BROMLEYEK | 69 | 320 | 2 | 0 | 2 | 1.61 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY
293798 | W4-005 E | 0.69 | 222 | 74 | 0 | 305.37 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | W4-005
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1088.67 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | RKG1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1356 | 1088.67 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | MTG1
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1043.71 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | RKG2
274656 | BYRON ;1U | 25 | 222 | 45 | 700 | 1168.5 | 938.14 |  |  | -0.001 |  |  | 0.01494 |  | 1 | CAPACITY
274657 | BYRON ;2U | 25 | 222 | 45 | 700 | 1141.5 | 916.46 |  |  | -0.001 |  |  | 0.01494 |  | 1 | CAPACITY
274663 | QUAD CITI;2U | 18 | 222 | 48 | 150 | 911.7 | 731.97 |  |  | -0.00099 |  |  | 0.01494 |  | 1 | CAPACITY
274662 | QUAD CITI;1U | 18 | 222 | 48 | 150 | 911.1 | 731.48 |  |  | -0.00099 |  |  | 0.01494 |  | 1 | CAPACITY
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | Z2-087
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | S27
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | S28
235587 | 01HARRN3 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
235586 | 01HARRN2 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
235585 | 01HARRN1 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 124 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | ENERGY | L05_CE22
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 443.18 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 437.96 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 409.46 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | P36 1
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | P36 2
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | AC1-089
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O29 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | P26
293516 | O-009 E1 | 0.69 | 222 | 74 | 0 | 82.04 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O09 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | P11 2
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | P11 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | P46
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O35
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 240.86 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O29 2
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | NQ71
293518 | O-009 E3 | 0.57 | 222 | 74 | 0 | 45.89 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O09 3
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 45.5 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | Z1-073
916211 | Z1-072 E | 0.6 | 222 | 74 | 0 | 44.8 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | Z1-072
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O29 3
293517 | O-009 E2 | 0.6 | 222 | 74 | 0 | 41.67 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O09 2
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 144.51 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 136.16 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | NELSON
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 135.12 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | NELSON
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 134.32 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 134.16 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | CORDOVA
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 31.5 |  |  |  | -0.001
919221 | AA1-146 | 345 | 222 | 58 | 0 | 157 | 126.05 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CLIF5
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CLIF1
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF2
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CLIF3
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CLIF4
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CLIF6
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 99.47 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | NELSON
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 98.59 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | NELSON
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | NQ72
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 133.1 | 153 | 133.28 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 129.7 | 149.1 | 129.88 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 128.6 | 147.8 | 128.75 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 67.52 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF1
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF4
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF5
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CLIF2
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF3
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF6
926103 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 45.76 |  |  | -0.001 |  |  | 0.05 |  | 1 | NEW | AC1-089
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 36.93 |  |  | -0.00099 |  |  | 0.07484 |  | 1 | CAPACITY
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 36.61 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | W4-005
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 28.74 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | S28
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 27.94 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | S27
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | L05_CE22
274889 | BRIGHTSTK;1U | 0.7 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Z2-087
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 17.58 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O29 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 17.58 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | P26
293513 | O-009 C1 | 0.69 | 222 | 74 | 0 | 20.5 | 16.46 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O09 1
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | P11 2
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | P11 1
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 15.58 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | P46
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | P36 2
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | P36 1
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 13.3 | 10.68 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Z1-073
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 9.64 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O29 2
293515 | O-009 C3 | 0.57 | 222 | 74 | 0 | 11.5 | 9.23 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O09 3
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 8.91 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O29 3
293514 | O-009 C2 | 0.6 | 222 | 74 | 0 | 10.4 | 8.35 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O09 2
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 10.3 | 8.27 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O35
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 10 | 8.03 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Z1-072
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.6 | 7.71 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY
295108 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 5.7 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | NQ71
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 5.14 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY
342550 | 4BAVARIAN LF | 138 | 320 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY
295110 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 2.57 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | NQ72
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 949.78 |  |  | -0.00101 |  |  | 0.01494 |  | 1 | CAPACITY
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 926.5 |  |  | -0.00101 |  |  | 0.01494 |  | 1 | CAPACITY
274661 | LASCO STA;2U | 25 | 222 | 49 | 150 | 1135.9 | 911.97 |  |  | -0.00101 |  |  | 0.01494 |  | 1 | CAPACITY
274660 | LASCO STA;1U | 25 | 222 | 49 | 150 | 1131.2 | 908.19 |  |  | -0.00101 |  |  | 0.01494 |  | 1 | CAPACITY
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 200 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | Q57
274658 | DRESDEN ;2U | 18 | 222 | 48 | 150 | 902.5 | 724.58 |  |  | -0.001 |  |  | 0.01494 |  | 1 | CAPACITY
274659 | DRESDEN ;3U | 18 | 222 | 48 | 150 | 895.5 | 718.96 |  |  | -0.001 |  |  | 0.01494 |  | 1 | CAPACITY
930042 | AB1-006 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | AB1-006
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | U3-002 2
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O50
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 159.7 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | S06
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Q01 3
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O22 2
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | P10
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 589.3 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | ZIMM
293799 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | S36
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | S37
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | AA1-018
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Q01 4
253314 | AC1-085 A_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 A
253317 | AC1-085 B_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 B
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O51 1
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O51 2
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | N15
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 470.47 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | ZIMM
927091 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-204
927093 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AC1-204
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 415.88 |  |  | -0.00101 |  |  | 0.10478 |  | 1 | CAPACITY
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 415.88 |  |  | -0.00101 |  |  | 0.10478 |  | 1 | CAPACITY
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
274687 | WILL CNTY;4U | 20 | 222 | 15 | 0 | 510 | 409.46 |  |  | -0.00101 |  |  | 0.10478 |  | 1 | CAPACITY | WILL4
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Q01 21
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 81.6 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O22 1
247943 | T-127 E | 0.74 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | T127 5
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | T126 2
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | T126 3
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | T127 4
247903 | 05FR-22G E | 0.69 | 205 | 75 | 0 | 78.8 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Q01 22
247900 | 05FR-11G E | 0.6 | 205 | 75 | 0 | 78.3 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Q01 11
930062 | AB1-014 E | 138 | 212 | 75 | 0 | 77.5 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | AB1-014
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 522.66 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Q01 12
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 284.53 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK8
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 263.34 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK7
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-169
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AB1-169
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 294 | 236.04 |  |  | -0.00101 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-079
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 225.6 |  |  | -0.00101 |  |  | 0.10478 |  | 1 | CAPACITY
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AB1-169
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 219 | 175.82 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Z1-079
274708 | KENDALL ;3C | 18 | 222 | 58 | 140 | 184.3 | 147.97 |  |  | -0.00101 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 3
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 146.36 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 1
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 146.36 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 2
274710 | KENDALL ;4C | 18 | 222 | 58 | 138 | 182.3 | 146.36 |  |  | -0.00101 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 4
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 1
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 2
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 132.47 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 131.75 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 130.06 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | -0.001 |  |  | 0.08446 |  | 1 | ENERGY
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 99.72 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | KYG1
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | KYG2
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | KYG4
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | KYG3
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | KYG5
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 97.87 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Kendall 1
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 97.87 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Kendall 2
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 97.87 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Kendall 3
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 97.87 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Kendall 4
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 96.42 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 115.4 | 92.65 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | EQUISTAR MORRIS
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 75.6 | 104 | 83.5 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 72.7 | 101.6 | 81.57 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.001 |  |  | 0.05 |  | 1 | MTX | AA2-123
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.001 |  |  | 0.05 |  | 1 | MTX | Z1-108
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00101 |  |  | 0.05 |  | 1 | MTX | Z1-107
276592 | O-012 C | 138 | 222 | 64 | 0 | 20 | 0 |  |  | -0.00101 |  |  | 0.12623 |  | 1 | ENERGY
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 80.93 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 71.2 | 100.6 | 80.77 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 80.21 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
243415 | 05WWVSTA | 69 | 205 | 61 | 60 | 96 | 77.08 |  |  | -0.00101 |  |  | 0.07484 |  | 1 | CAPACITY
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 65.51 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 81.5 | 65.43 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.8 | 64.87 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 64.31 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 62.14 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
250166 | HLCRST AB114 | 138 | 212 | 75 | 0 | 76 | 61.02 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AB1-014
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | AC1-085 A
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | AC1-085 B
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 58.77 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 58.45 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | KYG1
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | KYG3
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | KYG4
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | KYG2
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | KYG5
251957 | 08MADSN6 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251959 | 08MADSN8 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251955 | 08MADSN4 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251956 | 08MADSN5 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251958 | 08MADSN7 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251952 | 08MADSN1 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251953 | 08MADSN2 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251954 | 08MADSN3 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 56.84 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 55.4 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251828 | CLNTESP1 | 34.5 | 212 | 76 | 0 | 12 | 0 |  |  | -0.001 |  |  | 0.05 |  | 1 | MTX | Z1-080
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 43.03 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.001 |  |  | 0.05 |  | 1 | MTX | Z1-106
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.001 |  |  | 0.05 |  | 1 | MTX | Z1-106
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 40.54 |  |  | -0.00101 |  |  | 0.04435 |  | 1 | CAPACITY | MIDDLETOWN COKE
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Q57
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O50
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.001 |  |  | 0.07484 |  | 1 | CAPACITY
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.001 |  |  | 0.07484 |  | 1 | CAPACITY
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.001 |  |  | 0.07484 |  | 1 | CAPACITY
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 28.18 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O22 2
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | S36
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | S37
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 42.68 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 42.6 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 42.51 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -0.001 |  |  | 0.05 |  | 1 | MTX | Z1-065
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 24.08 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 23.36 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Q01 4
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | X3-005
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 20.3 | 27.6 | 22.16 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 22 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | N15
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 21.68 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
930041 | AB1-006 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | AB1-006
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 20.79 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | S06
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 20.63 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Q01 11
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 20.07 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O51 2
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O51 1
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 16.22 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | T127 5
274891 | OTTER CRK;1U | 0.69 | 222 | 74 | 0 | 19.5 | 15.66 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AA1-018
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 14.77 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O22 1
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 12.28 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | T126 3
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | T126 2
276173 | Z2-081 | 138 | 222 | 2 | 0 | 13.3 | 10.68 |  |  | -0.001 |  |  | 0.12623 |  | 1 | CAPACITY
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 10.6 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | U3-002 1
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Q01 22
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Q01 21
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 10.36 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 10.28 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | U3-002 2
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Q01 12
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Q01 3
904211 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 9.71 |  |  | -0.001 |  |  | 0.07484 |  | 1 | CAPACITY
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 9.47 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | T127 4
904201 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 8.51 |  |  | -0.00101 |  |  | 0.07484 |  | 1 | CAPACITY
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 8.19 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | P10
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | MTX | Y3-099
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | MTX | Y3-100
276159 | W4-082 | 138 | 222 | 64 | 0 | 5.8 | 4.66 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.8 | 3.85 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 2.73 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | X3-005
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1402 |  |  |  | -0.001
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | U2-090
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | V3-007
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | AC2-176
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | S71
902531 | W2-040 C | 69 | 209 | 75 | 0 | 20 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEW | W2-040
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 80.69 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 64.23 |  |  | -0.00101 |  |  | 0.10478 |  | 1 | CAPACITY
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
902532 | W2-040 E | 69 | 209 | 75 | 0 | 12.4 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | W2-040
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 60 | 48.17 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 48.09 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 47.93 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 46.65 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 46.41 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 37.49 |  |  | -0.00101 |  |  | 0.07484 |  | 1 | CAPACITY
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | U2-090
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | V3-007
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 19.27 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | S71
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 22.91 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
933594 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 13.57 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | AC2-176
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | V4-073
247968 | Z2-115 E | 12 | 205 | 74 | 0 | 1.25 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Z2-115
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.76 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 1 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Z2-115
904721 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | V4-073
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1148 | 921.68 |  |  | -0.00102 |  |  | 0.01494 |  | 1 | CAPACITY
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 814.5 |  |  | -0.00103 |  |  | 0.01494 |  | 1 | CAPACITY
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00103 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-116
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | AA2-116
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 268.96 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 267.35 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | AA2-116
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 201.52 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | X2-052
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 193.49 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00102 |  |  | 0.04435 |  | 1 | CAPACITY | X2-052
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | X2-052
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 162.9 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | AC2-067
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | AC1-165
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | AC1-166
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | AC1-068
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | AC1-069
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | AC1-068
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | AC1-069
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | AC1-165
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | AC1-166
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 21.28 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | AC2-067
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00102 |  |  | 0.12623 |  | 1 | CAPACITY
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 8.03 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY
247969 | Z2-116 E | 138 | 205 | 76 | 0 | 1.3 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | Z2-116
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 4.82 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 3.13 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.8 | 2.25 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 2.09 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | Z2-116
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00104 |  |  | 0.08446 |  | 1 | CAPACITY
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00104 |  |  | 0.08446 |  | 1 | CAPACITY
927184 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -0.00104 |  |  | 0.05 |  | 1 | MTX | AC1-212
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 65.03 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 64.23 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 63.43 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
932312 | AC2-045 E | 69 | 205 | 75 | 0 | 6.2 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEWENERGY | AC2-045
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00104 |  |  | 0.07484 |  | 1 | CAPACITY
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00104 |  |  | 0.07484 |  | 1 | CAPACITY
932311 | AC2-045 C | 69 | 205 | 75 | 0 | 3.8 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEW | AC2-045
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00104 |  |  | 0.12623 |  | 1 | CAPACITY
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | Z2-113
AC1-212 | BATTERY_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | -0.001
247604 | X1-042 | 12 | 205 | 64 | 0 | 3 | 2.41 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 1.85 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | Z2-113
927183 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.53 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | AC1-212
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.5 | 1.2 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 120.8 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEWENERGY | R49
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEWENERGY | T131
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00105 |  |  | 0 |  | 1 | NEWENERGY | V1-011
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEWENERGY | AC1-173
247528 | 05COVRT1 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00104 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 1
247530 | 05COVRT3 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00104 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 3
247529 | 05COVRT2 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00104 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 2
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00105 |  |  | 0.08446 |  | 1 | CAPACITY
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00105 |  |  | 0.08446 |  | 1 | CAPACITY
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 120.19 |  |  | -0.00105 |  |  | 0.08446 |  | 1 | CAPACITY
247533 | 05COVRT6 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | Covert 3
247531 | 05COVRT4 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | Covert 1
247532 | 05COVRT5 | 16.5 | 205 | 58 | 90 | 131.2 | 105.33 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | Covert 2
247521 | T131 | 0.69 | 205 | 74 | 22.4 | 30 | 24.08 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | T131
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 18.39 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | R49
247607 | V1-011 C | 34.5 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY | V1-011
294740 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -0.00105 |  |  | 0 |  | 1 | ENERGY
926865 | AC1-173 C | 0.65 | 205 | 75 | 0 | 9.9 | 7.95 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | AC1-173
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | U2-072
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 94.4 | 0 |  |  | -0.00105 |  |  | 0 |  | 1 | NEWENERGY | R60 3
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00105 |  |  | 0 |  | 1 | NEWENERGY | R60 2
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00105 |  |  | 0 |  | 1 | NEWENERGY | R60 1
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 31.31 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | U2-072
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00105 |  |  | 0 |  | 1 | MTX
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 13.25 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY | R60 3
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY | R60 2
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY | R60 1
247919 | U2-041 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | U2-041
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | AB2-067
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00106 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-067
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00106 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-044
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 292.88 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 318.8 | 255.95 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY | RONCO
247506 | U2-041 C | 345 | 205 | 74 | 0 | 39 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | U2-041
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY | RONCO
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00107 |  |  | 0.04435 |  | 1 | CAPACITY | RONCO
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00106 |  |  | 0.04435 |  | 1 | CAPACITY | WATERFORD
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | V3-028
247549 | V3-028 C | 345 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | V3-028
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 618.28 |  |  | -0.00107 |  |  | 0.10478 |  | 1 | CAPACITY
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 533.66 |  |  | -0.00107 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-173
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 238.45 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00107 |  |  | 0.04435 |  | 1 | CAPACITY | WASHINGTON
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY
245413 | 05S FULTHA | 69 | 205 | 65 | 0 | 0.85 | 0 |  |  | -0.00108 |  |  | 0 |  | 1 | ENERGY
893022 | V2-006 E | 138 | 205 | 74 | 0 | 130.5 | 0 |  |  | -0.00108 |  |  | 0 |  | 1 | NEWENERGY | V2-006
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 225.4 | 180.96 |  |  | -0.00109 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 0 |  |  | -0.00109 |  |  | 0 |  | 1 | NEWENERGY | U1-059
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.00109 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.00109 |  |  | 0.04435 |  | 1 | CAPACITY | DRESDEN
893021 | V2-006 C | 138 | 205 | 74 | 0 | 19.5 | 0 |  |  | -0.00108 |  |  | 0 |  | 1 | NEWENERGY | V2-006
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 0 |  |  | -0.00109 |  |  | 0 |  | 1 | NEWENERGY | W1-056
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 0 |  |  | -0.00109 |  |  | 0 |  | 1 | NEWENERGY | U1-059
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.93 |  |  | -0.00109 |  |  | 0 |  | 1 | CAPACITY | W1-056
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.0011 |  |  | 0.08446 |  | 1 | CAPACITY
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.0011 |  |  | 0.08446 |  | 1 | CAPACITY
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.66 | 96.07 |  |  | -0.0011 |  |  | 0.08446 |  | 1 | CAPACITY
930262 | AB1-065 E | 34.5 | 201 | 75 | 0 | 6.8 | 0 |  |  | -0.00109 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 17.66 |  |  | -0.0011 |  |  | 0.08446 |  | 1 | CAPACITY
235013 | 01AB1-065 C | 34.5 | 201 | 75 | 0 | 4.1 | 0 |  |  | -0.00109 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 8.83 |  |  | -0.0011 |  |  | 0.10478 |  | 1 | CAPACITY
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00111 |  |  | 0.07484 |  | 1 | CAPACITY
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00111 |  |  | 0.07484 |  | 1 | CAPACITY
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 10.19 |  |  | -0.00112 |  |  | 0.10478 |  | 1 | CAPACITY
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 15.25 |  |  | -0.00112 |  |  | 0.07484 |  | 1 | CAPACITY
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 634.42 |  |  | -0.00113 |  |  | 0.10478 |  | 1 | CAPACITY
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEWENERGY | U4-028
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEWENERGY | U4-029
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00113 |  |  | 0.08446 |  | 1 | CAPACITY
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00113 |  |  | 0.08446 |  | 1 | CAPACITY
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00114 |  |  | 0 |  | 1 | NEW | U4-028
247552 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00114 |  |  | 0 |  | 1 | NEW | U4-029
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEWENERGY | V4-010
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 261.89 |  |  | -0.00115 |  |  | 0 |  | 1 | CAPACITY | OREGON
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 248.73 |  |  | -0.00115 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00115 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00115 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-107
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00115 |  |  | 0 |  | 1 | CAPACITY | OREGON
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00115 |  |  | 0.04435 |  | 1 | CAPACITY | OREGON
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00114 |  |  | 0.08446 |  | 1 | CAPACITY
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00114 |  |  | 0.10478 |  | 1 | CAPACITY
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00114 |  |  | 0.10478 |  | 1 | CAPACITY
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00114 |  |  | 0.08446 |  | 1 | CAPACITY
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 109.19 |  |  | -0.00115 |  |  | 0.10478 |  | 1 | CAPACITY
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEW | V4-010
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEWENERGY
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 10.68 |  |  | -0.00115 |  |  | 0.10478 |  | 1 | CAPACITY
924440 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 389.39 |  |  | -0.00115 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-093
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 364.2 | 292.4 |  |  | -0.00117 |  |  | 0 |  | 1 | CAPACITY | FREMONT
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 170 | 136.49 |  |  | -0.00117 |  |  | 0.04435 |  | 1 | CAPACITY | FREMONT
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 166.4 | 133.6 |  |  | -0.00117 |  |  | 0 |  | 1 | CAPACITY | FREMONT
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 4.41 |  |  | -0.00117 |  |  | 0 |  | 1 | CAPACITY | N32
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | -0.00117 |  |  | 0 |  | 1 | NEW | AB1-069
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00117 |  |  | 0.04435 |  | 1 | NEW | AB1-069
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00117 |  |  | 0 |  | 1 | NEW | AB1-069
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 780.51 |  |  | -0.00118 |  |  | 0.01494 |  | 1 | CAPACITY
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 8.03 |  |  | -0.0012 |  |  | 0 |  | 1 | CAPACITY
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 7.95 |  |  | -0.0012 |  |  | 0 |  | 1 | CAPACITY
936011 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 16.06 |  |  | -0.0012 |  |  | 0.10478 |  | 1 | CAPACITY
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 19.6 | 15.74 |  |  | -0.00122 |  |  | 0.08446 |  | 1 | CAPACITY
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 1.85 |  |  | -0.00122 |  |  | 0 |  | 1 | CAPACITY
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0 |  |  | -0.00123 |  |  | 0 |  | 1 | NEWENERGY | W1-045
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.5 |  |  | -0.00123 |  |  | 0 |  | 1 | CAPACITY
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.13 | 4.12 |  |  | -0.00123 |  |  | 0 |  | 1 | CAPACITY | W1-045
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00125 |  |  | 0.10478 |  | 1 | CAPACITY
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 498.09 |  |  | -0.00125 |  |  | 0.10478 |  | 1 | CAPACITY
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00125 |  |  | 0.10478 |  | 1 | CAPACITY
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 272 | 218.38 |  |  | -0.00125 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00125 |  |  | 0.04435 |  | 1 | CAPACITY | Y2-050
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00125 |  |  | 0 |  | 1 | CAPACITY | Y2-050
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 11.24 |  |  | -0.00125 |  |  | 0.12623 |  | 1 | CAPACITY
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 41.03 |  |  | -0.00127 |  |  | 0.12623 |  | 1 | CAPACITY
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 39.82 |  |  | -0.00127 |  |  | 0.12623 |  | 1 | CAPACITY
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 62.22 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 60.86 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 60.29 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 898.96 |  |  | -0.00128 |  |  | 0.01494 |  | 1 | CAPACITY
237082 | AA2-121 | 345 | 201 | 58 | 0 | 830 | 666.37 |  |  | -0.00129 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-121
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 503.47 |  |  | -0.0013 |  |  | 0.04435 |  | 1 | CAPACITY | AVON LAKE
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 39.5 | 31.71 |  |  | -0.00129 |  |  | 0.08446 |  | 1 | CAPACITY
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 3.21 |  |  | -0.00129 |  |  | 0 |  | 1 | CAPACITY
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00132 |  |  | 0.10478 |  | 1 | CAPACITY
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00132 |  |  | 0.10478 |  | 1 | CAPACITY
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 455.62 |  |  | -0.00132 |  |  | 0.10478 |  | 1 | CAPACITY
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | AA1-123
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 233.87 |  |  | -0.00132 |  |  | 0.10478 |  | 1 | CAPACITY
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.00133 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-123
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | AA1-123
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 81.57 |  |  | -0.00132 |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND
253970 | 15BI2 | 13.8 | 215 | 58 | 60 | 96.2 | 77.24 |  |  | -0.00132 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | Y3-103
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.7 | 39.1 |  |  | -0.00132 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0 |  |  | -0.00132 |  |  | 0 |  | 1 | NEWENERGY | AC2-168
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 28.1 |  |  | -0.00132 |  |  | 0.10478 |  | 1 | CAPACITY
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00133 |  |  | 0.04435 |  | 1 | CAPACITY | Y3-103
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | Y3-103
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 21 | 16.86 |  |  | -0.00132 |  |  | 0.12623 |  | 1 | CAPACITY
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 14.53 |  |  | -0.00132 |  |  | 0.08446 |  | 1 | CAPACITY
933531 | AC2-168 C | 138 | 215 | 75 | 0 | 7.55 | 6.06 |  |  | -0.00132 |  |  | 0 |  | 1 | CAPACITY | AC2-168
253900 | 15BVRVL1 | 22 | 215 | 44 | 843.9 | 970 | 844.97 |  |  | -0.00133 |  |  | 0.01494 |  | 1 | CAPACITY
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 783.39 |  |  | -0.00133 |  |  | 0.01494 |  | 1 | CAPACITY
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 300.6 | 241.34 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY | Z2-028
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00134 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-028
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY | Z2-028
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | -0.00134 |  |  | 0.10478 |  | 1 | ENERGY
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 24.6 | 19.75 |  |  | -0.00134 |  |  | 0.12623 |  | 1 | CAPACITY
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 329.17 |  |  | -0.00136 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00136 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00136 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-044
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 38.7 | 31.07 |  |  | -0.00136 |  |  | 0.08446 |  | 1 | CAPACITY
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 3.21 |  |  | -0.00136 |  |  | 0 |  | 1 | CAPACITY
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 16.46 |  |  | -0.00138 |  |  | 0.12623 |  | 1 | CAPACITY
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 0 |  |  | -0.00138 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
204555 | 27QUEEN ST | 115 | 227 | 74 | 0 | 5 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 0 |  |  | -0.00138 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
239024 | 02NWCAG5 | 16.5 | 202 | 58 | 23 | 141 | 113.2 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
239023 | 02NWCAG4 | 14.4 | 202 | 58 | 20 | 92 | 73.86 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
204638 | 27CAT TRAC | 13.2 | 227 | 58 | 0 | 32.3 | 25.93 |  |  | -0.00141 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
204706 | 27CAT TRC2 | 13.2 | 227 | 58 | 0 | 13.9 | 11.16 |  |  | -0.00141 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 2.01 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 1.37 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | K20
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 261.73 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | T-174
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | T-174
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00141 |  |  | 0.04435 |  | 1 | CAPACITY | T-174
239022 | 02NWCAG3 | 14.4 | 202 | 58 | 20 | 92.3 | 74.11 |  |  | -0.00142 |  |  | 0.04435 |  | 1 | CAPACITY | NEW CASTLE
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 24.08 |  |  | -0.00146 |  |  | 0.10478 |  | 1 | CAPACITY
920571 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 411.86 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | NEW | AA2-161
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.82 |  |  | -0.00151 |  |  | 0 |  | 1 | CAPACITY
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1086.27 |  |  | -0.00152 |  |  | 0.01494 |  | 1 | CAPACITY
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 3.05 |  |  | -0.00159 |  |  | 0 |  | 1 | CAPACITY
213798 | MERCK 3 | 13.8 | 230 | 2 | 13 | 35 | 28.1 |  |  | -0.0016 |  |  | 0 |  | 1 | CAPACITY
213797 | MERCK 2 | 13.8 | 230 | 2 | 4 | 25 | 20.07 |  |  | -0.0016 |  |  | 0 |  | 1 | CAPACITY
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 3.29 |  |  | -0.0016 |  |  | 0 |  | 1 | CAPACITY
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 353.26 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00162 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-076
913142 | Y1-033 E OP1 | 115 | 226 | 74 | 0 | 34.02 | 0 |  |  | -0.00161 |  |  | 0 |  | 1 | NEWENERGY | Y1-033
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 4.01 |  |  | -0.00161 |  |  | 0 |  | 1 | CAPACITY | Y1-033
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 16.55 |  |  | -0.00169 |  |  | 0.07484 |  | 1 | CAPACITY
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 140 | 182.2 | 146.28 |  |  | -0.0017 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 118.7 | 175.2 | 140.66 |  |  | -0.0017 |  |  | 0.04435 |  | 1 | CAPACITY | AE SPRINGDALE
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 118.7 | 172.2 | 138.25 |  |  | -0.0017 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.0017 |  |  | 0.08446 |  | 1 | CAPACITY
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.0017 |  |  | 0.08446 |  | 1 | CAPACITY
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 5.54 |  |  | -0.0018 |  |  | 0 |  | 1 | CAPACITY
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00184 |  |  | 0 |  | 1 | NEWENERGY | K23
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 0 |  |  | -0.00184 |  |  | 0 |  | 1 | NEWENERGY | L13
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 0 |  |  | -0.00184 |  |  | 0 |  | 1 | NEWENERGY | O48
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | -0.00184 |  |  | 0.05 |  | 1 | MTX
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | -0.00184 |  |  | 0.05 |  | 1 | MTX
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 0 |  |  | -0.00184 |  |  | 0 |  | 1 | NEWENERGY | R40
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 5.06 |  |  | -0.00184 |  |  | 0 |  | 1 | CAPACITY | O48
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 4.74 |  |  | -0.00184 |  |  | 0 |  | 1 | CAPACITY | L13
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 5.1 | 4.09 |  |  | -0.00184 |  |  | 0 |  | 1 | CAPACITY | K23
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 682.91 |  |  | -0.00186 |  |  | 0.10478 |  | 1 | CAPACITY | Cone1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 682.43 |  |  | -0.00186 |  |  | 0.10478 |  | 1 | CAPACITY | Cone2
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 400 | 321.14 |  |  | -0.00188 |  |  | 0.04435 |  | 1 | CAPACITY | AD2-114
235620 | 01SBEND2 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
235622 | 01SBEND4 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
235619 | 01SBEND1 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
235621 | 01SBEND3 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 853.3 | 685.08 |  |  | -0.00189 |  |  | 0.10478 |  | 1 | CAPACITY | Keys1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 853.1 | 684.92 |  |  | -0.00189 |  |  | 0.10478 |  | 1 | CAPACITY | Keys2
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 6.1 |  |  | -0.00191 |  |  | 0 |  | 1 | CAPACITY
219123 | BCRR_COGEN | 13.8 | 231 | 64 | 0 | 6 | 0 |  |  | -0.00192 |  |  | 0.12623 |  | 1 | CAPACITY
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.45 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.72 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | K22
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 5.46 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00209 |  |  | 0.12623 |  | 1 | CAPACITY
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 601.34 |  |  | -0.0021 |  |  | 0.10478 |  | 1 | CAPACITY
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 293.93 |  |  | -0.0021 |  |  | 0.10478 |  | 1 | CAPACITY | Bris2
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 248.4 |  |  | -0.0021 |  |  | 0.10478 |  | 1 | CAPACITY | Bris1
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEWENERGY | P60
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 6.82 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | P60
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 68.24 |  |  | -0.00211 |  |  | 0.10478 |  | 1 | CAPACITY
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 42.95 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 42.95 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.02 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 23.2 | 0 |  |  | -0.00215 |  |  | 0 |  | 1 | NEWENERGY | K13
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 2.57 |  |  | -0.00215 |  |  | 0 |  | 1 | CAPACITY | K13
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 10.44 |  |  | -0.00216 |  |  | 0.12623 |  | 1 | CAPACITY
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 24.24 |  |  | -0.00216 |  |  | 0.07484 |  | 1 | CAPACITY
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00217 |  |  | 0.12623 |  | 1 | CAPACITY
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 422.06 |  |  | -0.00219 |  |  | 0.10478 |  | 1 | CAPACITY
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 60 | 0 |  |  | -0.00222 |  |  | 0 |  | 1 | NEWENERGY | R32
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 52 | 0 |  |  | -0.00222 |  |  | 0 |  | 1 | NEWENERGY | O18
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 10.19 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | R32
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | O18
200805 | 26COLVER13 | 13.2 | 226 | 12 | 77 | 110 | 88.31 |  |  | -0.00223 |  |  | 0.10478 |  | 1 | CAPACITY
903644 | W3-099 E OP1 | 230 | 226 | 74 | 0 | 87 | 0 |  |  | -0.00224 |  |  | 0 |  | 1 | NEWENERGY | W3-099
201144 | W3-099 C OP1 | 230 | 226 | 74 | 0 | 13 | 0 |  |  | -0.00224 |  |  | 0 |  | 1 | NEW | W3-099
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 497.77 |  |  | -0.00226 |  |  | 0.10478 |  | 1 | CAPACITY
200809 | 26SITHE | 138 | 226 | 15 | 0 | 36 | 28.9 |  |  | -0.00226 |  |  | 0.10478 |  | 1 | CAPACITY
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 900.89 |  |  | -0.00229 |  |  | 0.01494 |  | 1 | CAPACITY
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 0 |  |  | -0.0023 |  |  | 0 |  | 1 | NEWENERGY | V3-030
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 4.25 |  |  | -0.0023 |  |  | 0 |  | 1 | CAPACITY | V3-030
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 48 | 0 |  |  | -0.00235 |  |  | 0 |  | 1 | NEWENERGY | Q53
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 5.14 |  |  | -0.00235 |  |  | 0 |  | 1 | CAPACITY | Q53
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 0 |  |  | -0.00238 |  |  | 0 |  | 1 | NEWENERGY | N39
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00238 |  |  | 0 |  | 1 | NEWENERGY | O38
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00238 |  |  | 0 |  | 1 | CAPACITY | N39
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.4 | 7.55 |  |  | -0.00238 |  |  | 0 |  | 1 | CAPACITY | O38
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 521.86 |  |  | -0.00241 |  |  | 0.10478 |  | 1 | CAPACITY
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 492.95 |  |  | -0.00241 |  |  | 0.10478 |  | 1 | CAPACITY
208947 | WSHO CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00242 |  |  | 0.08446 |  | 1 | CAPACITY
208348 | EELI | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00255 |  |  | 0 |  | 1 | CAPACITY
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 57 | 45.76 |  |  | -0.00257 |  |  | 0.08446 |  | 1 | CAPACITY
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | -0.00259 |  |  | 0 |  | 1 | ENERGY
208942 | HARR CT | 12.5 | 229 | 55 | 0 | 42 | 33.72 |  |  | -0.0026 |  |  | 0.08446 |  | 1 | CAPACITY
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 9.64 |  |  | -0.0026 |  |  | 0.12623 |  | 1 | CAPACITY
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 8.19 |  |  | -0.0026 |  |  | 0.10478 |  | 1 | CAPACITY
210022 | LING 2 | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00259 |  |  | 0 |  | 1 | CAPACITY
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 40 | 0 |  |  | -0.00262 |  |  | 0 |  | 1 | NEWENERGY | Q36
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 24.08 |  |  | -0.00261 |  |  | 0.10478 |  | 1 | CAPACITY
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 6.66 |  |  | -0.00262 |  |  | 0 |  | 1 | CAPACITY | Q36
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 16.86 |  |  | -0.00263 |  |  | 0.07484 |  | 1 | CAPACITY
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 187.87 |  |  | -0.00272 |  |  | 0.0316 |  | 1 | CAPACITY
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 177.43 |  |  | -0.00272 |  |  | 0.0316 |  | 1 | CAPACITY
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 26.13 |  |  | -0.00272 |  |  | 0.07484 |  | 1 | CAPACITY
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | -0.00275 |  |  | 0.12623 |  | 1 | ENERGY
208697 | PRIN B34 | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00275 |  |  | 0 |  | 1 | CAPACITY
208885 | WNHO | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00275 |  |  | 0 |  | 1 | CAPACITY
210319 | WCAR 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00277 |  |  | 0 |  | 1 | CAPACITY
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4.82 |  |  | -0.00288 |  |  | 0 |  | 1 | CAPACITY
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 33.96 |  |  | -0.00292 |  |  | 0.10478 |  | 1 | CAPACITY
200722 | 26SHAWVL 2 | 18 | 226 | 12 | 62 | 124.7 | 100.12 |  |  | -0.00297 |  |  | 0.10478 |  | 1 | CAPACITY
200715 | 26SHAWVL 1 | 18 | 226 | 12 | 62 | 122 | 97.95 |  |  | -0.00297 |  |  | 0.10478 |  | 1 | CAPACITY
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | -0.00303 |  |  | 0 |  | 1 | MTX | AC1-025
200666 | 26SHAWVL 4 | 22 | 226 | 12 | 120 | 171 | 137.29 |  |  | -0.00305 |  |  | 0.10478 |  | 1 | CAPACITY
236828 | 01GRAYMONT | 46 | 201 | 2 | 0 | 4 | 0 |  |  | -0.00304 |  |  | 0 |  | 1 | ENERGY
200665 | 26SHAWVL 3 | 22 | 226 | 12 | 120 | 174.2 | 139.86 |  |  | -0.00305 |  |  | 0.10478 |  | 1 | CAPACITY
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | -0.00311 |  |  | 0 |  | 1 | ENERGY
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.61 |  |  | -0.00311 |  |  | 0 |  | 1 | CAPACITY
204664 | 27AES GEN3 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00316 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204662 | 27AES GEN1 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00316 |  |  | 0.04435 |  | 1 | CAPACITY | IRONWOOD
204663 | 27AES GEN2 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00316 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | ENERGY
208580 | MGTN 2 | 12.5 | 229 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY
922932 | AB1-082 OP | 46 | 201 | 55 | 0 | 19.9 | 0 |  |  | -0.00344 |  |  | 0.08446 |  | 1 | NEW
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY | Z1-069
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY | Z1-069
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 389.39 |  |  | -0.00434 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-115
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 30.1 | 24.17 |  |  | -0.00439 |  |  | 0.08446 |  | 1 | CAPACITY
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 4.82 |  |  | -0.00444 |  |  | 0 |  | 1 | CAPACITY
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 6 | 4.82 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 19 | 15.25 |  |  | -0.00465 |  |  | 0.08446 |  | 1 | CAPACITY
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 0 |  |  | -0.00481 |  |  | 0 |  | 1 | NEWENERGY | P47
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.8 | 12.69 |  |  | -0.00481 |  |  | 0 |  | 1 | CAPACITY | P47
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00481 |  |  | 0 |  | 1 | NEWENERGY | K02
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 64.23 |  |  | -0.00483 |  |  | 0.10478 |  | 1 | CAPACITY
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 152.86 |  |  | -0.00491 |  |  | 0.04435 |  | 1 | CAPACITY | ONTELAUNEE
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 152.86 |  |  | -0.00491 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 139.94 |  |  | -0.00491 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 17.18 |  |  | -0.00502 |  |  | 0.12623 |  | 1 | CAPACITY
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 16.86 |  |  | -0.00502 |  |  | 0.12623 |  | 1 | CAPACITY
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 16.86 |  |  | -0.00505 |  |  | 0.12623 |  | 1 | CAPACITY
920341 | AA2-132 | 34.5 | 226 | 55 | 0 | 19.9 | 0 |  |  | -0.00545 |  |  | 0.08446 |  | 1 | NEW
919201 | AA1-144 OP | 230 | 226 | 58 | 0 | 163 | 130.87 |  |  | -0.00567 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-144
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00573 |  |  | 0.04435 |  | 1 | CAPACITY | X1-109
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00573 |  |  | 0 |  | 1 | CAPACITY | X1-109
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.04 |  |  | -0.00576 |  |  | 0 |  | 1 | CAPACITY
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 317.93 |  |  | -0.00619 |  |  | 0 |  | 1 | CAPACITY | Hummel
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 194.29 |  |  | -0.00619 |  |  | 0 |  | 1 | CAPACITY | Hummel
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.00619 |  |  | 0.04435 |  | 1 | CAPACITY | Hummel
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.00619 |  |  | 0 |  | 1 | CAPACITY | Hummel
203932 | AA2-133 GEN | 13.8 | 226 | 55 | 0 | 19.89 | 0 |  |  | -0.00618 |  |  | 0.08446 |  | 1 | NEW
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 0 |  |  | -0.00669 |  |  | 0 |  | 1 | NEWENERGY | P28
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | -0.00669 |  |  | 0.10478 |  | 1 | NEW
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 47.37 |  |  | -0.00669 |  |  | 0.10478 |  | 1 | CAPACITY
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00669 |  |  | 0 |  | 1 | CAPACITY | P28
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 17.18 |  |  | -0.00669 |  |  | 0.12623 |  | 1 | CAPACITY
209018 | SUNBIPCT | 12.5 | 229 | 55 | 0 | 36 | 28.9 |  |  | -0.00697 |  |  | 0.08446 |  | 1 | CAPACITY
212345 | PENS | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00697 |  |  | 0 |  | 1 | CAPACITY
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0 |  |  | -0.00701 |  |  | 0 |  | 1 | NEWENERGY | W1-121 Z
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00701 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00701 |  |  | 0 |  | 1 | CAPACITY | W1-121 Z
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.46 |  |  | -0.00701 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00713 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00713 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00713 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00713 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00713 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200044 | BETH CT1 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00713 |  |  | 0.04435 |  | 1 | CAPACITY | BETH1234
200048 | BETH CT5 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00713 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
212435 | SMIL | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00723 |  |  | 0 |  | 1 | CAPACITY
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 11.24 |  |  | -0.00729 |  |  | 0.08446 |  | 1 | CAPACITY
208948 | WILL CT | 12.5 | 229 | 55 | 0 | 27.4 | 22 |  |  | -0.00734 |  |  | 0.08446 |  | 1 | CAPACITY
212005 | ALWD | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00734 |  |  | 0 |  | 1 | CAPACITY
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00743 |  |  | 0.04435 |  | 1 | CAPACITY | MOXIE PATRIOT
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00743 |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 18.3 | 14.69 |  |  | -0.00751 |  |  | 0.12623 |  | 1 | CAPACITY
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 608.97 |  |  | -0.00753 |  |  | 0.10478 |  | 1 | CAPACITY
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 608.49 |  |  | -0.00753 |  |  | 0.10478 |  | 1 | CAPACITY
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 34.28 |  |  | -0.00759 |  |  | 0.10478 |  | 1 | CAPACITY
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 26.09 |  |  | -0.00759 |  |  | 0.10478 |  | 1 | CAPACITY
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 6.42 |  |  | -0.00759 |  |  | 0 |  | 1 | CAPACITY
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 4.9 |  |  | -0.00759 |  |  | 0 |  | 1 | CAPACITY
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1090.36 |  |  | -0.0079 |  |  | 0.01494 |  | 1 | CAPACITY
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 69.05 |  |  | -0.0079 |  |  | 0.10478 |  | 1 | CAPACITY
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 65.83 |  |  | -0.0079 |  |  | 0.10478 |  | 1 | CAPACITY
208941 | FISH CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.0079 |  |  | 0.08446 |  | 1 | CAPACITY
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.4 | 9.15 |  |  | -0.0079 |  |  | 0 |  | 1 | CAPACITY | Q27
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.81 |  |  | -0.0079 |  |  | 0 |  | 1 | CAPACITY | N14
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00799 |  |  | 0 |  | 1 | CAPACITY | Z2-046
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00799 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-046
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1091.76 |  |  | -0.00829 |  |  | 0.01494 |  | 1 | CAPACITY
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 35.57 |  |  | -0.00855 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 23.44 |  |  | -0.00855 |  |  | 0.04435 |  | 1 | CAPACITY | HUNLOCK
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 39.1 |  |  | -0.00856 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 38.86 |  |  | -0.00856 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
211375 | BEAC | 69 | 229 | 2 | 0 | 20 | 0 |  |  | -0.00859 |  |  | 0.10478 |  | 1 | ENERGY
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 47.77 |  |  | -0.00859 |  |  | 0.08446 |  | 1 | CAPACITY
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 47.21 |  |  | -0.00859 |  |  | 0.08446 |  | 1 | CAPACITY
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 23.76 |  |  | -0.00859 |  |  | 0.08446 |  | 1 | CAPACITY
208943 | HARW CT | 12.5 | 229 | 55 | 0 | 27.2 | 21.84 |  |  | -0.00859 |  |  | 0.08446 |  | 1 | CAPACITY
211591 | HARW | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00859 |  |  | 0 |  | 1 | CAPACITY
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.00865 |  |  | 0.05 |  | 1 | MTX | AB1-182
208944 | JENK CT | 12.5 | 229 | 55 | 0 | 28 | 22.48 |  |  | -0.00865 |  |  | 0.08446 |  | 1 | CAPACITY
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.65 |  |  | -0.00865 |  |  | 0 |  | 1 | CAPACITY | L18
211374 | AVOC | 12.5 | 229 | 2 | 0 | 17.4 | 13.97 |  |  | -0.00884 |  |  | 0 |  | 1 | CAPACITY
208940 | ALLE CT | 12.5 | 229 | 55 | 0 | 56 | 44.96 |  |  | -0.00904 |  |  | 0.08446 |  | 1 | CAPACITY
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00905 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00914 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G2
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00914 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G1
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00914 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G3
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | -0.00914 |  |  | 0.05 |  | 1 | MTX | Z2-107
209009 | PEIP 2 | 13.8 | 229 | 56 | 0 | 43.7 | 35.08 |  |  | -0.00914 |  |  | 0.08446 |  | 1 | CAPACITY
209010 | PEIP 1 | 13.8 | 229 | 29 | 0 | 26.7 | 21.43 |  |  | -0.00914 |  |  | 0.10478 |  | 1 | CAPACITY
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 7.23 |  |  | -0.00914 |  |  | 0 |  | 1 | CAPACITY | K21
209003 | KSTN IPP | 13.8 | 229 | 65 | 0 | 4.9 | 3.93 |  |  | -0.00914 |  |  | 0 |  | 1 | CAPACITY
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 0 |  |  | -0.00916 |  |  | 0 |  | 1 | NEWENERGY | AC1-071
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 7.02 |  |  | -0.00916 |  |  | 0 |  | 1 | NEW | AC1-071
209007 | NOEN IPP | 13.8 | 229 | 12 | 80 | 111.4 | 89.44 |  |  | -0.00919 |  |  | 0.10478 |  | 1 | CAPACITY
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 0 |  |  | -0.00929 |  |  | 0 |  | 1 | NEWENERGY | AA2-017
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 0 |  |  | -0.00929 |  |  | 0 |  | 1 | NEW | AA2-017
211065 | PSPA IPP | 13.8 | 229 | 75 | 0 | 18.4 | 6.74 |  |  | -0.00952 |  |  | 0 |  | 1 | NEWENERGY | U4-014
208946 | MACR CT | 12.5 | 229 | 55 | 0 | 72 | 57.81 |  |  | -0.01014 |  |  | 0.08446 |  | 1 | CAPACITY
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.33 |  |  | -0.01026 |  |  | 0 |  | 1 | CAPACITY
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 152 | 122.03 |  |  | -0.01041 |  |  | 0.08446 |  | 1 | CAPACITY
206341 | 28GIL 8 | 13.8 | 228 | 58 | 69.9 | 90 | 72.26 |  |  | -0.01041 |  |  | 0.04435 |  | 1 | CAPACITY | GILBERT
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 87 | 100 | 87.11 |  |  | -0.01041 |  |  | 0 |  | 1 | CAPACITY | GILBERT
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 85.3 | 98 | 85.37 |  |  | -0.01041 |  |  | 0 |  | 1 | CAPACITY | GILBERT
208920 | WLPK | 12.5 | 229 | 60 | 0 | 40.9 | 32.84 |  |  | -0.01055 |  |  | 0.07484 |  | 1 | CAPACITY
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.01062 |  |  | 0.10478 |  | 1 | CAPACITY
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.01062 |  |  | 0.10478 |  | 1 | CAPACITY
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 192.53 |  |  | -0.01062 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 160.57 |  |  | -0.01062 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 160.57 |  |  | -0.01062 |  |  | 0.04435 |  | 1 | CAPACITY | LOWER MT BETHEL
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01092 |  |  | 0 |  | 1 | NEWENERGY | W4-097
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.01092 |  |  | 0 |  | 1 | CAPACITY | W4-097
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0 |  |  | -0.01097 |  |  | 0 |  | 1 | NEWENERGY | AD2-070
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 2.81 |  |  | -0.01097 |  |  | 0 |  | 1 | CAPACITY | AD2-070
207402 | 28AA2-082 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.01101 |  |  | 0.05 |  | 1 | MTX | AA2-082
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.01107 |  |  | 0 |  | 1 | NEWENERGY | W4-073
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.01107 |  |  | 0 |  | 1 | CAPACITY
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01109 |  |  | 0 |  | 1 | NEWENERGY | W1-127
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0 |  |  | -0.01109 |  |  | 0 |  | 1 | NEWENERGY | U2-059
925462 | AC1-018 E | 34.5 | 228 | 75 | 0 | 0.9 | 0 |  |  | -0.01109 |  |  | 0 |  | 1 | NEWENERGY | AC1-018
925461 | AC1-018 C | 34.5 | 228 | 75 | 0 | 0.5 | 0 |  |  | -0.01109 |  |  | 0 |  | 1 | NEW | AC1-018
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01109 |  |  | 0 |  | 1 | CAPACITY | W1-127
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.01109 |  |  | 0 |  | 1 | CAPACITY | U2-059
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 4 | 3.21 |  |  | -0.01136 |  |  | 0 |  | 1 | CAPACITY
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 120 |  |  |  | -0.0116
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 20 | 16.06 |  |  | -0.01162 |  |  | 0.08446 |  | 1 | CAPACITY
218780 | PRINCENTON_U | 26 | 231 | 2 | 0 | 31.56 | 25.34 |  |  | -0.01179 |  |  | 0 |  | 1 | CAPACITY
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0 |  |  | -0.01179 |  |  | 0 |  | 1 | NEWENERGY | Z1-096
219622 | TRENT_BIOGAS | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.01179 |  |  | 0 |  | 1 | CAPACITY
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 2.39 |  |  | -0.01179 |  |  | 0 |  | 1 | CAPACITY | Z1-096
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.01181 |  |  | 0 |  | 1 | NEWENERGY | W3-077
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 5.7 | 4.58 |  |  | -0.01181 |  |  | 0 |  | 1 | CAPACITY | W3-077
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.01181 |  |  | 0 |  | 1 | CAPACITY | W2-091
204651 | 27PORT CT | 13.8 | 227 | 56 | 4 | 35 | 28.1 |  |  | -0.01185 |  |  | 0.08446 |  | 1 | CAPACITY
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.01205 |  |  | 0 |  | 1 | NEWENERGY | W2-016
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.01205 |  |  | 0 |  | 1 | CAPACITY | W2-016
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 134 | 107.58 |  |  | -0.01215 |  |  | 0.08446 |  | 1 | CAPACITY
206747 | 28DSM_X3-029 | 34.5 | 228 | 29 | 0 | 11.15 | 0 |  |  | -0.0126 |  |  | 0.10478 |  | 1 | ENERGY
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | -0.0126 |  |  | 0.08446 |  | 1 | ENERGY
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01265 |  |  | 0 |  | 1 | NEWENERGY | Y2-018
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.01279 |  |  | 0.0316 |  | 1 | CAPACITY
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.01279 |  |  | 0.0316 |  | 1 | CAPACITY
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.01279 |  |  | 0.0316 |  | 1 | CAPACITY
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 0 |  |  | -0.0129 |  |  | 0 |  | 1 | NEWENERGY | W3-044
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 6.1 |  |  | -0.0129 |  |  | 0 |  | 1 | CAPACITY | W3-044
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.01316 |  |  | 0 |  | 1 | NEWENERGY | W4-046
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 1.93 |  |  | -0.01316 |  |  | 0 |  | 1 | CAPACITY | W4-046
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.01348 |  |  | 0 |  | 1 | NEWENERGY | V4-001
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.61 |  |  | -0.01348 |  |  | 0 |  | 1 | CAPACITY | V4-001
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 35.24 |  |  | -0.01371 |  |  | 0.10478 |  | 1 | CAPACITY
933322 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | -0.01386 |  |  | 0 |  | 1 | MTX | AC2-144
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0 |  |  | -0.01438 |  |  | 0 |  | 1 | NEWENERGY | V2-009 3
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0 |  |  | -0.01438 |  |  | 0 |  | 1 | NEWENERGY | V2-009 4
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 1.92 |  |  | -0.01438 |  |  | 0 |  | 1 | CAPACITY | V2-009 3
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 1.15 |  |  | -0.01438 |  |  | 0 |  | 1 | CAPACITY | V2-009 4
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0 |  |  | -0.01483 |  |  | 0 |  | 1 | NEWENERGY | W3-124
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0 |  |  | -0.01483 |  |  | 0 |  | 1 | NEWENERGY | V2-009 1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.87 |  |  | -0.01483 |  |  | 0 |  | 1 | CAPACITY | W3-124
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.01483 |  |  | 0 |  | 1 | CAPACITY | V2-009 1
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.01485 |  |  | 0 |  | 1 | NEWENERGY | V3-024
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0 |  |  | -0.01485 |  |  | 0 |  | 1 | NEWENERGY | V2-009 2
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0 |  |  | -0.01485 |  |  | 0 |  | 1 | NEWENERGY | X2-088
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.01485 |  |  | 0 |  | 1 | CAPACITY | V3-024
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 1.52 |  |  | -0.01485 |  |  | 0 |  | 1 | CAPACITY | V2-009 2
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.72 |  |  | -0.01485 |  |  | 0 |  | 1 | CAPACITY | X2-088
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0 |  |  | -0.01491 |  |  | 0 |  | 1 | NEWENERGY | W2-050
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01492 |  |  | 0 |  | 1 | NEWENERGY | W4-064
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.01492 |  |  | 0 |  | 1 | CAPACITY | W4-064
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.01512 |  |  | 0 |  | 1 | NEWENERGY | X1-012
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 2.97 |  |  | -0.01512 |  |  | 0 |  | 1 | CAPACITY | X1-012
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | -0.01516 |  |  | 0.05 |  | 1 | MTX | AA2-061
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | -0.01516 |  |  | 0.05 |  | 1 | MTX | AA2-060
206742 | 28SUX_V3-011 | 34.5 | 228 | 64 | 0 | 2 | 0 |  |  | -0.01518 |  |  | 0 |  | 1 | CAPACITY
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0 |  |  | -0.01522 |  |  | 0 |  | 1 | NEWENERGY | W3-106
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0 |  |  | -0.01526 |  |  | 0 |  | 1 | NEWENERGY | V3-070
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0 |  |  | -0.01526 |  |  | 0 |  | 1 | NEWENERGY | W3-110
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.01526 |  |  | 0 |  | 1 | CAPACITY | V3-070
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 2.29 |  |  | -0.01526 |  |  | 0 |  | 1 | CAPACITY | W3-110
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 2.99 |  |  | -0.01539 |  |  | 0 |  | 1 | CAPACITY | Y1-020
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0 |  |  | -0.01544 |  |  | 0 |  | 1 | NEWENERGY | W2-080
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.01544 |  |  | 0 |  | 1 | CAPACITY | W2-080
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0 |  |  | -0.01548 |  |  | 0 |  | 1 | NEWENERGY | AC2-175
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0 |  |  | -0.01548 |  |  | 0 |  | 1 | NEWENERGY | AE1-081
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.77 |  |  | -0.01548 |  |  | 0 |  | 1 | CAPACITY | AE1-081
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0 |  |  | -0.01559 |  |  | 0 |  | 1 | NEWENERGY | X2-075
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 1.83 |  |  | -0.01559 |  |  | 0 |  | 1 | CAPACITY | X2-075
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | W3-029
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | W3-003
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEW | AE1-156
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | AE1-156
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | W1-132
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | W2-061
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | V4-070
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | V4-069
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.01562 |  |  | 0 |  | 1 | CAPACITY | W3-029
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01562 |  |  | 0 |  | 1 | CAPACITY | V4-069
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01562 |  |  | 0 |  | 1 | CAPACITY | V4-070
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.01562 |  |  | 0 |  | 1 | CAPACITY | W2-061
218455 | CINNBAY_CGEN | 26.4 | 231 | 75 | 0 | 9 | 0 |  |  | -0.01636 |  |  | 0 |  | 1 | NEWENERGY
924132 | NEWROADSO E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.01636 |  |  | 0 |  | 1 | NEWENERGY | AB2-057
217198 | EDGEBORO_1E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.01636 |  |  | 0 |  | 1 | NEWENERGY | V3-058
217199 | EDGEBORO_2E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.01636 |  |  | 0 |  | 1 | NEWENERGY | V3-059
924131 | NEWROADSO C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.01636 |  |  | 0 |  | 1 | CAPACITY | AB2-057
218781 | BRIS_MYERS | 26 | 231 | 2 | 0 | 3 | 2.41 |  |  | -0.01636 |  |  | 0 |  | 1 | CAPACITY
933332 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | -0.01694 |  |  | 0 |  | 1 | MTX | AC2-145
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0 |  |  | -0.01703 |  |  | 0 |  | 1 | NEWENERGY | X2-089
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.61 |  |  | -0.01703 |  |  | 0 |  | 1 | CAPACITY | X2-089
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 538.72 |  |  | -0.01704 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-116
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0 |  |  | -0.01704 |  |  | 0 |  | 1 | NEWENERGY | AB1-139
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0 |  |  | -0.01704 |  |  | 0 |  | 1 | NEWENERGY | AE1-041
930901 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 2.01 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY | AB1-139
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0 |  |  | -0.01704 |  |  | 0 |  | 1 | NEWENERGY | W2-052
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY | W2-052
938281 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY | AE1-041
219001 | SEWAREN7GT | 25 | 231 | 58 | 101.5 | 324.6 | 260.61 |  |  | -0.01712 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-089
219002 | SEWAREN7ST | 18 | 231 | 58 | 96.3 | 216.4 | 173.74 |  |  | -0.01712 |  |  | 0 |  | 1 | CAPACITY | Z2-089
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | -0.01712 |  |  | 0 |  | 1 | ENERGY | Z2-089
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | -0.01712 |  |  | 0.04435 |  | 1 | ENERGY | Z2-089
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 309 | 248.08 |  |  | -0.01742 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.01742 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.01742 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.01742 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC2
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | -0.01742 |  |  | 0.08446 |  | 1 | CAPACITY
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | -0.01742 |  |  | 0.08446 |  | 1 | CAPACITY
218344 | TOSCO_G6 | 18 | 231 | 2 | 90 | 180 | 144.51 |  |  | -0.01746 |  |  | 0.04435 |  | 1 | CAPACITY | TOSCO
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  |  |  | -0.0175
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 309 | 248.08 |  |  | -0.01754 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 180 | 144.51 |  |  | -0.01754 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -0.01754 |  |  | 0.08446 |  | 1 | CAPACITY
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -0.01754 |  |  | 0.08446 |  | 1 | CAPACITY
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 30.03 |  |  | -0.01754 |  |  | 0.10478 |  | 1 | CAPACITY
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0 |  |  | -0.01763 |  |  | 0 |  | 1 | NEWENERGY | W1-101
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.43 |  |  | -0.01763 |  |  | 0 |  | 1 | CAPACITY | W1-101
900003 | DEANS E | 500 | 231 | 74 | 0 | 1779.4 | 0 |  |  | -0.01763 |  |  | 0 |  | 1 | NEWENERGY | OSW_DEANS
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 5.3 |  |  | -0.01764 |  |  | 0 |  | 1 | CAPACITY
200006 | DEANS C | 500 | 231 | 74 | 0 | 762.6 | 762.6 |  |  | -0.01763 |  |  | 0 |  | 1 | CAPACITY | OSW_DEANS
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0 |  |  | -0.01771 |  |  | 0 |  | 1 | NEWENERGY | V3-067
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0 |  |  | -0.01771 |  |  | 0 |  | 1 | NEWENERGY | V3-068
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.23 |  |  | -0.01771 |  |  | 0 |  | 1 | CAPACITY | V3-067
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.01771 |  |  | 0 |  | 1 | CAPACITY | V3-068
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 169.24 |  |  | -0.01773 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.01773 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.01773 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.01773 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.01773 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.01772 |  |  | 0.10478 |  | 1 | CAPACITY
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.01772 |  |  | 0.10478 |  | 1 | CAPACITY
217825 | UMD_NJ | 26 | 231 | 2 | 0 | 10.5 | 8.43 |  |  | -0.01773 |  |  | 0 |  | 1 | CAPACITY
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 202.48 |  |  | -0.01776 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 143.63 |  |  | -0.01776 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN2
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 143.63 |  |  | -0.01776 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
218092 | PRIMEENG_G | 26.4 | 231 | 29 | 10 | 70.3 | 56.44 |  |  | -0.01776 |  |  | 0.10478 |  | 1 | CAPACITY
217850 | MONTCLAIR_U | 26 | 231 | 2 | 0 | 10.6 | 8.51 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY
934302 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.01776 |  |  | 0 |  | 1 | NEWENERGY | AD1-054
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.74 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0 |  |  | -0.01776 |  |  | 0 |  | 1 | NEWENERGY | X1-072
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.01776 |  |  | 0 |  | 1 | CAPACITY | X1-072
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 207.94 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.01777 |  |  | 0.04435 |  | 1 | CAPACITY | DELANCY STREET
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 76.11 |  |  | -0.01777 |  |  | 0.08446 |  | 1 | CAPACITY
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.01777 |  |  | 0.08446 |  | 1 | CAPACITY
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.01777 |  |  | 0.08446 |  | 1 | CAPACITY
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.01777 |  |  | 0.08446 |  | 1 | CAPACITY
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.01777 |  |  | 0.08446 |  | 1 | CAPACITY
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 70.56 |  |  | -0.01777 |  |  | 0.08446 |  | 1 | CAPACITY
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.01777 |  |  | 0.04435 |  | 1 | CAPACITY | NEWARK BAY
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 27.46 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.01778 |  |  | 0 |  | 1 | NEWENERGY | V2-025
217831 | PB_NUTCLIF | 26 | 231 | 2 | 0 | 10.7 | 8.59 |  |  | -0.01778 |  |  | 0 |  | 1 | CAPACITY
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.85 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0 |  |  | -0.01777 |  |  | 0 |  | 1 | NEWENERGY | V3-065
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0 |  |  | -0.01777 |  |  | 0 |  | 1 | NEWENERGY | V3-066
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.17 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY | V3-065
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY | V3-066
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0 |  |  | -0.01779 |  |  | 0 |  | 1 | NEWENERGY | W4-059
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.18 |  |  | -0.01779 |  |  | 0 |  | 1 | CAPACITY | W4-059
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0 |  |  | -0.0178 |  |  | 0 |  | 1 | NEWENERGY | AB1-021
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.0178 |  |  | 0 |  | 1 | CAPACITY | AB1-021
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0 |  |  | -0.01802 |  |  | 0 |  | 1 | NEWENERGY | X2-087
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.01802 |  |  | 0 |  | 1 | CAPACITY | X2-087
937512 | AD2-210 E | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | -0.01819 |  |  | 0 |  | 1 | MTX | AD2-210
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.01834 |  |  | 0 |  | 1 | NEWENERGY | X1-095
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01834 |  |  | 0 |  | 1 | CAPACITY | X1-095
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0 |  |  | -0.02089 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0 |  |  | -0.02089 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
932032 | AC2-009 E | 13.2 | 231 | 75 | -0.5 | 0.49 | 0 |  |  | -0.02089 |  |  | 0 |  | 1 | NEWENERGY | AC2-009
932031 | AC2-009 C | 13.2 | 231 | 75 | -0.1 | 0.1 | 0 |  |  | -0.02089 |  |  | 0 |  | 1 | NEW | AC2-009
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.02089 |  |  | 0 |  | 1 | CAPACITY | AA2-058
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0 |  |  | -0.0223 |  |  | 0 |  | 1 | NEWENERGY | W2-036
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.0223 |  |  | 0 |  | 1 | CAPACITY | W2-036
219650 | TRENT_COLLEG | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.02321 |  |  | 0 |  | 1 | CAPACITY
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0 |  |  | -0.02321 |  |  | 0 |  | 1 | NEWENERGY | W4-058
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.22 |  |  | -0.02321 |  |  | 0 |  | 1 | CAPACITY | W4-058
900004 | SMITHBRG E | 500 | 228 | 74 | 0 | 820.4 | 0 |  |  | -0.02479 |  |  | 0 |  | 1 | NEWENERGY | OSW_SMITHB
200017 | SMITHBRG C | 500 | 228 | 74 | 0 | 327.6 | 327.6 |  |  | -0.02479 |  |  | 0 |  | 1 | CAPACITY | OSW_SMITHB
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  |  |  | -0.0427
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 245.67 |  |  | -0.04268 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.04268 |  |  | 0.04435 |  | 1 | CAPACITY | RARITAN RIVER
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.04268 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
207435 | AD1-113 CT2 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.04268 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207441 | AD1-113 ST | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.04268 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207434 | AD1-113 CT1 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.04268 |  |  | 0.04435 |  | 1 | NEW | RARITAN RIVER
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 97.1 | 111.6 | 97.21 |  |  | -0.04268 |  |  | 0.08446 |  | 1 | CAPACITY
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 90.9 | 104.5 | 91.03 |  |  | -0.04268 |  |  | 0.08446 |  | 1 | CAPACITY
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 199.11 |  |  | -0.04516 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.04516 |  |  | 0.04435 |  | 1 | CAPACITY | RED OAK
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.04582 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 141.3 |  |  | -0.04582 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 43.63 |  |  | -0.047 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 46.17 |  |  | -0.047 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0 |  |  | -0.04713 |  |  | 0 |  | 1 | NEWENERGY | W2-078
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.04713 |  |  | 0 |  | 1 | NEWENERGY | W1-113
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.04713 |  |  | 0 |  | 1 | CAPACITY | W2-078
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 2.25 |  |  | -0.04713 |  |  | 0 |  | 1 | CAPACITY | W1-113
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 66.1 | 98 | 78.68 |  |  | -0.04728 |  |  | 0.08446 |  | 1 | CAPACITY
206327 | 28S RIV G1 | 13.8 | 228 | 57 | 86.9 | 99.9 | 87.02 |  |  | -0.04728 |  |  | 0.08446 |  | 1 | CAPACITY
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 87.02 |  |  | -0.04728 |  |  | 0.08446 |  | 1 | CAPACITY
207419 | AB2-139 E | 34.5 | 228 | 76 | 0 | 0.21 | 0 |  |  | -0.04971 |  |  | 0 |  | 1 | ENERGY | AB2-139
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | AC1-207
207420 | AC1-207 C | 34.5 | 228 | 75 | 0 | 4.9 | 3.93 |  |  | -0.05064 |  |  | 0 |  | 1 | CAPACITY | AC1-207
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.05088 |  |  | 0 |  | 1 | NEWENERGY | X1-085
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.05088 |  |  | 0 |  | 1 | CAPACITY | X1-085
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.05336 |  |  | 0.05 |  | 1 | MTX
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.05339 |  |  | 0 |  | 1 | NEWENERGY | W4-060
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.05339 |  |  | 0 |  | 1 | CAPACITY | W4-060
901032 | W1-024E OP1 | 34.5 | 228 | 0 | 0 | 0 | 0 |  |  | -0.05448 |  |  | 0 |  | 1 | NEW
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.05448 |  |  | 0 |  | 1 | CAPACITY | W1-024
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.05479 |  |  | 0 |  | 1 | NEWENERGY | W1-032
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.05479 |  |  | 0 |  | 1 | CAPACITY | W1-032
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0 |  |  | -0.057 |  |  | 0 |  | 1 | NEWENERGY | W2-019
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 1.85 |  |  | -0.057 |  |  | 0 |  | 1 | CAPACITY | W2-019
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.05755 |  |  | 0 |  | 1 | NEWENERGY | W4-025
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.05755 |  |  | 0 |  | 1 | NEWENERGY | W1-129
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.05755 |  |  | 0 |  | 1 | CAPACITY | W4-025
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.05755 |  |  | 0 |  | 1 | CAPACITY | W1-129
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.05782 |  |  | 0 |  | 1 | NEWENERGY | X4-015
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.05782 |  |  | 0 |  | 1 | CAPACITY | X4-015
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.0582 |  |  | 0 |  | 1 | NEWENERGY | W2-082
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.0582 |  |  | 0 |  | 1 | CAPACITY | W2-082
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0 |  |  | -0.06123 |  |  | 0 |  | 1 | NEWENERGY | Z2-102
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 3.97 |  |  | -0.06123 |  |  | 0 |  | 1 | CAPACITY | Z2-102
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.06132 |  |  | 0 |  | 1 | NEWENERGY | W1-120
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.06132 |  |  | 0 |  | 1 | NEWENERGY | W1-119
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.06132 |  |  | 0 |  | 1 | CAPACITY | W1-120
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.06132 |  |  | 0 |  | 1 | CAPACITY | W1-119
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0 |  |  | -0.06231 |  |  | 0 |  | 1 | NEWENERGY | W1-112
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.06231 |  |  | 0 |  | 1 | CAPACITY | W1-112
206201 | 28JERSVGEN | 34.5 | 228 | 2 | 0 | 2 | 1.61 |  |  | -0.06558 |  |  | 0 |  | 1 | CAPACITY
920732 | AA2-184 E | 34.5 | 228 | 75 | 0 | 20 | 0 |  |  | -0.06967 |  |  | 0 |  | 1 | NEWENERGY | AA2-184
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.07042 |  |  | 0 |  | 1 | NEWENERGY | W1-124
921743 | AA2-049 E | 34.5 | 228 | 76 | -3 | 3 | 0 |  |  | -0.07042 |  |  | 0 |  | 1 | MTX | AA2-049
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.07042 |  |  | 0 |  | 1 | CAPACITY | W1-124
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0 |  |  | -0.07062 |  |  | 0 |  | 1 | NEWENERGY | X1-037
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 3.37 |  |  | -0.07062 |  |  | 0 |  | 1 | CAPACITY | X1-037
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.07375 |  |  | 0 |  | 1 | NEWENERGY | X4-031
923463 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.08533 |  |  | 0 |  | 1 | NEWENERGY | AB1-163
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.08697 |  |  | 0 |  | 1 | NEWENERGY | W3-079
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.08697 |  |  | 0 |  | 1 | CAPACITY | W3-079
900005 | 28LARRABEE E | 230 | 228 | 74 | 0 | 840 | 0 |  |  | -0.09114 |  |  | 0 |  | 1 | NEWENERGY | OSW_LARRAB
206294 | 28LARRABEE C | 230 | 228 | 74 | 0 | 360 | 360 |  |  | -0.09114 |  |  | 0 |  | 1 | CAPACITY | OSW_LARRAB
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.0912 |  |  | 0 |  | 1 | NEWENERGY | Y2-051
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.0912 |  |  | 0 |  | 1 | CAPACITY | Y2-051
923293 | AB1-138 E | 34.5 | 228 | 75 | 0 | 6 | 0 |  |  | -0.10235 |  |  | 0 |  | 1 | NEWENERGY | AB1-138
206280 | 28LAKEHURS | 34.5 | 228 | 64 | 0 | 13.8 | 11.08 |  |  | -0.10235 |  |  | 0.08446 |  | 1 | CAPACITY
923292 | AB1-138 C | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.10235 |  |  | 0 |  | 1 | CAPACITY | AB1-138
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.116 |  |  | 0.08446 |  | 1 | CAPACITY
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.116 |  |  | 0.08446 |  | 1 | CAPACITY
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 61.6 | 88.4 | 70.97 |  |  | -0.116 |  |  | 0.04435 |  | 1 | CAPACITY | LAKEWOOD
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 61.2 | 88.3 | 70.89 |  |  | -0.116 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 76.92 |  |  | -0.116 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD

## FG 28-GD-S2-S9
****** PJM Generator Deliverability Detailed Report ****** POWER-GEM [TARA Ver 2001.1a PJMGD RC3 64-bit - Wed Aug 18 16:48:02 2021]
FG Index | 9 | Monitored Facility:206302 28OYSTER C 230 206297 28MANITOU 230 1 / Contingency:JC-P2-3-JCC-230-234OC[Breaker]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
817 | 104.45 | 102.05 | AC | 114.08 | 723.1 | 1.27 | 17.94 | -3.05 | 853.34 | 833.7 | 0.001715 | 0 | 12817.4 | 0 | 10597.7 | 0.07728 | 2219.67 | 2219.72 | -0.05 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited?
900002 | 28OYSTER E | 230 | 228 | 74 | 0 | 586.7 | 0 | 586.7 | FiftyFifty | 0.68992 | 404.7759 |  | 0 | 0.7635 | 1 | NEWENERGY | OSW_OYSCK
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 27.3 | 34 | FiftyFifty | 0.68992 | 4.6245 |  | 0.12623 | 0.8738 | 1 | CAPACITY
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 27 | 31 | FiftyFifty | 0.68992 | 2.7569 |  | 0.12623 | 0.7635 | 1 | CAPACITY
206302 | 28OYSTER C | 230 | 228 | 74 | 0 | 229.3 | 229.3 | 229.3 | FiftyFifty | 0.68992 |  |  | 0 | 0.7635 | 1 | CAPACITY | OSW_OYSCK
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0 | 1.43 | FiftyFifty | 0.27445 | 0.3925 |  | 0 | 0.7635 | 1 | NEWENERGY | AB1-001
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.7 | 0.87 | FiftyFifty | 0.27445 | 0.0469 |  | 0 | 0.7635 | 1 | CAPACITY | AB1-001
900000 | CARDIFF E | 230 | 234 | 74 | 0 | 1235 | 0 | 1235 | FiftyFifty | 0.2027 | 250.3396 |  | 0 | 0.7635 | 1 | NEWENERGY | OSW_CARDIF
227900 | CARDIFF C | 230 | 234 | 74 | 0 | 275 | 275 | 275 | FiftyFifty | 0.2027 |  |  | 0 | 0.7635 | 1 | CAPACITY | OSW_CARDIF
227928 | V4-067E | 12.9 | 234 | 75 | 1.6 | 1.6 | 0 | 1.6 | FiftyFifty | 0.18965 | 0.3034 |  | 0 | 0.7635 | 1 | NEWENERGY | V4-067
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.79 | 0.98 | FiftyFifty | 0.18965 | 0.0368 |  | 0 | 0.7635 | 1 | CAPACITY | V4-067
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0 | 1.2 | FiftyFifty | 0.18962 | 0.2275 |  | 0 | 0.7635 | 1 | NEWENERGY | AB2-122
924701 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.56 | 0.7 | FiftyFifty | 0.18962 | 0.026 |  | 0 | 0.7635 | 1 | CAPACITY | AB2-122
228014 | PVILLEG | 0.48 | 234 | 65 | 1.7 | 3 | 1.04 | 3 | FiftyFifty | 0.18592 | 0.3637 |  | 0 | 0.7635 | 1 | CAPACITY
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 | 7.8 | FiftyFifty | 0.1844 | 1.4383 |  | 0.12623 | 0.6671 | 1 | ENERGY
227801 | ONTC&DCT | 13.8 | 234 | 56 | 38.6 | 38.6 | 0 | 38.6 | FiftyFifty | 0.18429 | 7.1138 |  | 0.08446 | 0.6108 | 1 | NEW
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 | 5.5 | FiftyFifty | 0.18429 | 1.0136 |  | 0.10478 | 0.5468 | 1 | ENERGY
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0 | 6 | FiftyFifty | 0.18057 | 1.0834 |  | 0 | 0.5468 | 1 | NEWENERGY | W2-030
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 2.93 | 3.65 | FiftyFifty | 0.18057 | 0.1296 |  | 0 | 0.5468 | 1 | CAPACITY | W2-030
900001 | BLE E | 138 | 234 | 74 | 0 | 310.6 | 0 | 310.6 | FiftyFifty | 0.15211 | 47.2455 |  | 0 | 0.5468 | 1 | NEWENERGY | OSW_BLE
228110 | BLE C | 138 | 234 | 74 | 0 | 121.4 | 121.4 | 121.4 | FiftyFifty | 0.15211 |  |  | 0 | 0.5468 | 1 | CAPACITY | OSW_BLE
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.61 | 2 | FiftyFifty | 0.13191 | 0.052 |  | 0 | 0.5468 | 1 | CAPACITY
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 74.48 | 85.5 | FiftyFifty | 0.10263 | 1.131 |  | 0.08446 | 0.5006 | 1 | CAPACITY
228712 | V2-041E | 13.2 | 234 | 75 | 2.5 | 2.48 | 0 | 2.11 | Adder/OL | 0.1004 | 0.2116 | 0.0036 | 0 |  | 1 | NEWENERGY | V2-041
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0 | 4.84 | Adder/OL | 0.09368 | 0.4539 | 0.0083 | 0 |  | 1 | NEWENERGY | W1-130
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  | 105 | LTF/CMTX NF | 0.04268 | 4.4809 | -0.1801
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  | 673 | LTF/CMTX NF | 0.01776 | 11.9537 | -1.1544
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  | 55.3 | CLTF | 0.01159 | 0.6407 | -0.0949
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.6 |  | 173.6 | CLTF | 0.00098 | 0.1703 | -0.2978
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 0.00098 | 0.0547 | -0.0955
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 0.00098 | 0.0536 | -0.0937
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  | 258.3 | CLTF | 0.00095 | 0.2462 | -0.4431
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  | 210 | CLTF | 0.00089 | 0.1875 | -0.3602
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 0.00084 | 0.0422 | -0.0859
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 0.00085 | 0.0421 | -0.0853
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  | 35 | CLTF | 0.00073 | 0.0257 | -0.06
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  | 57.8 | CLTF | 0.00068 | 0.0392 | -0.0991
919662 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 | -7 | Adder/NFTWR/OL | -0.08697 | 0.6088 | -0.012 | 0.05 |  | 1 | MTX NFTWR | AA2-048
228203 | P06 | 13.8 | 234 | 57 | 80.6 | 92.7 | 80.75 |  |  | 0.10096 |  |  | 0.08446 |  | 1 | CAPACITY
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 1.22 |  |  | 0.1004 |  |  | 0 |  | 1 | CAPACITY | V2-041
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 73.09 |  |  | 0.09692 |  |  | 0.08446 |  | 1 | CAPACITY
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 2.57 |  |  | 0.09368 |  |  | 0 |  | 1 | CAPACITY | W1-130
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 48.35 |  |  | 0.08659 |  |  | 0.08446 |  | 1 | CAPACITY
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.5 | 18.87 |  |  | 0.0836 |  |  | 0.08446 |  | 1 | CAPACITY
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 49.65 |  |  | 0.08204 |  |  | 0.10478 |  | 1 | CAPACITY
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0 |  |  | 0.07517 |  |  | 0 |  | 1 | NEWENERGY | V4-054
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 3.05 |  |  | 0.07517 |  |  | 0 |  | 1 | CAPACITY | V4-054
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 4.8 | 0 |  |  | 0.07515 |  |  | 0 |  | 1 | NEW
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.6 | 39.8 | 34.67 |  |  | 0.07505 |  |  | 0.08446 |  | 1 | CAPACITY
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 32.75 |  |  | 0.07505 |  |  | 0.08446 |  | 1 | CAPACITY
228721 | V2-035E | 12.9 | 234 | 75 | 1.2 | 1.2 | 0 |  |  | 0.06608 |  |  | 0 |  | 1 | NEWENERGY | V2-035
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.61 |  |  | 0.06608 |  |  | 0 |  | 1 | CAPACITY | V2-035
228343 | QUINTN#1 | 12.9 | 234 | 64 | 0 | 1.7 | 0 |  |  | 0.05958 |  |  | 0 |  | 1 | CAPACITY
228357 | V2-046E | 12.9 | 234 | 75 | 12.9 | 12.9 | 0 |  |  | 0.05184 |  |  | 0 |  | 1 | NEWENERGY | V2-046
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 6.26 |  |  | 0.05184 |  |  | 0 |  | 1 | CAPACITY | V2-046
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 192.69 |  |  | 0.05112 |  |  | 0.10478 |  | 1 | CAPACITY
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 58.9 | 47.29 |  |  | 0.04026 |  |  | 0.04435 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 58.9 | 47.29 |  |  | 0.04026 |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 175.82 |  |  | 0.03655 |  |  | 0.10478 |  | 1 | CAPACITY
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | 0.03314 |  |  | 0 |  | 1 | ENERGY
228471 | VALERO1 | 13.8 | 234 | 2 | 19.1 | 22 | 19.16 |  |  | 0.03276 |  |  | 0 |  | 1 | CAPACITY
228473 | VALERO3 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.03276 |  |  | 0 |  | 1 | CAPACITY
228484 | VALERO4 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.03276 |  |  | 0 |  | 1 | CAPACITY
228472 | VALERO2 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.03276 |  |  | 0 |  | 1 | CAPACITY
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 55.49 |  |  | 0.03118 |  |  | 0.08446 |  | 1 | CAPACITY
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 271.13 |  |  | 0.02399 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.02399 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.02399 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 998.11 |  |  | 0.01988 |  |  | 0.01494 |  | 1 | CAPACITY
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 992.1 |  |  | 0.01988 |  |  | 0.01494 |  | 1 | CAPACITY
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | 0.01988 |  |  | 0.08446 |  | 1 | ENERGY
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1026.43 |  |  | 0.01974 |  |  | 0.01494 |  | 1 | CAPACITY
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 60.21 |  |  | 0.01892 |  |  | 0.10478 |  | 1 | CAPACITY
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0 |  |  | 0.01748 |  |  | 0 |  | 1 | NEWENERGY | Y2-081
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | 0.01748 |  |  | 0 |  | 1 | CAPACITY | Y2-081
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | 0.01724 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 33.72 |  |  | 0.01723 |  |  | 0.04435 |  | 1 | CAPACITY | EAGLE POINT
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 24.08 |  |  | 0.01723 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | 0.01721 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0 |  |  | 0.01672 |  |  | 0 |  | 1 | NEWENERGY | Y3-087
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 1.84 |  |  | 0.01672 |  |  | 0 |  | 1 | CAPACITY | Y3-087
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0 |  |  | 0.01564 |  |  | 0 |  | 1 | NEWENERGY | X3-075
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | 0.015 |  |  | 0 |  | 1 | MTX | Z1-082
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 64.31 |  |  | 0.0148 |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 52.35 |  |  | 0.0148 |  |  | 0.04435 |  | 1 | CAPACITY | CAMDEN COGEN TECH
925391 | AC1-010 C | 26.4 | 231 | 75 | 0 | 6 | 0 |  |  | 0.0148 |  |  | 0 |  | 1 | NEW | AC1-010
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 19.27 |  |  | 0.0148 |  |  | 0.10478 |  | 1 | CAPACITY
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | 0.0148 |  |  | 0 |  | 1 | NEWENERGY | AC1-010
219765 | PARADISE E | 26.4 | 231 | 75 | 0 | 3.2 | 0 |  |  | 0.0148 |  |  | 0 |  | 1 | NEWENERGY | U4-036
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.3 | 9.07 |  |  | 0.0148 |  |  | 0.10478 |  | 1 | CAPACITY
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | 0.0148 |  |  | 0 |  | 1 | MTX | X2-013
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | 0.0148 |  |  | 0 |  | 1 | CAPACITY | U4-036
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | 0.0148 |  |  | 0.04435 |  | 1 | NEW | AA2-069
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 154.95 |  |  | 0.0148 |  |  | 0.04435 |  | 1 | CAPACITY | Garrison
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 93.29 |  |  | 0.0148 |  |  | 0 |  | 1 | CAPACITY | Garrison
232901 | NORTHST | 69 | 235 | 56 | 5 | 46 | 36.93 |  |  | 0.0148 |  |  | 0.08446 |  | 1 | CAPACITY
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 12.2 |  |  | 0.0148 |  |  | 0.10478 |  | 1 | CAPACITY
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 39.34 |  |  | 0.01467 |  |  | 0.08446 |  | 1 | CAPACITY
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 38.54 |  |  | 0.01467 |  |  | 0.08446 |  | 1 | CAPACITY
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 0 |  |  | 0.01426 |  |  | 0 |  | 1 | NEWENERGY | AB1-056
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 330.7 |  |  | 0.01426 |  |  | 0.10478 |  | 1 | CAPACITY
930201 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 51.71 |  |  | 0.01426 |  |  | 0 |  | 1 | CAPACITY | AB1-056
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 152.54 |  |  | 0.01426 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01426 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC2
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01426 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01426 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
232920 | IR10 | 13.2 | 235 | 55 | 12.6 | 16.1 | 12.93 |  |  | 0.01425 |  |  | 0.08446 |  | 1 | CAPACITY
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0 |  |  | 0.01424 |  |  | 0 |  | 1 | NEWENERGY | AB1-137
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 3.37 |  |  | 0.01424 |  |  | 0 |  | 1 | CAPACITY | AB1-137
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | 0.01422 |  |  | 0.10478 |  | 1 | ENERGY
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.01422 |  |  | 0 |  | 1 | NEWENERGY | Z2-077
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.01422 |  |  | 0 |  | 1 | NEWENERGY | Z2-076
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.01422 |  |  | 0 |  | 1 | CAPACITY | Z2-077
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.01422 |  |  | 0 |  | 1 | CAPACITY | Z2-076
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.41 |  |  | 0.01422 |  |  | 0 |  | 1 | CAPACITY
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.05 |  |  | 0.01418 |  |  | 0 |  | 1 | CAPACITY
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.01418 |  |  | 0.08446 |  | 1 | CAPACITY
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.01418 |  |  | 0.08446 |  | 1 | CAPACITY
917082 | CHERRYDALE E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01412 |  |  | 0 |  | 1 | NEWENERGY | Z2-012
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01412 |  |  | 0 |  | 1 | NEWENERGY | W1-003
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01412 |  |  | 0 |  | 1 | NEWENERGY | W1-006
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01412 |  |  | 0 |  | 1 | NEWENERGY | W1-004
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01412 |  |  | 0 |  | 1 | NEWENERGY | W1-005
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232915 | OH NUG4 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 39.03 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 38.94 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 38.68 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 26.05 |  |  | 0.01412 |  |  | 0.08446 |  | 1 | CAPACITY
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.01412 |  |  | 0 |  | 1 | CAPACITY | W1-003
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.01412 |  |  | 0 |  | 1 | CAPACITY | W1-004
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.01412 |  |  | 0 |  | 1 | CAPACITY | W1-005
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.01412 |  |  | 0 |  | 1 | CAPACITY | W1-006
232905 | BAYVIEW1 | 24.9 | 235 | 65 | 0 | 12.5 | 10.04 |  |  | 0.01412 |  |  | 0.12623 |  | 1 | CAPACITY
917081 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.01412 |  |  | 0 |  | 1 | CAPACITY | Z2-012
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 0 |  |  | 0.01409 |  |  | 0 |  | 1 | NEWENERGY | AA1-102
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 45.76 |  |  | 0.01409 |  |  | 0 |  | 1 | CAPACITY | AA1-102
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0 |  |  | 0.0141 |  |  | 0 |  | 1 | NEWENERGY | X1-032
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 8.03 |  |  | 0.01409 |  |  | 0 |  | 1 | CAPACITY
293670 | O-025 C | 25 | 235 | 64 | 0 | 6 | 4.82 |  |  | 0.0141 |  |  | 0 |  | 1 | CAPACITY
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0 |  |  | 0.01407 |  |  | 0 |  | 1 | NEWENERGY | Y3-058
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 5.7 | 4.58 |  |  | 0.01407 |  |  | 0 |  | 1 | CAPACITY | Y3-058
232919 | VN10 | 13.2 | 235 | 55 | 12.4 | 14.3 | 12.46 |  |  | 0.01397 |  |  | 0 |  | 1 | CAPACITY
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 122.84 |  |  | 0.01394 |  |  | 0.10478 |  | 1 | CAPACITY
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0 |  |  | 0.01394 |  |  | 0 |  | 1 | NEWENERGY | Y1-080
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 1.03 |  |  | 0.01394 |  |  | 0 |  | 1 | CAPACITY | Y1-080
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01386 |  |  | 0 |  | 1 | NEWENERGY | X3-008
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.01386 |  |  | 0 |  | 1 | CAPACITY | X3-008
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 55.4 |  |  | 0.01358 |  |  | 0.12623 |  | 1 | CAPACITY
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0 |  |  | 0.01341 |  |  | 0 |  | 1 | NEWENERGY | Y1-079
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.01341 |  |  | 0 |  | 1 | CAPACITY | Y1-079
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 57.24 |  |  | 0.01335 |  |  | 0.10478 |  | 1 | CAPACITY
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 45.76 |  |  | 0.01335 |  |  | 0.08446 |  | 1 | CAPACITY
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 44.16 |  |  | 0.01335 |  |  | 0.04435 |  | 1 | CAPACITY | DELAWARE CITY
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 14.29 |  |  | 0.01335 |  |  | 0.08446 |  | 1 | CAPACITY
219647 | COOPERSOLA E | 13.2 | 231 | 75 | 0 | 0.4 | 0 |  |  | 0.01333 |  |  | 0 |  | 1 | NEWENERGY | AB1-063
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0 |  |  | 0.01331 |  |  | 0 |  | 1 | NEWENERGY | X3-066
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 2.28 | 1.83 |  |  | 0.01331 |  |  | 0 |  | 1 | CAPACITY | X3-066
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 19.11 |  |  | 0.01331 |  |  | 0.12623 |  | 1 | CAPACITY
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.0132 |  |  | 0 |  | 1 | NEWENERGY | AB1-142
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.0132 |  |  | 0 |  | 1 | NEWENERGY | AB1-141
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.0132 |  |  | 0 |  | 1 | CAPACITY | AB1-142
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.0132 |  |  | 0 |  | 1 | CAPACITY | AB1-141
219913 | PENNSAU2 E | 26.4 | 231 | 75 | 0 | 8.2 | 0 |  |  | 0.01259 |  |  | 0 |  | 1 | NEWENERGY | AD2-042
219915 | CINNAMSOL E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | 0.01259 |  |  | 0 |  | 1 | NEWENERGY | AD2-027
219912 | PENNSAU2 C | 26.4 | 231 | 75 | 0 | 5 | 0 |  |  | 0.01259 |  |  | 0 |  | 1 | NEW | AD2-042
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.63 | 3.72 |  |  | 0.01259 |  |  | 0 |  | 1 | CAPACITY
219914 | CINNAMSOL C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | 0.01259 |  |  | 0 |  | 1 | CAPACITY | AD2-027
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.4 |  |  | 0.01259 |  |  | 0 |  | 1 | CAPACITY
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01255 |  |  | 0 |  | 1 | NEWENERGY | AB2-179
233931 | AB2-179 C | 0.38 | 235 | 75 | 0 | 38 | 30.51 |  |  | 0.01255 |  |  | 0 |  | 1 | CAPACITY | AB2-179
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.09 |  |  | 0.01216 |  |  | 0 |  | 1 | CAPACITY
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 18.47 |  |  | 0.01184 |  |  | 0.08446 |  | 1 | CAPACITY
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 18.39 |  |  | 0.01184 |  |  | 0.08446 |  | 1 | CAPACITY
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 13.81 |  |  | 0.01181 |  |  | 0.08446 |  | 1 | CAPACITY
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 139.7 |  |  | 0.01161 |  |  | 0.10478 |  | 1 | CAPACITY
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01161 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01161 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01158 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 69.05 |  |  | 0.01158 |  |  | 0.10478 |  | 1 | CAPACITY
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 11.4 |  |  | 0.01158 |  |  | 0.08446 |  | 1 | CAPACITY
925112 | AB2-168 E | 34.5 | 235 | 75 | 0 | 5.2 | 0 |  |  | 0.01149 |  |  | 0 |  | 1 | NEWENERGY | AB2-168
925111 | AB2-168 C | 34.5 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.01149 |  |  | 0 |  | 1 | CAPACITY | AB2-168
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 361.29 |  |  | 0.0107 |  |  | 0.10478 |  | 1 | CAPACITY
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 148.77 |  |  | 0.0107 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC1
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.00993 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.00993 |  |  | 0.04435 |  | 1 | CAPACITY | PHILLIPS ISLAND
213893 | PHLISST1 | 20 | 230 | 58 | 184 | 267 | 214.36 |  |  | 0.00993 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.00993 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.5 | 0 |  |  | 0.00955 |  |  | 0 |  | 1 | NEWENERGY | AC1-030
925561 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | 0.00955 |  |  | 0 |  | 1 | CAPACITY | AC1-030
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0 |  |  | 0.00952 |  |  | 0 |  | 1 | NEWENERGY | X1-071
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.28 |  |  | 0.00952 |  |  | 0 |  | 1 | CAPACITY | X1-071
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | 0.00924 |  |  | 0.08446 |  | 1 | CAPACITY
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | 0.00924 |  |  | 0.08446 |  | 1 | CAPACITY
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 31.31 |  |  | 0.00796 |  |  | 0.08446 |  | 1 | CAPACITY
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | 0.00795 |  |  | 0.08446 |  | 1 | CAPACITY
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | 0.00795 |  |  | 0.08446 |  | 1 | CAPACITY
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | 0.00783 |  |  | 0.10478 |  | 1 | CAPACITY
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | 0.00781 |  |  | 0.10478 |  | 1 | CAPACITY
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 27.3 |  |  | 0.00782 |  |  | 0.08446 |  | 1 | CAPACITY
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | 0.00777 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 238 | 191.08 |  |  | 0.00777 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | 0.00777 |  |  | 0.04435 |  | 1 | CAPACITY | LIBERTY EDDY
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | 0.0077 |  |  | 0.08446 |  | 1 | CAPACITY
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | 0.00724 |  |  | 0.08446 |  | 1 | CAPACITY
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0 |  |  | 0.00683 |  |  | 0 |  | 1 | NEWENERGY | W2-071
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.85 |  |  | 0.00683 |  |  | 0 |  | 1 | CAPACITY | W2-071
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 130.87 |  |  | 0.00642 |  |  | 0.04435 |  | 1 | CAPACITY | GRAYS FERRY
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | 0.0064 |  |  | 0.08446 |  | 1 | CAPACITY
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | 0.00639 |  |  | 0.08446 |  | 1 | CAPACITY
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | 0.00639 |  |  | 0.08446 |  | 1 | CAPACITY
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0 |  |  | 0.00619 |  |  | 0 |  | 1 | NEWENERGY | AC1-017
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0 |  |  | 0.00619 |  |  | 0 |  | 1 | NEWENERGY | X1-070
925451 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 1.12 |  |  | 0.00619 |  |  | 0 |  | 1 | CAPACITY | AC1-017
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.96 |  |  | 0.00619 |  |  | 0 |  | 1 | CAPACITY | X1-070
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | 0.00605 |  |  | 0.08446 |  | 1 | CAPACITY
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | 0.00605 |  |  | 0.08446 |  | 1 | CAPACITY
214030 | WAYNEJCT | 13.8 | 230 | 2 | 0 | 8.8 | 7.07 |  |  | 0.00603 |  |  | 0 |  | 1 | CAPACITY
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0 |  |  | 0.00583 |  |  | 0 |  | 1 | NEWENERGY | Y1-075
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 0.00583 |  |  | 0 |  | 1 | CAPACITY | Y1-075
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0 |  |  | 0.0057 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 S
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 0.0057 |  |  | 0 |  | 1 | CAPACITY | AB1-025 S
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 77.07 |  |  | 0.00533 |  |  | 0.07484 |  | 1 | CAPACITY
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | 0.00533 |  |  | 0.07484 |  | 1 | CAPACITY
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | 0.00533 |  |  | 0.07484 |  | 1 | CAPACITY
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 38.54 |  |  | 0.00533 |  |  | 0.07484 |  | 1 | CAPACITY
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | 0.00533 |  |  | 0.07484 |  | 1 | CAPACITY
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | 0.00533 |  |  | 0.07484 |  | 1 | CAPACITY
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 369.31 |  |  | 0.00524 |  |  | 0.04435 |  | 1 | CAPACITY | Y1-065
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00524 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00524 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200055 | ROCKSP 4 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00524 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 4
200054 | ROCKSP 3 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00524 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 3
200052 | ROCKSP 1 | 18 | 225 | 57 | 145.7 | 167.5 | 145.91 |  |  | 0.00524 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 1
200053 | ROCKSP 2 | 18 | 225 | 57 | 144.9 | 166.5 | 145.04 |  |  | 0.00524 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 2
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | 0.00483 |  |  | 0 |  | 1 | ENERGY
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0 |  |  | 0.00464 |  |  | 0 |  | 1 | NEWENERGY | V4-005
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.88 |  |  | 0.00464 |  |  | 0 |  | 1 | CAPACITY | V4-005
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 0 |  |  | 0.00374 |  |  | 0 |  | 1 | NEWENERGY | W3-080
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.00374 |  |  | 0.08446 |  | 1 | CAPACITY
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.00374 |  |  | 0.08446 |  | 1 | CAPACITY
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.00374 |  |  | 0.08446 |  | 1 | CAPACITY
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.00374 |  |  | 0.08446 |  | 1 | CAPACITY
925442 | AC1-016 E | 26.4 | 231 | 75 | 0 | 5.45 | 0 |  |  | 0.00374 |  |  | 0 |  | 1 | NEWENERGY | AC1-016
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | 0.00374 |  |  | 0 |  | 1 | NEWENERGY | W2-102
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | 0.00374 |  |  | 0 |  | 1 | NEWENERGY | W4-103
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | 0.00374 |  |  | 0 |  | 1 | NEWENERGY | Y3-026
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | 0.00374 |  |  | 0 |  | 1 | CAPACITY | Y3-026
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 2.97 |  |  | 0.00374 |  |  | 0 |  | 1 | CAPACITY | W3-080
925441 | AC1-016 C | 26.4 | 231 | 75 | 0 | 3.34 | 2.68 |  |  | 0.00374 |  |  | 0 |  | 1 | CAPACITY | AC1-016
219685 | NATIONAL_GYP | 26 | 231 | 2 | 0 | 2.8 | 2.25 |  |  | 0.00374 |  |  | 0 |  | 1 | CAPACITY
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | 0.00374 |  |  | 0 |  | 1 | CAPACITY | W4-103
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | 0.00374 |  |  | 0 |  | 1 | CAPACITY | W2-102
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 38.54 |  |  | 0.00364 |  |  | 0.08446 |  | 1 | CAPACITY
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | 0.00327 |  |  | 0.0316 |  | 1 | CAPACITY
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | 0.00326 |  |  | 0.0316 |  | 1 | CAPACITY
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | 0.00327 |  |  | 0.0316 |  | 1 | CAPACITY
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | 0.00326 |  |  | 0.0316 |  | 1 | CAPACITY
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 260.3 | 208.98 |  |  | 0.00317 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | 0.00317 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill B
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | 0.00317 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 205.69 |  |  | 0.00317 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | 0.00317 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill A
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | 0.00317 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1034.24 |  |  | 0.00295 |  |  | 0.01494 |  | 1 | CAPACITY
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 306.69 |  |  | 0.00294 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00294 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA2
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 154.95 |  |  | 0.00294 |  |  | 0 |  | 1 | CAPACITY | DELTA
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00294 |  |  | 0 |  | 1 | CAPACITY | DELTA
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00294 |  |  | 0 |  | 1 | CAPACITY | DELTA
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1049.33 |  |  | 0.00285 |  |  | 0.01494 |  | 1 | CAPACITY
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 22.48 |  |  | 0.00233 |  |  | 0.10478 |  | 1 | CAPACITY
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0 |  |  | 0.00078 |  |  | 0 |  | 1 | NEWENERGY | AA2-072
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 140.6 | 112.88 |  |  | 0.00072 |  |  | 0.08446 |  | 1 | CAPACITY
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 91.2 |  |  | 0.00072 |  |  | 0.08446 |  | 1 | CAPACITY
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 83.5 |  |  | 0.00072 |  |  | 0.08446 |  | 1 | CAPACITY
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 41.75 |  |  | 0.00072 |  |  | 0.08446 |  | 1 | CAPACITY
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.21 |  |  | 0.00072 |  |  | 0 |  | 1 | CAPACITY
220904 | CRANE G2 | 20 | 232 | 12 | 60 | 195 | 0 |  |  | 0.00064 |  |  | 0.10478 |  | 1 | NEW
220905 | CRANE GT | 4.16 | 232 | 55 | 0 | 14 | 0 |  |  | 0.00064 |  |  | 0.08446 |  | 1 | NEW
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | 0.00061 |  |  | 0 |  | 1 | ENERGY
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 256.27 |  |  | 0.00061 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | 0.00061 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | 0.00061 |  |  | 0.04435 |  | 1 | CAPACITY | HUNTERSTOWN
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 134.08 |  |  | 0.00061 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.5 | 24.49 |  |  | 0.00059 |  |  | 0.08446 |  | 1 | CAPACITY
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 30 | 24.08 |  |  | 0.00059 |  |  | 0.08446 |  | 1 | CAPACITY
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 45.76 |  |  | 0.00058 |  |  | 0.10478 |  | 1 | CAPACITY
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 246 |  |  | 0.00056 |  |  | 0.10478 |  | 1 | CAPACITY
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 102.85 |  |  | 0.00056 |  |  | 0.10478 |  | 1 | CAPACITY
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | 0.00056 |  |  | 0.08446 |  | 1 | ENERGY
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 10.68 |  |  | 0.00056 |  |  | 0.08446 |  | 1 | CAPACITY
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 516 |  |  | 0.00054 |  |  | 0.10478 |  | 1 | CAPACITY
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 512.95 |  |  | 0.00054 |  |  | 0.10478 |  | 1 | CAPACITY
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 318.73 |  |  | 0.00054 |  |  | 0.10478 |  | 1 | CAPACITY
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.49 |  |  | 0.0004 |  |  | 0 |  | 1 | CAPACITY
226895 | WOAKV2-037 E | 69 | 233 | 65 | 0 | 4.5 | 0 |  |  | 0.00033 |  |  | 0 |  | 1 | ENERGY
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 695.27 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 675.85 |  |  | 0.00026 |  |  | 0.01494 |  | 1 | CAPACITY
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | 0.00026 |  |  | 0.08446 |  | 1 | ENERGY
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.76 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0 |  |  | 0.00025 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 N
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0 |  |  | 0.00025 |  |  | 0 |  | 1 | NEWENERGY | AB2-157
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.69 |  |  | 0.00024 |  |  | 0 |  | 1 | CAPACITY
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY | AB1-025 N
925011 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.64 |  |  | 0.00025 |  |  | 0 |  | 1 | CAPACITY | AB2-157
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 477.7 |  |  | 0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 469.91 |  |  | 0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
227024 | SMECOCT | 13.8 | 238 | 57 | 30 | 80.2 | 64.39 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 19.59 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 14.45 |  |  | 0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 497.29 |  |  | 0.00022 |  |  | 0.10478 |  | 1 | CAPACITY
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 492.39 |  |  | 0.00022 |  |  | 0.10478 |  | 1 | CAPACITY
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 0 |  |  | 0.00022 |  |  | 0 |  | 1 | NEWENERGY | AC2-101
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 0 |  |  | 0.00022 |  |  | 0 |  | 1 | NEWENERGY | AC2-120
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | CAPACITY
226915 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 9.92 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY | AC2-101
226912 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 8.39 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY | AC2-120
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 272.01 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | 0.00022 |  |  | 0.04435 |  | 1 | CAPACITY | WALDORF
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY | WALDORF
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0 |  |  | 0.0002 |  |  | 0 |  | 1 | NEWENERGY | W2-056
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 3.36 |  |  | 0.0002 |  |  | 0 |  | 1 | CAPACITY | W2-056
910861 | X3-087 C | 230 | 233 | 58 | 0 | 744 | 597.33 |  |  | 0.00017 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
917371 | Z2-060 | 230 | 233 | 58 | 0 | 116 | 93.13 |  |  | 0.00017 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
920642 | AA2-170 E | 230 | 233 | 58 | 0 | 19.1 | 0 |  |  | 0.00017 |  |  | 0.04435 |  | 1 | NEW | AA2-170
920641 | AA2-170 C | 230 | 233 | 58 | 0 | 92 | 73.86 |  |  | 0.00017 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-170
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 64.23 |  |  | 0.00017 |  |  | 0 |  | 1 | CAPACITY | PANDA
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | 0.00017 |  |  | 0 |  | 1 | CAPACITY | PANDA
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | 0.00017 |  |  | 0.04435 |  | 1 | CAPACITY | PANDA
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 330 | 264.94 |  |  | 0.00016 |  |  | 0 |  | 1 | CAPACITY | X4-035
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | 0.00016 |  |  | 0 |  | 1 | CAPACITY | X4-035
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | 0.00016 |  |  | 0.04435 |  | 1 | CAPACITY | X4-035
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | 0.00014 |  |  | 0.10478 |  | 1 | ENERGY
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | 3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | 3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 41.75 |  |  | 3e-05 |  |  | 0.10478 |  | 1 | CAPACITY
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 14.45 |  |  | 3e-05 |  |  | 0.08446 |  | 1 | CAPACITY
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-129
924771 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEW | AB2-129
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -8e-05 |  |  | 0.08446 |  | 1 | CAPACITY
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 1.04 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY | T20
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 245.67 |  |  | -0.0001 |  |  | 0 |  | 1 | CAPACITY | X4-039
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.0001 |  |  | 0.04435 |  | 1 | CAPACITY | X4-039
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.0001 |  |  | 0 |  | 1 | CAPACITY | X4-039
313821 | 6PACIFIC | 230 | 345 | 75 | 0 | 0.09 | 0 |  |  | -0.00011 |  |  | 0 |  | 1 | NEWENERGY
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 201.52 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00014 |  |  | 0.04435 |  | 1 | CAPACITY | POSSUM POINT
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 28.74 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | CAPACITY
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 28.66 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | CAPACITY
314088 | 6VANDORN | 230 | 345 | 2 | 7 | 21 | 16.86 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | CAPACITY
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | CAPACITY
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00017 |  |  | 0 |  | 1 | NEWENERGY | AC2-072
932521 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00017 |  |  | 0 |  | 1 | CAPACITY | AC2-072
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 0.68 | 0 |  |  | -0.00019 |  |  | 0 |  | 1 | NEWENERGY
235002 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0 |  |  | -0.0002 |  |  | 0 |  | 1 | NEW | AC1-039
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0 |  |  | -0.0002 |  |  | 0 |  | 1 | NEWENERGY | AC1-039
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0 |  |  | -0.0002 |  |  | 0 |  | 1 | NEWENERGY | AA1-109
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 3.61 |  |  | -0.0002 |  |  | 0 |  | 1 | CAPACITY | AA1-109
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.00021 |  |  | 0 |  | 1 | NEWENERGY | W1-116
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 4.27 |  |  | -0.00021 |  |  | 0 |  | 1 | CAPACITY | W1-116
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 1.61 |  |  | -0.00021 |  |  | 0 |  | 1 | CAPACITY
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 152.3 | 122.28 |  |  | -0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 120.19 |  |  | -0.00023 |  |  | 0.10478 |  | 1 | CAPACITY
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 128.86 |  |  | -0.00023 |  |  | 0.08446 |  | 1 | CAPACITY
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00023 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 0 |  |  | -0.00024 |  |  | 0 |  | 1 | NEWENERGY | AB2-029
923213 | AB1-125 E OP | 34.5 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.00023 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
923202 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.00023 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0 |  |  | -0.00023 |  |  | 0 |  | 1 | NEWENERGY | AB1-096
923212 | AB1-125 C OP | 34.5 | 201 | 75 | 0 | 5.7 | 0 |  |  | -0.00023 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
314078 | 3REMNGTN | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00024 |  |  | 0 |  | 1 | CAPACITY | AB2-029
930521 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00023 |  |  | 0 |  | 1 | CAPACITY | AB1-096
315033 | 1BIRCHWDA | 18 | 345 | 13 | 85 | 238 | 191.08 |  |  | -0.00024 |  |  | 0.10478 |  | 1 | CAPACITY
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.00025 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 2
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.00025 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 1
926737 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | AC1-158 1
926738 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | AC1-158 2
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 6.98 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 128.94 |  |  | -0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 128.54 |  |  | -0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 128.3 |  |  | -0.00026 |  |  | 0.08446 |  | 1 | CAPACITY
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0 |  |  | -0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC2-136
933251 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 4.41 |  |  | -0.00026 |  |  | 0 |  | 1 | CAPACITY | AC2-136
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 761.83 |  |  | -0.00027 |  |  | 0.01494 |  | 1 | CAPACITY
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 761.51 |  |  | -0.00027 |  |  | 0.01494 |  | 1 | CAPACITY
923872 | AB2-027 E | 34.5 | 201 | 75 | 0 | 5.5 | 0 |  |  | -0.00028 |  |  | 0 |  | 1 | NEWENERGY | AB2-027
235006 | AB2-027 C | 34.5 | 201 | 75 | 0 | 3.3 | 0 |  |  | -0.00028 |  |  | 0 |  | 1 | NEW | AB2-027
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00028 |  |  | 0 |  | 1 | CAPACITY
316149 | AD1-046 E | 230 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00029 |  |  | 0 |  | 1 | NEWENERGY | AD1-044
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | W4-102
237799 | 01AA2-159 C | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
920562 | AA2-159 E | 34.5 | 201 | 75 | 0 | 7.3 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00029 |  |  | 0 |  | 1 | NEWENERGY | AE1-124
316148 | AD1-046 C | 230 | 345 | 75 | 0 | 30.7 | 24.65 |  |  | -0.00029 |  |  | 0 |  | 1 | CAPACITY | AD1-044
938961 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00029 |  |  | 0 |  | 1 | CAPACITY | AE1-124
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY | W4-102
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-158
925021 | AB2-158 C | 230 | 345 | 75 | 0 | 61 | 48.97 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY | AB2-158
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB2-097
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | AC1-118
314766 | 6LOUISA | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY
314190 | 6WESTMOR | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | CAPACITY | AC1-118
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 2.09 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.88 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 136.49 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
923192 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | AA1-095
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 2.33 |  |  | -0.00031 |  |  | 0 |  | 1 | CAPACITY | AA1-095
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.00033 |  |  | 0.08446 |  | 1 | CAPACITY
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.00033 |  |  | 0.08446 |  | 1 | CAPACITY
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 126.85 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00033 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 6
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00033 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 5
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 61.9 |  |  | -0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00032 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00032 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 2
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00033 |  |  | 0 |  | 1 | NEWENERGY | AC2-138
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 19.99 |  |  | -0.00033 |  |  | 0.10478 |  | 1 | CAPACITY
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00032 |  |  | 0 |  | 1 | CAPACITY | South Anna 2
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00032 |  |  | 0 |  | 1 | CAPACITY | South Anna 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 19.27 |  |  | -0.00033 |  |  | 0.10478 |  | 1 | CAPACITY
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 6.3 | 5.06 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | AC2-138
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0 |  |  | -0.00033 |  |  | 0 |  | 1 | NEWENERGY | AA1-092
314172 | 6DUNNSVL | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00033 |  |  | 0 |  | 1 | NEWENERGY
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 6.42 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | AA1-092
314734 | 6CASHSCORNER | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00034 |  |  | 0 |  | 1 | NEWENERGY
314222 | 6HANOVER | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00034 |  |  | 0 |  | 1 | NEWENERGY
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AC1-112
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AB1-027
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AC2-070
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 8.83 |  |  | -0.00036 |  |  | 0.12623 |  | 1 | CAPACITY
314241 | 6OLDCHRC | 230 | 345 | 75 | 0 | 1.82 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AB1-027
932501 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 7.39 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AC2-070
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 3.21 |  |  | -0.00035 |  |  | 0 |  | 1 | CAPACITY
314213 | 3CARVER | 115 | 345 | 75 | 0 | 0 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEW | AC1-107
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00036 |  |  | 0.04435 |  | 1 | NEW | AC1-107
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEW | AC1-107
926785 | AC1-164 E | 0.44 | 345 | 75 | 0 | 99.2 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AC1-164
316114 | AB2-068 ST | 22 | 345 | 58 | 0 | 492 | 395.01 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316113 | AB2-068 CT2 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316112 | AB2-068 CT1 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00036 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-068
926784 | AC1-164 C | 0.44 | 345 | 75 | 0 | 220.8 | 177.27 |  |  | -0.00036 |  |  | 0 |  | 1 | NEW | AC1-164
315085 | 1SPRUNCC | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00037 |  |  | 0.10478 |  | 1 | NEW
315086 | 1SPRUNCD | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00037 |  |  | 0.10478 |  | 1 | NEW
314189 | 6PAPERMILL | 230 | 345 | 1 | 12 | 37 | 0 |  |  | -0.00036 |  |  | 0.10478 |  | 1 | ENERGY
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AC1-065
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 104.93 |  |  | -0.00037 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 7
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 103.25 |  |  | -0.00037 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 8
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 69.05 |  |  | -0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 68.97 |  |  | -0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 68.72 |  |  | -0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 68.64 |  |  | -0.00036 |  |  | 0.10478 |  | 1 | CAPACITY
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 53.15 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 48.17 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7
925863 | AC1-065 C | 0.39 | 345 | 75 | 0 | 41.8 | 33.56 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AC1-065
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AC2-137
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AD2-030
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | AE1-074
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AB2-024
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY | AD1-063
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 16.06 |  |  | -0.00036 |  |  | 0.12623 |  | 1 | CAPACITY
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.3 | 13.09 |  |  | -0.00036 |  |  | 0.12623 |  | 1 | CAPACITY
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 11.96 |  |  | -0.00037 |  |  | 0.12623 |  | 1 | CAPACITY
938551 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | AE1-074
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AD2-030
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 11.4 | 9.15 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AC2-137
314375 | 6CORRCTN | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AB2-024
314187 | 3WAN 176 | 115 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY
934391 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY | AD1-063
314176 | 6HARMONY | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00036 |  |  | 0 |  | 1 | NEWENERGY
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 4.98 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY
314294 | 6ENON | 230 | 345 | 75 | 0 | 0.23 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | -0.00038 |  |  | 0.10478 |  | 1 | ENERGY
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 106.94 |  |  | -0.00038 |  |  | 0.07484 |  | 1 | CAPACITY
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 101.16 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00038 |  |  | 0.04435 |  | 1 | CAPACITY | HOPEWELL HCF
208904 | HOLT 696 | 13.2 | 229 | 60 | 23 | 58.4 | 46.89 |  |  | -0.00038 |  |  | 0.07484 |  | 1 | CAPACITY
208903 | HOLT 695 | 13.2 | 229 | 60 | 26 | 53.2 | 42.71 |  |  | -0.00038 |  |  | 0.07484 |  | 1 | CAPACITY
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00038 |  |  | 0.10478 |  | 1 | CAPACITY
919535 | V4-027 E | 0 | 229 | 75 | 0 | 3.1 | 0 |  |  | -0.00038 |  |  | 0 |  | 1 | NEWENERGY | V4-027
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 3.93 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY | V4-027
208474 | KINZ 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY
314177 | 3HAYES89 | 115 | 345 | 75 | 0 | 0.31 | 0 |  |  | -0.00038 |  |  | 0 |  | 1 | NEWENERGY
313828 | 3WHITEMARSH | 115 | 345 | 75 | 0 | 0.05 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 788.9 | 633.38 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 422.86 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY | AB2-134
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00039 |  |  | 0.04435 |  | 1 | CAPACITY | WARREN COUNTY CC
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY | AB2-160
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY | AB2-190
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 89.92 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | AB2-190
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 57.65 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | AB2-134
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 24.41 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | AB2-160
316158 | AD2-164 | 230 | 345 | 57 | 0 | 26.7 | 21.44 |  |  | -0.00039 |  |  | 0.08446 |  | 1 | CAPACITY
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 12.04 |  |  | -0.00039 |  |  | 0.12623 |  | 1 | CAPACITY
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 8.03 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY
313812 | 6ROCKLANDING | 230 | 345 | 75 | 0 | 0.11 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 678.09 |  |  | -0.00039 |  |  | 0.01494 |  | 1 | CAPACITY
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 677.21 |  |  | -0.00039 |  |  | 0.01494 |  | 1 | CAPACITY
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AB2-161
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 69.77 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 69.69 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
314331 | 6POE | 230 | 345 | 75 | 0 | 12.27 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AD1-060
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AE1-162
935212 | AD1-156 E | 230 | 345 | 75 | 0 | 7.92 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AD1-156
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 23.76 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AB2-161
316258 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AE1-162
935211 | AD1-156 C | 230 | 345 | 75 | 0 | 11.82 | 9.49 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AD1-156
314533 | 6SMITFLD | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY
934362 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 4.58 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AD1-060
314525 | 6KINGFORK | 230 | 345 | 75 | 0 | 24.3 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
314550 | 6HICKORY | 230 | 345 | 75 | 0 | 22.93 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 88.96 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 87.83 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 86.31 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
314466 | 6FENTRES | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | Z1-068
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AC1-147
316145 | AE1-027 E | 230 | 345 | 75 | 0 | 6.9 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AE1-027
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AC2-196
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AC1-027
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AB2-026
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AE1-075
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AD1-144
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AD2-215
316147 | AE1-028 E | 230 | 345 | 75 | 0 | 4.4 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AE1-028
314333 | 6POWHATN | 230 | 345 | 75 | 0 | 3.97 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AB2-026
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 12.2 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 11.96 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
316144 | AE1-027 C | 230 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AE1-027
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 10.36 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
926661 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 10.12 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AC1-147
938561 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AE1-075
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 9.55 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 9.05 |  |  | -0.0004 |  |  | 0.12623 |  | 1 | CAPACITY
933731 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 8.03 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AC2-196
316150 | AD2-215 C | 230 | 345 | 76 | 0 | 9.8 | 7.87 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AD2-215
935111 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 7.79 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AD1-144
314491 | 3PENDLTN | 115 | 345 | 75 | 0 | 1.89 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AC1-027
316146 | AE1-028 C | 230 | 345 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AE1-028
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.2 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | Z1-068
314453 | 6CHRHLND | 230 | 345 | 75 | 0 | 0.08 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY
314487 | 3MCLAUGH | 115 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AA1-139
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 63.18 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AA1-139
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | Y1-086
314632 | 6AYDLETOLD | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
313717 | 6SLIGO L2192 | 230 | 345 | 75 | 0 | 12.34 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | AB2-022
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | Z2-030
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AC2-174
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | Z2-027
933571 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEW | AC2-174
314645 | 6SLIGO L269 | 230 | 345 | 75 | 0 | 3.22 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 12.04 |  |  | -0.00041 |  |  | 0.12623 |  | 1 | CAPACITY
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 10.44 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | AB2-022
314648 | 6SUNBURY | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 3.93 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | Z2-030
314638 | 6ELIZ CT | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | Y1-086
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 1.61 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY
314639 | 6TANGLEW | 230 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | Z2-027
314640 | 6KITTY HAWK | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
901082 | W1-029 E | 230 | 345 | 74 | 0 | 261 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | W1-029
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | W1-029
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY | AB2-025
314651 | 6WINFALL | 230 | 345 | 75 | 0 | 3.35 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY
314435 | 6SAPONY | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY | AB2-025
942852 | AE2-304 E | 230 | 345 | 75 | 0 | 1.4 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY | AE2-304
942851 | AE2-304 C | 230 | 345 | 75 | 0 | 3.3 | 2.65 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY | AE2-304
314662 | 6S HERTFORD | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.56 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY | Z1-036
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | -0.00044 |  |  | 0.10478 |  | 1 | ENERGY
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY | Z1-036
314637 | 6EDENTON | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00044 |  |  | 0 |  | 1 | NEWENERGY | AA2-059
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 480.11 |  |  | -0.00044 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 452.01 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00044 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00044 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-086
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00044 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00045 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNSWICK COUNTY
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 0 |  |  | -0.00044 |  |  | 0 |  | 1 | NEW | AB2-015
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 0 |  |  | -0.00044 |  |  | 0 |  | 1 | NEWENERGY | AB2-015
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00045 |  |  | 0 |  | 1 | NEWENERGY | AA2-178
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | AA2-178
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00045 |  |  | 0.10478 |  | 1 | CAPACITY
314541 | 3WATKINS | 115 | 345 | 1 | 0 | 4 | 0 |  |  | -0.00045 |  |  | 0 |  | 1 | ENERGY
314566 | 3CRESWEL | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00045 |  |  | 0 |  | 1 | NEWENERGY
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 322.35 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AA2-088
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 198.31 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00046 |  |  | 0.04435 |  | 1 | CAPACITY | BEAR GARDEN
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00046 |  |  | 0.04435 |  | 1 | CAPACITY | FLUVANNA
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 30.51 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AA2-088
314594 | 6PLYMOTH | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 2
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AB1-128
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AB1-127
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AC1-116
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AC2-071
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AB2-100 2
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AB2-100 1
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AB2-045
314589 | 3MURPHYS | 115 | 345 | 75 | 0 | 4.66 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | V4-068
932511 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AC2-071
314677 | 6BUCKING | 230 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AB2-045
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | V4-068
235041 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AB1-128
235040 | 01AB1-127 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AB1-127
314620 | 6CASHIE | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY
926451 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 3.77 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AC1-116
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY
313826 | 6HYDRAULIC | 230 | 345 | 75 | 0 | 0.04 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AB2-174
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AA1-065
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AA1-063A
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 53.6 | 43.03 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AA1-065
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 40.87 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | AA1-063A
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 40.14 |  |  | -0.00047 |  |  | 0.19858 |  | 1 | CAPACITY
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 33.72 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | AB2-174
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEW
314617 | 3TUNIS | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY
314568 | 3EARLEYS | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AB2-099
314551 | 3AHOSKIE | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY
314626 | 3WOODLND | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AB2-099
314604 | 3SEABORD | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.5 | 354.46 |  |  | -0.00049 |  |  | 0.10478 |  | 1 | CAPACITY
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 350.93 |  |  | -0.00049 |  |  | 0.10478 |  | 1 | CAPACITY
923262 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
923991 | AB2-040 C O1 | 115 | 345 | 75 | 0 | 44 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEW | AB2-040
923992 | AB2-040 E O1 | 115 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AB2-040
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
925122 | AB2-169 E | 115 | 345 | 75 | 0 | 35 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AB2-169
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AA2-053
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.00048 |  |  | 0.07484 |  | 1 | CAPACITY
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.00048 |  |  | 0.07484 |  | 1 | CAPACITY
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 76.6 | 61.5 |  |  | -0.00049 |  |  | 0.04435 |  | 1 | CAPACITY | ROSEMARY
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 44 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AA2-053
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 40.38 |  |  | -0.00049 |  |  | 0.07484 |  | 1 | CAPACITY
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 38.54 |  |  | -0.00049 |  |  | 0.07484 |  | 1 | CAPACITY
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 47.5 | 38.13 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 32.44 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | AB1-173
925121 | AB2-169 C | 115 | 345 | 75 | 0 | 39 | 31.31 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AB2-169
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 35.9 | 28.82 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AB1-173
314579 | 6HORNRTN | 230 | 345 | 75 | 0 | 3.91 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
314266 | 6NORTHAMPTON | 230 | 345 | 75 | 0 | 2.47 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 8.83 |  |  | -0.00049 |  |  | 0.12623 |  | 1 | CAPACITY
314559 | 3CAROLNA | 115 | 345 | 75 | 0 | 1.21 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
314596 | 3POPLR C | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
314582 | 3KELFORD | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | Z2-043
314762 | 3JAMES R | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AD1-085
314713 | 3PAMPLIN | 115 | 345 | 75 | 0 | 9.73 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY
314807 | 3MT JACK | 115 | 345 | 75 | 0 | 9.7 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
316143 | AD1-160 E | 115 | 345 | 75 | 0 | 9.1 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | AD1-160
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | AD1-157
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AC2-074
314578 | 3HORNRTN | 115 | 345 | 75 | 0 | 5.15 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
313853 | 3PONTONDP | 115 | 345 | 2 | 0 | 4 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | ENERGY
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 16 | 12.85 |  |  | -0.0005 |  |  | 0.12623 |  | 1 | CAPACITY
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 9.88 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AD1-085
314603 | 3SCOT NK | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY
932541 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AC2-074
935221 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | AD1-157
316142 | AD1-160 C | 115 | 345 | 75 | 0 | 6.6 | 5.3 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | AD1-160
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 1.04 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.64 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY | AC1-036
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00051 |  |  | 0.08446 |  | 1 | CAPACITY
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00051 |  |  | 0.08446 |  | 1 | CAPACITY
314593 | 3PARMELE | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY
925611 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 6.9 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | AC1-036
314629 | 3MARTNCO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY
314798 | 3MERCK5 | 115 | 345 | 75 | 0 | 0.16 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY | AC1-054
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 35.73 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | AC1-054
314574 | 6EVERETS | 230 | 345 | 75 | 0 | 5.89 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY | AE1-099
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY | AE1-098
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AA1-067
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | AE1-099
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | AE1-098
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AB2-043
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AB2-060
919702 | AA2-057 E OP | 115 | 345 | 75 | 0 | 21.1 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AA2-057
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 43.67 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | AB2-060
313719 | 3CHESTNUT | 115 | 345 | 75 | 0 | 44.7 | 35.89 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | AA2-057
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AB2-077
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AB2-078
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AB2-079
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 15.17 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | AB2-043
924301 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00052 |  |  | 0 |  | 1 | NEW | AB2-077
924321 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00052 |  |  | 0 |  | 1 | NEW | AB2-079
924311 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00052 |  |  | 0 |  | 1 | NEW | AB2-078
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY | Z2-088
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 53 | 42.55 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | Z2-088
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
314608 | 3TARBORO | 115 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY | Z2-044
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 12.04 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
314623 | 3WITAKRS | 115 | 345 | 75 | 0 | 2.51 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | Z2-044
314549 | 3TOT1 | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY
314557 | 3BETHELC | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY
314607 | 3TAR RVR | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY
314545 | 3TOT5 | 115 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY
314560 | 3CNETO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY | AB2-059
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY | AB1-081
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 52.99 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | AB2-059
922922 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | AB1-081
314554 | 3BTLEBRO | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY
314205 | 3HEARTS | 115 | 345 | 75 | 0 | 0.41 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 0 |  |  | -0.00055 |  |  | 0 |  | 1 | NEWENERGY | T157
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 0 |  |  | -0.00055 |  |  | 0 |  | 1 | NEWENERGY | AC1-105
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 36.61 |  |  | -0.00055 |  |  | 0.10478 |  | 1 | CAPACITY
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 27.7 |  |  | -0.00055 |  |  | 0 |  | 1 | CAPACITY | AC1-105
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 16.46 |  |  | -0.00055 |  |  | 0 |  | 1 | CAPACITY | T157
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 404.48 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 403.68 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 403.27 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 403.2 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315616 | AA1-038 C | 230 | 345 | 74 | 0 | 76.6 | 0 |  |  | -0.00057 |  |  | 0 |  | 1 | NEW | AA1-038
918232 | AA1-038 E | 230 | 345 | 74 | 0 | 66.7 | 0 |  |  | -0.00057 |  |  | 0 |  | 1 | NEWENERGY | AA1-038
314860 | 4E MILL | 138 | 345 | 2 | 0 | 50 | 0 |  |  | -0.00057 |  |  | 0.10478 |  | 1 | ENERGY
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 20.23 |  |  | -0.00057 |  |  | 0.10478 |  | 1 | CAPACITY
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 20.15 |  |  | -0.00057 |  |  | 0.10478 |  | 1 | CAPACITY
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00057 |  |  | 0 |  | 1 | CAPACITY
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 0 |  |  | -0.00058 |  |  | 0 |  | 1 | NEWENERGY | K11
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 30.67 |  |  | -0.00058 |  |  | 0 |  | 1 | CAPACITY | K11
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 443.98 |  |  | -0.00059 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM2
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 440.13 |  |  | -0.00059 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 419.81 |  |  | -0.00059 |  |  | 0.10478 |  | 1 | CAPACITY
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 9.55 |  |  | -0.00059 |  |  | 0.08446 |  | 1 | CAPACITY
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 0 |  |  | -0.00062 |  |  | 0 |  | 1 | NEWENERGY | AC1-075
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 30.75 |  |  | -0.00062 |  |  | 0 |  | 1 | CAPACITY | AC1-075
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 0 |  |  | -0.00062 |  |  | 0 |  | 1 | NEWENERGY | AC1-080
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 23.68 |  |  | -0.00062 |  |  | 0.12623 |  | 1 | CAPACITY
926023 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 10.28 |  |  | -0.00062 |  |  | 0 |  | 1 | CAPACITY | AC1-080
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 68.3 |  |  |  | -0.0006
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 91.93 |  |  | -0.00064 |  |  | 0.07484 |  | 1 | CAPACITY
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 61.42 |  |  | -0.00064 |  |  | 0.07484 |  | 1 | CAPACITY
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.00065 |  |  | 0.08446 |  | 1 | CAPACITY
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 77.88 |  |  | -0.00068 |  |  | 0.07484 |  | 1 | CAPACITY
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 51.78 |  |  | -0.00068 |  |  | 0.07484 |  | 1 | CAPACITY
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 51.38 |  |  | -0.00068 |  |  | 0.07484 |  | 1 | CAPACITY
244012 | 05PINNACLE | 4 | 205 | 1 | 0 | 11 | 0 |  |  | -0.00069 |  |  | 0.10478 |  | 1 | ENERGY
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 42.07 |  |  | -0.00069 |  |  | 0.10478 |  | 1 | CAPACITY
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 0 |  |  | -0.0007 |  |  | 0 |  | 1 | NEWENERGY | AC1-145
926645 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.0007 |  |  | 0 |  | 1 | CAPACITY | AC1-145
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.9 | 40.06 |  |  | -0.00071 |  |  | 0.07484 |  | 1 | CAPACITY
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 1044 |  |  |  | -0.0007
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 154.95 |  |  | -0.00072 |  |  | 0.0316 |  | 1 | CAPACITY
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 152.54 |  |  | -0.00072 |  |  | 0.0316 |  | 1 | CAPACITY
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 97.14 |  |  | -0.00072 |  |  | 0.0316 |  | 1 | CAPACITY
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 59.41 |  |  | -0.00072 |  |  | 0.0316 |  | 1 | CAPACITY
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 57 |  |  | -0.00072 |  |  | 0.0316 |  | 1 | CAPACITY
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 3.21 |  |  | -0.00073 |  |  | 0 |  | 1 | CAPACITY
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | AC1-048
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEW | AC1-048
205910 | AC2-053 E | 0.39 | 227 | 74 | 0 | 12.4 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | AC2-053
205909 | AC2-053 C | 0.39 | 227 | 74 | 0 | 7.6 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEW | AC2-053
208876 | WLAN | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00074 |  |  | 0 |  | 1 | CAPACITY
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 144.51 |  |  | -0.00077 |  |  | 0.10478 |  | 1 | CAPACITY
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | NEWENERGY | AC1-117
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | -0.00077 |  |  | 0.05 |  | 1 | MTX | AA1-100
926461 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | NEW | AC1-117
208769 | SISO | 12.5 | 229 | 2 | 0 | 2.48 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | ENERGY
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 6.42 |  |  | -0.00077 |  |  | 0 |  | 1 | CAPACITY
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.0008 |  |  | 0 |  | 1 | NEWENERGY | AD1-018
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.0008 |  |  | 0 |  | 1 | NEW | AD1-018
235520 | 01WVACO_S38 | 13.8 | 201 | 2 | 0 | 60 | 0 |  |  | -0.00081 |  |  | 0 |  | 1 | NEW
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00081 |  |  | 0.07484 |  | 1 | CAPACITY
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00081 |  |  | 0.07484 |  | 1 | CAPACITY
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 8.59 |  |  | -0.0008 |  |  | 0 |  | 1 | CAPACITY | N47
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 0 |  |  | -0.00082 |  |  | 0 |  | 1 | NEWENERGY | U2-073 A
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 0 |  |  | -0.00082 |  |  | 0 |  | 1 | NEWENERGY | U2-073 B
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 25.9 | 20.79 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY | U2-073 A
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY | U2-073 B
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 3.29 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY
270148 | AE1-018 E | 138 | 205 | 75 | 0 | 2.2 | 0 |  |  | -0.00082 |  |  | 0 |  | 1 | NEWENERGY | AE1-018
270147 | AE1-018 C | 138 | 205 | 75 | 0 | 2.8 | 2.25 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY | AE1-018
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | NEWENERGY | S14
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 11.24 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | S14
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 0 |  |  | -0.00084 |  |  | 0 |  | 1 | NEWENERGY | Y1-006
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 0 |  |  | -0.00085 |  |  | 0 |  | 1 | NEWENERGY | U2-030
913034 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 0 |  |  | -0.00084 |  |  | 0 |  | 1 | NEW | Y1-006
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | -0.00084 |  |  | 0.07484 |  | 1 | ENERGY
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00084 |  |  | 0 |  | 1 | MTX | AD2-205
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 14.1 | 11.32 |  |  | -0.00084 |  |  | 0.07484 |  | 1 | CAPACITY
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.7 | 7.79 |  |  | -0.00084 |  |  | 0 |  | 1 | CAPACITY
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 6.26 |  |  | -0.00085 |  |  | 0 |  | 1 | CAPACITY | U2-030
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00087 |  |  | 0.08446 |  | 1 | CAPACITY
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00087 |  |  | 0.08446 |  | 1 | CAPACITY
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00087 |  |  | 0.08446 |  | 1 | CAPACITY
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00088 |  |  | 0.08446 |  | 1 | CAPACITY
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00088 |  |  | 0.08446 |  | 1 | CAPACITY
242677 | 05INDDRV | 138 | 205 | 64 | 0 | 45 | 36.13 |  |  | -0.00087 |  |  | 0.12623 |  | 1 | CAPACITY
923772 | AB2-011 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00088 |  |  | 0 |  | 1 | NEWENERGY | AB2-011
923762 | AB2-010 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00088 |  |  | 0 |  | 1 | NEWENERGY | AB2-010
923761 | AB2-010 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00088 |  |  | 0 |  | 1 | NEW | AB2-010
923771 | AB2-011 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00088 |  |  | 0 |  | 1 | NEW | AB2-011
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  |  |  | -0.0009
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 489.98 |  |  | -0.00089 |  |  | 0.10478 |  | 1 | CAPACITY
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 127.4 | 102.28 |  |  | -0.00089 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 101.08 |  |  | -0.00089 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 106.7 | 85.67 |  |  | -0.00089 |  |  | 0 |  | 1 | CAPACITY
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 84.78 |  |  | -0.00089 |  |  | 0 |  | 1 | CAPACITY
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  |  |  | -0.0009
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 38 |  |  |  | -0.0009
903052 | W2-094 E | 115 | 227 | 75 | 0 | 1.9 | 0 |  |  | -0.0009 |  |  | 0 |  | 1 | NEWENERGY | W2-094
205911 | 27W2-094 | 115 | 227 | 75 | 0 | 1.1 | 0 |  |  | -0.0009 |  |  | 0 |  | 1 | NEWENERGY | W2-094
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 0 |  |  | -0.00091 |  |  | 0 |  | 1 | NEWENERGY | K28
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 0 |  |  | -0.00091 |  |  | 0 |  | 1 | NEWENERGY | K28
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.4 | 13.97 |  |  | -0.00091 |  |  | 0 |  | 1 | CAPACITY | K28
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 1.3 | 1.04 |  |  | -0.00091 |  |  | 0 |  | 1 | CAPACITY
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 896 |  |  |  | -0.0009
209030 | FRFA O01 | 12.5 | 229 | 2 | 0 | 3.2 | 0 |  |  | -0.00092 |  |  | 0 |  | 1 | NEW
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 0.4 | 0.32 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY | V3-051
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 180.64 |  |  | -0.00093 |  |  | 0.10478 |  | 1 | CAPACITY
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 93.13 |  |  | -0.00093 |  |  | 0.10478 |  | 1 | CAPACITY
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 64.23 |  |  | -0.00093 |  |  | 0.07484 |  | 1 | CAPACITY
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 56.2 |  |  | -0.00094 |  |  | 0.07484 |  | 1 | CAPACITY
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00094 |  |  | 0.07484 |  | 1 | CAPACITY
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00094 |  |  | 0 |  | 1 | CAPACITY
342070 | 2PINE GROVE | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00094 |  |  | 0 |  | 1 | CAPACITY
342442 | 2W GLASGOW | 69 | 320 | 2 | 0 | 1 | 0.8 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | NEWENERGY | M24
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | NEWENERGY | AB1-150
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | -0.00095 |  |  | 0.05 |  | 1 | MTX | M24 BAT
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | M24
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00094 |  |  | 0.07484 |  | 1 | CAPACITY
931011 | AB1-150 C | 138 | 201 | 74 | 0 | 6.7 | 5.38 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | AB1-150
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 244.87 |  |  | -0.00096 |  |  | 0.10478 |  | 1 | CAPACITY
247225 | 05FTHLG2 | 18 | 205 | 57 | 120 | 173.8 | 139.54 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247224 | 05FTHLG1 | 18 | 205 | 57 | 120 | 173.7 | 139.46 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247231 | 05RIVRG2 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247230 | 05RIVRG1 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247232 | 05RIVRG3 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.55 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1067.8 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY | AMG3
918472 | AA1-062 E | 138 | 201 | 74 | 0 | 195 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | AA1-062
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 642.29 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 642.29 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | P59
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | NEWENERGY | U2-061
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00097 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 2
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00097 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
292981 | N-007 E | 138 | 201 | 74 | 0 | 30.4 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | N07
235801 | 01WM_AA1_062 | 138 | 201 | 74 | 0 | 29 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEW | AA1-062
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 109.5 | 87.91 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
920072 | AA2-103 E | 138 | 201 | 76 | -20 | 20 | 0 |  |  | -0.00096 |  |  | 0.05 |  | 1 | MTX | AA2-103
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 60.94 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 60.78 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 60.7 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 60.53 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 72.9 | 58.53 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 72.6 | 58.29 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00096 |  |  | 0.08446 |  | 1 | CAPACITY
925972 | AC1-073 E | 138 | 201 | 74 | 0 | 5.9 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEWENERGY | AC1-073
925971 | AC1-073 C | 138 | 201 | 74 | 0 | 5.8 | 0 |  |  | -0.00096 |  |  | 0 |  | 1 | NEW | AC1-073
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 11.88 |  |  | -0.00097 |  |  | 0.07484 |  | 1 | CAPACITY
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 9.39 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY | P59
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | MTX | AB1-055
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY | K19
235000 | N-007 C | 138 | 201 | 74 | 0 | 7.6 | 6.1 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY | N07
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 5.22 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | U2-061
341329 | 2COLESBURG | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  |  |  | -0.001
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 62.8 |  |  |  | -0.001
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 55 | 44.16 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | -0.001
342031 | 2PACTOLUS | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY
237085 | AD2-192 GEN | 23 | 201 | 57 | 0 | 600 | 0 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | NEW
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1396 | 1120.79 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | GVG2
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1371 | 1100.72 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | GVG1
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | X2-022
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 570.03 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | W2-048
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 52.91 |  |  | -0.00099 |  |  | 0.07484 |  | 1 | CAPACITY
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 19.5 | 15.66 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
341584 | 2GRIFFIN | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY
341200 | 2BROMLEYEK | 69 | 320 | 2 | 0 | 2 | 1.61 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY
293798 | W4-005 E | 0.69 | 222 | 74 | 0 | 305.37 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | W4-005
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1088.67 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | RKG1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1356 | 1088.67 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | MTG1
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1043.71 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | RKG2
274656 | BYRON ;1U | 25 | 222 | 45 | 700 | 1168.5 | 938.14 |  |  | -0.001 |  |  | 0.01494 |  | 1 | CAPACITY
274657 | BYRON ;2U | 25 | 222 | 45 | 700 | 1141.5 | 916.46 |  |  | -0.001 |  |  | 0.01494 |  | 1 | CAPACITY
274663 | QUAD CITI;2U | 18 | 222 | 48 | 150 | 911.7 | 731.97 |  |  | -0.00099 |  |  | 0.01494 |  | 1 | CAPACITY
274662 | QUAD CITI;1U | 18 | 222 | 48 | 150 | 911.1 | 731.48 |  |  | -0.00099 |  |  | 0.01494 |  | 1 | CAPACITY
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | Z2-087
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | S27
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | S28
235587 | 01HARRN3 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
235586 | 01HARRN2 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
235585 | 01HARRN1 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 124 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | ENERGY | L05_CE22
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 443.18 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 437.96 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 409.46 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | P36 1
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | P36 2
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | AC1-089
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O29 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | P26
293516 | O-009 E1 | 0.69 | 222 | 74 | 0 | 82.04 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O09 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | P11 2
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | P11 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | P46
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O35
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 240.86 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O29 2
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | NQ71
293518 | O-009 E3 | 0.57 | 222 | 74 | 0 | 45.89 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O09 3
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 45.5 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | Z1-073
916211 | Z1-072 E | 0.6 | 222 | 74 | 0 | 44.8 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | Z1-072
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O29 3
293517 | O-009 E2 | 0.6 | 222 | 74 | 0 | 41.67 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O09 2
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 144.51 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 136.16 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | NELSON
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 135.12 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | NELSON
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 134.32 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 134.16 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | CORDOVA
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 31.5 |  |  |  | -0.001
919221 | AA1-146 | 345 | 222 | 58 | 0 | 157 | 126.05 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CLIF5
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CLIF1
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF2
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CLIF3
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CLIF4
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CLIF6
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 99.47 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | NELSON
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 98.59 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | NELSON
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | NQ72
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 133.1 | 153 | 133.28 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 129.7 | 149.1 | 129.88 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 128.6 | 147.8 | 128.75 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 67.52 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF1
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF4
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF5
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | CLIF2
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF3
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF6
926103 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 45.76 |  |  | -0.001 |  |  | 0.05 |  | 1 | NEW | AC1-089
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 36.93 |  |  | -0.00099 |  |  | 0.07484 |  | 1 | CAPACITY
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 36.61 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | W4-005
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 28.74 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | S28
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 27.94 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | S27
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | L05_CE22
274889 | BRIGHTSTK;1U | 0.7 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Z2-087
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 17.58 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O29 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 17.58 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | P26
293513 | O-009 C1 | 0.69 | 222 | 74 | 0 | 20.5 | 16.46 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O09 1
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | P11 2
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | P11 1
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 15.58 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | P46
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | P36 2
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | P36 1
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 13.3 | 10.68 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Z1-073
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 9.64 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O29 2
293515 | O-009 C3 | 0.57 | 222 | 74 | 0 | 11.5 | 9.23 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O09 3
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 8.91 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O29 3
293514 | O-009 C2 | 0.6 | 222 | 74 | 0 | 10.4 | 8.35 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O09 2
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 10.3 | 8.27 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O35
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 10 | 8.03 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Z1-072
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.6 | 7.71 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY
295108 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 5.7 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | NQ71
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 5.14 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY
342550 | 4BAVARIAN LF | 138 | 320 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY
295110 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 2.57 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | NQ72
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 949.78 |  |  | -0.00101 |  |  | 0.01494 |  | 1 | CAPACITY
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 926.5 |  |  | -0.00101 |  |  | 0.01494 |  | 1 | CAPACITY
274661 | LASCO STA;2U | 25 | 222 | 49 | 150 | 1135.9 | 911.97 |  |  | -0.00101 |  |  | 0.01494 |  | 1 | CAPACITY
274660 | LASCO STA;1U | 25 | 222 | 49 | 150 | 1131.2 | 908.19 |  |  | -0.00101 |  |  | 0.01494 |  | 1 | CAPACITY
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 200 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | Q57
274658 | DRESDEN ;2U | 18 | 222 | 48 | 150 | 902.5 | 724.58 |  |  | -0.001 |  |  | 0.01494 |  | 1 | CAPACITY
274659 | DRESDEN ;3U | 18 | 222 | 48 | 150 | 895.5 | 718.96 |  |  | -0.001 |  |  | 0.01494 |  | 1 | CAPACITY
930042 | AB1-006 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | AB1-006
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | U3-002 2
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O50
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 159.7 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | S06
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Q01 3
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O22 2
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | P10
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 589.3 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | ZIMM
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | S37
293799 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | S36
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | AA1-018
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Q01 4
253317 | AC1-085 B_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 B
253314 | AC1-085 A_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 A
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O51 1
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O51 2
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | N15
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 470.47 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | ZIMM
927091 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-204
927093 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AC1-204
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 415.88 |  |  | -0.00101 |  |  | 0.10478 |  | 1 | CAPACITY
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 415.88 |  |  | -0.00101 |  |  | 0.10478 |  | 1 | CAPACITY
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
274687 | WILL CNTY;4U | 20 | 222 | 15 | 0 | 510 | 409.46 |  |  | -0.00101 |  |  | 0.10478 |  | 1 | CAPACITY | WILL4
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Q01 21
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 81.6 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | O22 1
247943 | T-127 E | 0.74 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | T127 5
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | T126 2
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | T126 3
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | T127 4
247903 | 05FR-22G E | 0.69 | 205 | 75 | 0 | 78.8 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Q01 22
247900 | 05FR-11G E | 0.6 | 205 | 75 | 0 | 78.3 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Q01 11
930062 | AB1-014 E | 138 | 212 | 75 | 0 | 77.5 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | AB1-014
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 522.66 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Q01 12
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 284.53 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK8
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 263.34 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK7
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-169
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AB1-169
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 294 | 236.04 |  |  | -0.00101 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-079
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 225.6 |  |  | -0.00101 |  |  | 0.10478 |  | 1 | CAPACITY
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AB1-169
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 219 | 175.82 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Z1-079
274708 | KENDALL ;3C | 18 | 222 | 58 | 140 | 184.3 | 147.97 |  |  | -0.00101 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 3
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 146.36 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 1
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 146.36 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 2
274710 | KENDALL ;4C | 18 | 222 | 58 | 138 | 182.3 | 146.36 |  |  | -0.00101 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 4
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 1
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 2
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 132.47 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 131.75 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 130.06 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | -0.001 |  |  | 0.08446 |  | 1 | ENERGY
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 99.72 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | KYG1
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | KYG2
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | KYG4
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | KYG3
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | KYG5
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 97.87 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Kendall 1
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 97.87 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Kendall 2
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 97.87 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Kendall 3
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 97.87 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Kendall 4
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 96.42 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 115.4 | 92.65 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | EQUISTAR MORRIS
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 75.6 | 104 | 83.5 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 72.7 | 101.6 | 81.57 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.001 |  |  | 0.05 |  | 1 | MTX | AA2-123
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.001 |  |  | 0.05 |  | 1 | MTX | Z1-108
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00101 |  |  | 0.05 |  | 1 | MTX | Z1-107
276592 | O-012 C | 138 | 222 | 64 | 0 | 20 | 0 |  |  | -0.00101 |  |  | 0.12623 |  | 1 | ENERGY
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 80.93 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 71.2 | 100.6 | 80.77 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 80.21 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
243415 | 05WWVSTA | 69 | 205 | 61 | 60 | 96 | 77.08 |  |  | -0.00101 |  |  | 0.07484 |  | 1 | CAPACITY
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 65.51 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 81.5 | 65.43 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.8 | 64.87 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 64.31 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 62.14 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
250166 | HLCRST AB114 | 138 | 212 | 75 | 0 | 76 | 61.02 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AB1-014
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | AC1-085 A
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | AC1-085 B
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 58.77 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 58.45 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | KYG1
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | KYG3
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | KYG4
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.001 |  |  | 0.10478 |  | 1 | CAPACITY | KYG2
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | KYG5
251957 | 08MADSN6 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251959 | 08MADSN8 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251955 | 08MADSN4 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251956 | 08MADSN5 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251958 | 08MADSN7 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251952 | 08MADSN1 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251953 | 08MADSN2 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251954 | 08MADSN3 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 56.84 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 55.4 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251828 | CLNTESP1 | 34.5 | 212 | 76 | 0 | 12 | 0 |  |  | -0.001 |  |  | 0.05 |  | 1 | MTX | Z1-080
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 43.03 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.001 |  |  | 0.05 |  | 1 | MTX | Z1-106
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.001 |  |  | 0.05 |  | 1 | MTX | Z1-106
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 40.54 |  |  | -0.00101 |  |  | 0.04435 |  | 1 | CAPACITY | MIDDLETOWN COKE
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | Q57
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O50
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.001 |  |  | 0.07484 |  | 1 | CAPACITY
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.001 |  |  | 0.07484 |  | 1 | CAPACITY
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.001 |  |  | 0.07484 |  | 1 | CAPACITY
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 28.18 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O22 2
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | S36
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | S37
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 42.68 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 42.6 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 42.51 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -0.001 |  |  | 0.05 |  | 1 | MTX | Z1-065
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 24.08 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 23.36 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Q01 4
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | X3-005
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 20.3 | 27.6 | 22.16 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 22 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | N15
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 21.68 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
930041 | AB1-006 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | AB1-006
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 20.79 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | S06
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 20.63 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Q01 11
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 20.07 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O51 2
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O51 1
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 16.22 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | T127 5
274891 | OTTER CRK;1U | 0.69 | 222 | 74 | 0 | 19.5 | 15.66 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AA1-018
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 14.77 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | O22 1
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 12.28 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | T126 3
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | T126 2
276173 | Z2-081 | 138 | 222 | 2 | 0 | 13.3 | 10.68 |  |  | -0.001 |  |  | 0.12623 |  | 1 | CAPACITY
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 10.6 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | U3-002 1
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Q01 22
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Q01 21
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 10.36 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 10.28 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | U3-002 2
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Q01 12
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Q01 3
904211 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 9.71 |  |  | -0.001 |  |  | 0.07484 |  | 1 | CAPACITY
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 9.47 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | T127 4
904201 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 8.51 |  |  | -0.00101 |  |  | 0.07484 |  | 1 | CAPACITY
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 8.19 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | P10
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | MTX | Y3-099
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | MTX | Y3-100
276159 | W4-082 | 138 | 222 | 64 | 0 | 5.8 | 4.66 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.8 | 3.85 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 2.73 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | X3-005
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1402 |  |  |  | -0.001
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | U2-090
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | V3-007
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | AC2-176
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | S71
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 268.96 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
902531 | W2-040 C | 69 | 209 | 75 | 0 | 20 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEW | W2-040
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 80.69 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 64.23 |  |  | -0.00101 |  |  | 0.10478 |  | 1 | CAPACITY
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
902532 | W2-040 E | 69 | 209 | 75 | 0 | 12.4 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | W2-040
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 60 | 48.17 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 48.09 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 47.93 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 46.65 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 46.41 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 37.49 |  |  | -0.00101 |  |  | 0.07484 |  | 1 | CAPACITY
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | U2-090
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | V3-007
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 19.27 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | S71
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 22.91 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
933594 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 13.57 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | AC2-176
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | V4-073
247968 | Z2-115 E | 12 | 205 | 74 | 0 | 1.25 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Z2-115
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.76 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 1 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Z2-115
904721 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | V4-073
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1148 | 921.68 |  |  | -0.00102 |  |  | 0.01494 |  | 1 | CAPACITY
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 814.5 |  |  | -0.00103 |  |  | 0.01494 |  | 1 | CAPACITY
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00103 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-116
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | AA2-116
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 267.35 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | AA2-116
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 201.52 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | X2-052
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 193.49 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00102 |  |  | 0.04435 |  | 1 | CAPACITY | X2-052
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | X2-052
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 162.9 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | AC2-067
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | AC1-165
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | AC1-166
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | AC1-068
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | AC1-069
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | AC1-068
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | AC1-069
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | AC1-165
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | AC1-166
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 21.28 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | AC2-067
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00102 |  |  | 0.12623 |  | 1 | CAPACITY
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 8.03 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY
247969 | Z2-116 E | 138 | 205 | 76 | 0 | 1.3 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | Z2-116
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 4.82 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 3.13 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.8 | 2.25 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 2.09 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | Z2-116
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00104 |  |  | 0.08446 |  | 1 | CAPACITY
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00104 |  |  | 0.08446 |  | 1 | CAPACITY
927184 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -0.00104 |  |  | 0.05 |  | 1 | MTX | AC1-212
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 65.03 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 64.23 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 63.43 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
932312 | AC2-045 E | 69 | 205 | 75 | 0 | 6.2 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEWENERGY | AC2-045
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00104 |  |  | 0.07484 |  | 1 | CAPACITY
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00104 |  |  | 0.07484 |  | 1 | CAPACITY
932311 | AC2-045 C | 69 | 205 | 75 | 0 | 3.8 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEW | AC2-045
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00104 |  |  | 0.12623 |  | 1 | CAPACITY
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | Z2-113
AC1-212 | BATTERY_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | -0.001
247604 | X1-042 | 12 | 205 | 64 | 0 | 3 | 2.41 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 1.85 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | Z2-113
927183 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.53 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | AC1-212
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.5 | 1.2 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 120.8 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEWENERGY | R49
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEWENERGY | T131
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00105 |  |  | 0 |  | 1 | NEWENERGY | V1-011
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEWENERGY | AC1-173
247528 | 05COVRT1 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00104 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 1
247530 | 05COVRT3 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00104 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 3
247529 | 05COVRT2 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00104 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 2
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00105 |  |  | 0.08446 |  | 1 | CAPACITY
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00105 |  |  | 0.08446 |  | 1 | CAPACITY
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 120.19 |  |  | -0.00105 |  |  | 0.08446 |  | 1 | CAPACITY
247533 | 05COVRT6 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | Covert 3
247531 | 05COVRT4 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | Covert 1
247532 | 05COVRT5 | 16.5 | 205 | 58 | 90 | 131.2 | 105.33 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | Covert 2
247521 | T131 | 0.69 | 205 | 74 | 22.4 | 30 | 24.08 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | T131
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 18.39 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | R49
247607 | V1-011 C | 34.5 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY | V1-011
294740 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -0.00105 |  |  | 0 |  | 1 | ENERGY
926865 | AC1-173 C | 0.65 | 205 | 75 | 0 | 9.9 | 7.95 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | AC1-173
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | U2-072
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 94.4 | 0 |  |  | -0.00105 |  |  | 0 |  | 1 | NEWENERGY | R60 3
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00105 |  |  | 0 |  | 1 | NEWENERGY | R60 2
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00105 |  |  | 0 |  | 1 | NEWENERGY | R60 1
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 31.31 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | U2-072
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00105 |  |  | 0 |  | 1 | MTX
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 13.25 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY | R60 3
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY | R60 2
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY | R60 1
247919 | U2-041 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | U2-041
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | AB2-067
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00106 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-067
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00106 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-044
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 292.88 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 318.8 | 255.95 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY | RONCO
247506 | U2-041 C | 345 | 205 | 74 | 0 | 39 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | U2-041
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY | RONCO
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00107 |  |  | 0.04435 |  | 1 | CAPACITY | RONCO
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00106 |  |  | 0.04435 |  | 1 | CAPACITY | WATERFORD
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | V3-028
247549 | V3-028 C | 345 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | CAPACITY | V3-028
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 618.28 |  |  | -0.00107 |  |  | 0.10478 |  | 1 | CAPACITY
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 533.66 |  |  | -0.00107 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-173
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 238.45 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00107 |  |  | 0.04435 |  | 1 | CAPACITY | WASHINGTON
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY
245413 | 05S FULTHA | 69 | 205 | 65 | 0 | 0.85 | 0 |  |  | -0.00108 |  |  | 0 |  | 1 | ENERGY
893022 | V2-006 E | 138 | 205 | 74 | 0 | 130.5 | 0 |  |  | -0.00108 |  |  | 0 |  | 1 | NEWENERGY | V2-006
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 225.4 | 180.96 |  |  | -0.00109 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 0 |  |  | -0.00109 |  |  | 0 |  | 1 | NEWENERGY | U1-059
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.00109 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.00109 |  |  | 0.04435 |  | 1 | CAPACITY | DRESDEN
893021 | V2-006 C | 138 | 205 | 74 | 0 | 19.5 | 0 |  |  | -0.00108 |  |  | 0 |  | 1 | NEWENERGY | V2-006
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 0 |  |  | -0.00109 |  |  | 0 |  | 1 | NEWENERGY | W1-056
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 0 |  |  | -0.00109 |  |  | 0 |  | 1 | NEWENERGY | U1-059
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.93 |  |  | -0.00109 |  |  | 0 |  | 1 | CAPACITY | W1-056
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.0011 |  |  | 0.08446 |  | 1 | CAPACITY
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.0011 |  |  | 0.08446 |  | 1 | CAPACITY
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.66 | 96.07 |  |  | -0.0011 |  |  | 0.08446 |  | 1 | CAPACITY
930262 | AB1-065 E | 34.5 | 201 | 75 | 0 | 6.8 | 0 |  |  | -0.00109 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 17.66 |  |  | -0.0011 |  |  | 0.08446 |  | 1 | CAPACITY
235013 | 01AB1-065 C | 34.5 | 201 | 75 | 0 | 4.1 | 0 |  |  | -0.00109 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 8.83 |  |  | -0.0011 |  |  | 0.10478 |  | 1 | CAPACITY
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00111 |  |  | 0.07484 |  | 1 | CAPACITY
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00111 |  |  | 0.07484 |  | 1 | CAPACITY
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 10.19 |  |  | -0.00112 |  |  | 0.10478 |  | 1 | CAPACITY
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 15.25 |  |  | -0.00112 |  |  | 0.07484 |  | 1 | CAPACITY
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 634.42 |  |  | -0.00113 |  |  | 0.10478 |  | 1 | CAPACITY
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEWENERGY | U4-028
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEWENERGY | U4-029
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00113 |  |  | 0.08446 |  | 1 | CAPACITY
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00113 |  |  | 0.08446 |  | 1 | CAPACITY
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00114 |  |  | 0 |  | 1 | NEW | U4-028
247552 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00114 |  |  | 0 |  | 1 | NEW | U4-029
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEWENERGY | V4-010
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 261.89 |  |  | -0.00115 |  |  | 0 |  | 1 | CAPACITY | OREGON
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 248.73 |  |  | -0.00115 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00115 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00115 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-107
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00115 |  |  | 0 |  | 1 | CAPACITY | OREGON
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00115 |  |  | 0.04435 |  | 1 | CAPACITY | OREGON
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00114 |  |  | 0.08446 |  | 1 | CAPACITY
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00114 |  |  | 0.10478 |  | 1 | CAPACITY
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00114 |  |  | 0.10478 |  | 1 | CAPACITY
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00114 |  |  | 0.08446 |  | 1 | CAPACITY
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 109.19 |  |  | -0.00115 |  |  | 0.10478 |  | 1 | CAPACITY
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEW | V4-010
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 0 |  |  | -0.00114 |  |  | 0 |  | 1 | NEWENERGY
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 10.68 |  |  | -0.00115 |  |  | 0.10478 |  | 1 | CAPACITY
924440 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 389.39 |  |  | -0.00115 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-093
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 364.2 | 292.4 |  |  | -0.00117 |  |  | 0 |  | 1 | CAPACITY | FREMONT
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 170 | 136.49 |  |  | -0.00117 |  |  | 0.04435 |  | 1 | CAPACITY | FREMONT
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 166.4 | 133.6 |  |  | -0.00117 |  |  | 0 |  | 1 | CAPACITY | FREMONT
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 4.41 |  |  | -0.00117 |  |  | 0 |  | 1 | CAPACITY | N32
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | -0.00117 |  |  | 0 |  | 1 | NEW | AB1-069
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00117 |  |  | 0.04435 |  | 1 | NEW | AB1-069
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00117 |  |  | 0 |  | 1 | NEW | AB1-069
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 780.51 |  |  | -0.00118 |  |  | 0.01494 |  | 1 | CAPACITY
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 8.03 |  |  | -0.0012 |  |  | 0 |  | 1 | CAPACITY
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 7.95 |  |  | -0.0012 |  |  | 0 |  | 1 | CAPACITY
936011 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 16.06 |  |  | -0.0012 |  |  | 0.10478 |  | 1 | CAPACITY
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 19.6 | 15.74 |  |  | -0.00122 |  |  | 0.08446 |  | 1 | CAPACITY
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 1.85 |  |  | -0.00122 |  |  | 0 |  | 1 | CAPACITY
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0 |  |  | -0.00123 |  |  | 0 |  | 1 | NEWENERGY | W1-045
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.5 |  |  | -0.00123 |  |  | 0 |  | 1 | CAPACITY
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.13 | 4.12 |  |  | -0.00123 |  |  | 0 |  | 1 | CAPACITY | W1-045
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00125 |  |  | 0.10478 |  | 1 | CAPACITY
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 498.09 |  |  | -0.00125 |  |  | 0.10478 |  | 1 | CAPACITY
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00125 |  |  | 0.10478 |  | 1 | CAPACITY
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 272 | 218.38 |  |  | -0.00125 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00125 |  |  | 0.04435 |  | 1 | CAPACITY | Y2-050
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00125 |  |  | 0 |  | 1 | CAPACITY | Y2-050
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 11.24 |  |  | -0.00125 |  |  | 0.12623 |  | 1 | CAPACITY
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 41.03 |  |  | -0.00127 |  |  | 0.12623 |  | 1 | CAPACITY
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 39.82 |  |  | -0.00127 |  |  | 0.12623 |  | 1 | CAPACITY
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 62.22 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 60.86 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 60.29 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 898.96 |  |  | -0.00128 |  |  | 0.01494 |  | 1 | CAPACITY
237082 | AA2-121 | 345 | 201 | 58 | 0 | 830 | 666.37 |  |  | -0.00129 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-121
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 503.47 |  |  | -0.0013 |  |  | 0.04435 |  | 1 | CAPACITY | AVON LAKE
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 39.5 | 31.71 |  |  | -0.00129 |  |  | 0.08446 |  | 1 | CAPACITY
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 3.21 |  |  | -0.00129 |  |  | 0 |  | 1 | CAPACITY
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00132 |  |  | 0.10478 |  | 1 | CAPACITY
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00132 |  |  | 0.10478 |  | 1 | CAPACITY
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 455.62 |  |  | -0.00132 |  |  | 0.10478 |  | 1 | CAPACITY
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | AA1-123
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 233.87 |  |  | -0.00132 |  |  | 0.10478 |  | 1 | CAPACITY
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.00133 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-123
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | AA1-123
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 81.57 |  |  | -0.00132 |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND
253970 | 15BI2 | 13.8 | 215 | 58 | 60 | 96.2 | 77.24 |  |  | -0.00132 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | Y3-103
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.7 | 39.1 |  |  | -0.00132 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0 |  |  | -0.00132 |  |  | 0 |  | 1 | NEWENERGY | AC2-168
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 28.1 |  |  | -0.00132 |  |  | 0.10478 |  | 1 | CAPACITY
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00133 |  |  | 0.04435 |  | 1 | CAPACITY | Y3-103
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | Y3-103
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 21 | 16.86 |  |  | -0.00132 |  |  | 0.12623 |  | 1 | CAPACITY
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 14.53 |  |  | -0.00132 |  |  | 0.08446 |  | 1 | CAPACITY
933531 | AC2-168 C | 138 | 215 | 75 | 0 | 7.55 | 6.06 |  |  | -0.00132 |  |  | 0 |  | 1 | CAPACITY | AC2-168
253900 | 15BVRVL1 | 22 | 215 | 44 | 843.9 | 970 | 844.97 |  |  | -0.00133 |  |  | 0.01494 |  | 1 | CAPACITY
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 783.39 |  |  | -0.00133 |  |  | 0.01494 |  | 1 | CAPACITY
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 300.6 | 241.34 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY | Z2-028
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00134 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-028
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY | Z2-028
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | -0.00134 |  |  | 0.10478 |  | 1 | ENERGY
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 24.6 | 19.75 |  |  | -0.00134 |  |  | 0.12623 |  | 1 | CAPACITY
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 329.17 |  |  | -0.00136 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00136 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00136 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-044
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 38.7 | 31.07 |  |  | -0.00136 |  |  | 0.08446 |  | 1 | CAPACITY
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 3.21 |  |  | -0.00136 |  |  | 0 |  | 1 | CAPACITY
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 16.46 |  |  | -0.00138 |  |  | 0.12623 |  | 1 | CAPACITY
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 0 |  |  | -0.00138 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
204555 | 27QUEEN ST | 115 | 227 | 74 | 0 | 5 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 0 |  |  | -0.00138 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
239024 | 02NWCAG5 | 16.5 | 202 | 58 | 23 | 141 | 113.2 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
239023 | 02NWCAG4 | 14.4 | 202 | 58 | 20 | 92 | 73.86 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
204638 | 27CAT TRAC | 13.2 | 227 | 58 | 0 | 32.3 | 25.93 |  |  | -0.00141 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
204706 | 27CAT TRC2 | 13.2 | 227 | 58 | 0 | 13.9 | 11.16 |  |  | -0.00141 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 2.01 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 1.37 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | K20
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 261.73 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | T-174
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | T-174
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00141 |  |  | 0.04435 |  | 1 | CAPACITY | T-174
239022 | 02NWCAG3 | 14.4 | 202 | 58 | 20 | 92.3 | 74.11 |  |  | -0.00142 |  |  | 0.04435 |  | 1 | CAPACITY | NEW CASTLE
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 24.08 |  |  | -0.00146 |  |  | 0.10478 |  | 1 | CAPACITY
920571 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 411.86 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | NEW | AA2-161
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.82 |  |  | -0.00151 |  |  | 0 |  | 1 | CAPACITY
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1086.27 |  |  | -0.00152 |  |  | 0.01494 |  | 1 | CAPACITY
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 3.05 |  |  | -0.00159 |  |  | 0 |  | 1 | CAPACITY
213798 | MERCK 3 | 13.8 | 230 | 2 | 13 | 35 | 28.1 |  |  | -0.0016 |  |  | 0 |  | 1 | CAPACITY
213797 | MERCK 2 | 13.8 | 230 | 2 | 4 | 25 | 20.07 |  |  | -0.0016 |  |  | 0 |  | 1 | CAPACITY
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 3.29 |  |  | -0.0016 |  |  | 0 |  | 1 | CAPACITY
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 353.26 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00162 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-076
913142 | Y1-033 E OP1 | 115 | 226 | 74 | 0 | 34.02 | 0 |  |  | -0.00161 |  |  | 0 |  | 1 | NEWENERGY | Y1-033
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 4.01 |  |  | -0.00161 |  |  | 0 |  | 1 | CAPACITY | Y1-033
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 16.55 |  |  | -0.00169 |  |  | 0.07484 |  | 1 | CAPACITY
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 140 | 182.2 | 146.28 |  |  | -0.0017 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 118.7 | 175.2 | 140.66 |  |  | -0.0017 |  |  | 0.04435 |  | 1 | CAPACITY | AE SPRINGDALE
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 118.7 | 172.2 | 138.25 |  |  | -0.0017 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.0017 |  |  | 0.08446 |  | 1 | CAPACITY
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.0017 |  |  | 0.08446 |  | 1 | CAPACITY
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 5.54 |  |  | -0.0018 |  |  | 0 |  | 1 | CAPACITY
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00184 |  |  | 0 |  | 1 | NEWENERGY | K23
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 0 |  |  | -0.00184 |  |  | 0 |  | 1 | NEWENERGY | L13
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 0 |  |  | -0.00184 |  |  | 0 |  | 1 | NEWENERGY | O48
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | -0.00184 |  |  | 0.05 |  | 1 | MTX
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | -0.00184 |  |  | 0.05 |  | 1 | MTX
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 0 |  |  | -0.00184 |  |  | 0 |  | 1 | NEWENERGY | R40
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 5.06 |  |  | -0.00184 |  |  | 0 |  | 1 | CAPACITY | O48
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 4.74 |  |  | -0.00184 |  |  | 0 |  | 1 | CAPACITY | L13
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 5.1 | 4.09 |  |  | -0.00184 |  |  | 0 |  | 1 | CAPACITY | K23
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 682.91 |  |  | -0.00186 |  |  | 0.10478 |  | 1 | CAPACITY | Cone1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 682.43 |  |  | -0.00186 |  |  | 0.10478 |  | 1 | CAPACITY | Cone2
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 400 | 321.14 |  |  | -0.00188 |  |  | 0.04435 |  | 1 | CAPACITY | AD2-114
235620 | 01SBEND2 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
235622 | 01SBEND4 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
235619 | 01SBEND1 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
235621 | 01SBEND3 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 853.3 | 685.08 |  |  | -0.00189 |  |  | 0.10478 |  | 1 | CAPACITY | Keys1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 853.1 | 684.92 |  |  | -0.00189 |  |  | 0.10478 |  | 1 | CAPACITY | Keys2
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 6.1 |  |  | -0.00191 |  |  | 0 |  | 1 | CAPACITY
219123 | BCRR_COGEN | 13.8 | 231 | 64 | 0 | 6 | 0 |  |  | -0.00192 |  |  | 0.12623 |  | 1 | CAPACITY
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.45 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.72 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | K22
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 5.46 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00209 |  |  | 0.12623 |  | 1 | CAPACITY
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 601.34 |  |  | -0.0021 |  |  | 0.10478 |  | 1 | CAPACITY
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 293.93 |  |  | -0.0021 |  |  | 0.10478 |  | 1 | CAPACITY | Bris2
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 248.4 |  |  | -0.0021 |  |  | 0.10478 |  | 1 | CAPACITY | Bris1
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEWENERGY | P60
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 6.82 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | P60
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 68.24 |  |  | -0.00211 |  |  | 0.10478 |  | 1 | CAPACITY
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 42.95 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 42.95 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.02 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 23.2 | 0 |  |  | -0.00215 |  |  | 0 |  | 1 | NEWENERGY | K13
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 2.57 |  |  | -0.00215 |  |  | 0 |  | 1 | CAPACITY | K13
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 10.44 |  |  | -0.00216 |  |  | 0.12623 |  | 1 | CAPACITY
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 24.24 |  |  | -0.00216 |  |  | 0.07484 |  | 1 | CAPACITY
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00217 |  |  | 0.12623 |  | 1 | CAPACITY
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 422.06 |  |  | -0.00219 |  |  | 0.10478 |  | 1 | CAPACITY
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 60 | 0 |  |  | -0.00222 |  |  | 0 |  | 1 | NEWENERGY | R32
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 52 | 0 |  |  | -0.00222 |  |  | 0 |  | 1 | NEWENERGY | O18
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 10.19 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | R32
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | O18
200805 | 26COLVER13 | 13.2 | 226 | 12 | 77 | 110 | 88.31 |  |  | -0.00223 |  |  | 0.10478 |  | 1 | CAPACITY
903644 | W3-099 E OP1 | 230 | 226 | 74 | 0 | 87 | 0 |  |  | -0.00224 |  |  | 0 |  | 1 | NEWENERGY | W3-099
201144 | W3-099 C OP1 | 230 | 226 | 74 | 0 | 13 | 0 |  |  | -0.00224 |  |  | 0 |  | 1 | NEW | W3-099
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 497.77 |  |  | -0.00226 |  |  | 0.10478 |  | 1 | CAPACITY
200809 | 26SITHE | 138 | 226 | 15 | 0 | 36 | 28.9 |  |  | -0.00226 |  |  | 0.10478 |  | 1 | CAPACITY
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 900.89 |  |  | -0.00229 |  |  | 0.01494 |  | 1 | CAPACITY
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 0 |  |  | -0.0023 |  |  | 0 |  | 1 | NEWENERGY | V3-030
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 4.25 |  |  | -0.0023 |  |  | 0 |  | 1 | CAPACITY | V3-030
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 48 | 0 |  |  | -0.00235 |  |  | 0 |  | 1 | NEWENERGY | Q53
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 5.14 |  |  | -0.00235 |  |  | 0 |  | 1 | CAPACITY | Q53
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 0 |  |  | -0.00238 |  |  | 0 |  | 1 | NEWENERGY | N39
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00238 |  |  | 0 |  | 1 | NEWENERGY | O38
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00238 |  |  | 0 |  | 1 | CAPACITY | N39
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.4 | 7.55 |  |  | -0.00238 |  |  | 0 |  | 1 | CAPACITY | O38
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 521.86 |  |  | -0.00241 |  |  | 0.10478 |  | 1 | CAPACITY
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 492.95 |  |  | -0.00241 |  |  | 0.10478 |  | 1 | CAPACITY
208947 | WSHO CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00242 |  |  | 0.08446 |  | 1 | CAPACITY
208348 | EELI | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00255 |  |  | 0 |  | 1 | CAPACITY
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 57 | 45.76 |  |  | -0.00257 |  |  | 0.08446 |  | 1 | CAPACITY
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | -0.00259 |  |  | 0 |  | 1 | ENERGY
208942 | HARR CT | 12.5 | 229 | 55 | 0 | 42 | 33.72 |  |  | -0.0026 |  |  | 0.08446 |  | 1 | CAPACITY
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 9.64 |  |  | -0.0026 |  |  | 0.12623 |  | 1 | CAPACITY
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 8.19 |  |  | -0.0026 |  |  | 0.10478 |  | 1 | CAPACITY
210022 | LING 2 | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00259 |  |  | 0 |  | 1 | CAPACITY
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 40 | 0 |  |  | -0.00262 |  |  | 0 |  | 1 | NEWENERGY | Q36
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 24.08 |  |  | -0.00261 |  |  | 0.10478 |  | 1 | CAPACITY
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 6.66 |  |  | -0.00262 |  |  | 0 |  | 1 | CAPACITY | Q36
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 16.86 |  |  | -0.00263 |  |  | 0.07484 |  | 1 | CAPACITY
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 187.87 |  |  | -0.00272 |  |  | 0.0316 |  | 1 | CAPACITY
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 177.43 |  |  | -0.00272 |  |  | 0.0316 |  | 1 | CAPACITY
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 26.13 |  |  | -0.00272 |  |  | 0.07484 |  | 1 | CAPACITY
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | -0.00275 |  |  | 0.12623 |  | 1 | ENERGY
208697 | PRIN B34 | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00275 |  |  | 0 |  | 1 | CAPACITY
208885 | WNHO | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00275 |  |  | 0 |  | 1 | CAPACITY
210319 | WCAR 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00277 |  |  | 0 |  | 1 | CAPACITY
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4.82 |  |  | -0.00288 |  |  | 0 |  | 1 | CAPACITY
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 33.96 |  |  | -0.00292 |  |  | 0.10478 |  | 1 | CAPACITY
200722 | 26SHAWVL 2 | 18 | 226 | 12 | 62 | 124.7 | 100.12 |  |  | -0.00297 |  |  | 0.10478 |  | 1 | CAPACITY
200715 | 26SHAWVL 1 | 18 | 226 | 12 | 62 | 122 | 97.95 |  |  | -0.00297 |  |  | 0.10478 |  | 1 | CAPACITY
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | -0.00303 |  |  | 0 |  | 1 | MTX | AC1-025
200666 | 26SHAWVL 4 | 22 | 226 | 12 | 120 | 171 | 137.29 |  |  | -0.00305 |  |  | 0.10478 |  | 1 | CAPACITY
236828 | 01GRAYMONT | 46 | 201 | 2 | 0 | 4 | 0 |  |  | -0.00304 |  |  | 0 |  | 1 | ENERGY
200665 | 26SHAWVL 3 | 22 | 226 | 12 | 120 | 174.2 | 139.86 |  |  | -0.00305 |  |  | 0.10478 |  | 1 | CAPACITY
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | -0.00311 |  |  | 0 |  | 1 | ENERGY
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.61 |  |  | -0.00311 |  |  | 0 |  | 1 | CAPACITY
204664 | 27AES GEN3 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00316 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204662 | 27AES GEN1 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00316 |  |  | 0.04435 |  | 1 | CAPACITY | IRONWOOD
204663 | 27AES GEN2 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00316 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | -0.00336 |  |  | 0 |  | 1 | ENERGY
208580 | MGTN 2 | 12.5 | 229 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00336 |  |  | 0 |  | 1 | CAPACITY
922932 | AB1-082 OP | 46 | 201 | 55 | 0 | 19.9 | 0 |  |  | -0.00344 |  |  | 0.08446 |  | 1 | NEW
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY | Z1-069
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY | Z1-069
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 389.39 |  |  | -0.00434 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-115
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 30.1 | 24.17 |  |  | -0.00439 |  |  | 0.08446 |  | 1 | CAPACITY
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 4.82 |  |  | -0.00444 |  |  | 0 |  | 1 | CAPACITY
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 6 | 4.82 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 19 | 15.25 |  |  | -0.00465 |  |  | 0.08446 |  | 1 | CAPACITY
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 0 |  |  | -0.00481 |  |  | 0 |  | 1 | NEWENERGY | P47
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.8 | 12.69 |  |  | -0.00481 |  |  | 0 |  | 1 | CAPACITY | P47
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00481 |  |  | 0 |  | 1 | NEWENERGY | K02
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 64.23 |  |  | -0.00483 |  |  | 0.10478 |  | 1 | CAPACITY
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 152.86 |  |  | -0.00491 |  |  | 0.04435 |  | 1 | CAPACITY | ONTELAUNEE
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 152.86 |  |  | -0.00491 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 139.94 |  |  | -0.00491 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 17.18 |  |  | -0.00502 |  |  | 0.12623 |  | 1 | CAPACITY
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 16.86 |  |  | -0.00502 |  |  | 0.12623 |  | 1 | CAPACITY
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 16.86 |  |  | -0.00505 |  |  | 0.12623 |  | 1 | CAPACITY
920341 | AA2-132 | 34.5 | 226 | 55 | 0 | 19.9 | 0 |  |  | -0.00545 |  |  | 0.08446 |  | 1 | NEW
919201 | AA1-144 OP | 230 | 226 | 58 | 0 | 163 | 130.87 |  |  | -0.00567 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-144
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00573 |  |  | 0.04435 |  | 1 | CAPACITY | X1-109
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00573 |  |  | 0 |  | 1 | CAPACITY | X1-109
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.04 |  |  | -0.00576 |  |  | 0 |  | 1 | CAPACITY
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 317.93 |  |  | -0.00619 |  |  | 0 |  | 1 | CAPACITY | Hummel
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 194.29 |  |  | -0.00619 |  |  | 0 |  | 1 | CAPACITY | Hummel
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.00619 |  |  | 0.04435 |  | 1 | CAPACITY | Hummel
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.00619 |  |  | 0 |  | 1 | CAPACITY | Hummel
203932 | AA2-133 GEN | 13.8 | 226 | 55 | 0 | 19.89 | 0 |  |  | -0.00618 |  |  | 0.08446 |  | 1 | NEW
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 0 |  |  | -0.00669 |  |  | 0 |  | 1 | NEWENERGY | P28
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | -0.00669 |  |  | 0.10478 |  | 1 | NEW
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 47.37 |  |  | -0.00669 |  |  | 0.10478 |  | 1 | CAPACITY
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00669 |  |  | 0 |  | 1 | CAPACITY | P28
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 17.18 |  |  | -0.00669 |  |  | 0.12623 |  | 1 | CAPACITY
209018 | SUNBIPCT | 12.5 | 229 | 55 | 0 | 36 | 28.9 |  |  | -0.00697 |  |  | 0.08446 |  | 1 | CAPACITY
212345 | PENS | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00697 |  |  | 0 |  | 1 | CAPACITY
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0 |  |  | -0.00701 |  |  | 0 |  | 1 | NEWENERGY | W1-121 Z
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00701 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00701 |  |  | 0 |  | 1 | CAPACITY | W1-121 Z
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.46 |  |  | -0.00701 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00713 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00713 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00713 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00713 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00713 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200044 | BETH CT1 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00713 |  |  | 0.04435 |  | 1 | CAPACITY | BETH1234
200048 | BETH CT5 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00713 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
212435 | SMIL | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00723 |  |  | 0 |  | 1 | CAPACITY
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 11.24 |  |  | -0.00729 |  |  | 0.08446 |  | 1 | CAPACITY
208948 | WILL CT | 12.5 | 229 | 55 | 0 | 27.4 | 22 |  |  | -0.00734 |  |  | 0.08446 |  | 1 | CAPACITY
212005 | ALWD | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00734 |  |  | 0 |  | 1 | CAPACITY
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00743 |  |  | 0.04435 |  | 1 | CAPACITY | MOXIE PATRIOT
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00743 |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 18.3 | 14.69 |  |  | -0.00751 |  |  | 0.12623 |  | 1 | CAPACITY
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 608.97 |  |  | -0.00753 |  |  | 0.10478 |  | 1 | CAPACITY
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 608.49 |  |  | -0.00753 |  |  | 0.10478 |  | 1 | CAPACITY
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 34.28 |  |  | -0.00759 |  |  | 0.10478 |  | 1 | CAPACITY
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 26.09 |  |  | -0.00759 |  |  | 0.10478 |  | 1 | CAPACITY
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 6.42 |  |  | -0.00759 |  |  | 0 |  | 1 | CAPACITY
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 4.9 |  |  | -0.00759 |  |  | 0 |  | 1 | CAPACITY
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1090.36 |  |  | -0.0079 |  |  | 0.01494 |  | 1 | CAPACITY
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 69.05 |  |  | -0.0079 |  |  | 0.10478 |  | 1 | CAPACITY
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 65.83 |  |  | -0.0079 |  |  | 0.10478 |  | 1 | CAPACITY
208941 | FISH CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.0079 |  |  | 0.08446 |  | 1 | CAPACITY
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.4 | 9.15 |  |  | -0.0079 |  |  | 0 |  | 1 | CAPACITY | Q27
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.81 |  |  | -0.0079 |  |  | 0 |  | 1 | CAPACITY | N14
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00799 |  |  | 0 |  | 1 | CAPACITY | Z2-046
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00799 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-046
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1091.76 |  |  | -0.00829 |  |  | 0.01494 |  | 1 | CAPACITY
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 35.57 |  |  | -0.00855 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 23.44 |  |  | -0.00855 |  |  | 0.04435 |  | 1 | CAPACITY | HUNLOCK
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 39.1 |  |  | -0.00856 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 38.86 |  |  | -0.00856 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
211375 | BEAC | 69 | 229 | 2 | 0 | 20 | 0 |  |  | -0.00859 |  |  | 0.10478 |  | 1 | ENERGY
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 47.77 |  |  | -0.00859 |  |  | 0.08446 |  | 1 | CAPACITY
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 47.21 |  |  | -0.00859 |  |  | 0.08446 |  | 1 | CAPACITY
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 23.76 |  |  | -0.00859 |  |  | 0.08446 |  | 1 | CAPACITY
208943 | HARW CT | 12.5 | 229 | 55 | 0 | 27.2 | 21.84 |  |  | -0.00859 |  |  | 0.08446 |  | 1 | CAPACITY
211591 | HARW | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00859 |  |  | 0 |  | 1 | CAPACITY
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.00865 |  |  | 0.05 |  | 1 | MTX | AB1-182
208944 | JENK CT | 12.5 | 229 | 55 | 0 | 28 | 22.48 |  |  | -0.00865 |  |  | 0.08446 |  | 1 | CAPACITY
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.65 |  |  | -0.00865 |  |  | 0 |  | 1 | CAPACITY | L18
211374 | AVOC | 12.5 | 229 | 2 | 0 | 17.4 | 13.97 |  |  | -0.00884 |  |  | 0 |  | 1 | CAPACITY
208940 | ALLE CT | 12.5 | 229 | 55 | 0 | 56 | 44.96 |  |  | -0.00904 |  |  | 0.08446 |  | 1 | CAPACITY
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00905 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00914 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G2
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00914 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G1
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00914 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G3
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | -0.00914 |  |  | 0.05 |  | 1 | MTX | Z2-107
209009 | PEIP 2 | 13.8 | 229 | 56 | 0 | 43.7 | 35.08 |  |  | -0.00914 |  |  | 0.08446 |  | 1 | CAPACITY
209010 | PEIP 1 | 13.8 | 229 | 29 | 0 | 26.7 | 21.43 |  |  | -0.00914 |  |  | 0.10478 |  | 1 | CAPACITY
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 7.23 |  |  | -0.00914 |  |  | 0 |  | 1 | CAPACITY | K21
209003 | KSTN IPP | 13.8 | 229 | 65 | 0 | 4.9 | 3.93 |  |  | -0.00914 |  |  | 0 |  | 1 | CAPACITY
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 0 |  |  | -0.00916 |  |  | 0 |  | 1 | NEWENERGY | AC1-071
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 7.02 |  |  | -0.00916 |  |  | 0 |  | 1 | NEW | AC1-071
209007 | NOEN IPP | 13.8 | 229 | 12 | 80 | 111.4 | 89.44 |  |  | -0.00919 |  |  | 0.10478 |  | 1 | CAPACITY
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 0 |  |  | -0.00929 |  |  | 0 |  | 1 | NEWENERGY | AA2-017
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 0 |  |  | -0.00929 |  |  | 0 |  | 1 | NEW | AA2-017
211065 | PSPA IPP | 13.8 | 229 | 75 | 0 | 18.4 | 6.74 |  |  | -0.00952 |  |  | 0 |  | 1 | NEWENERGY | U4-014
208946 | MACR CT | 12.5 | 229 | 55 | 0 | 72 | 57.81 |  |  | -0.01014 |  |  | 0.08446 |  | 1 | CAPACITY
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.33 |  |  | -0.01026 |  |  | 0 |  | 1 | CAPACITY
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 152 | 122.03 |  |  | -0.01041 |  |  | 0.08446 |  | 1 | CAPACITY
206341 | 28GIL 8 | 13.8 | 228 | 58 | 69.9 | 90 | 72.26 |  |  | -0.01041 |  |  | 0.04435 |  | 1 | CAPACITY | GILBERT
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 87 | 100 | 87.11 |  |  | -0.01041 |  |  | 0 |  | 1 | CAPACITY | GILBERT
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 85.3 | 98 | 85.37 |  |  | -0.01041 |  |  | 0 |  | 1 | CAPACITY | GILBERT
208920 | WLPK | 12.5 | 229 | 60 | 0 | 40.9 | 32.84 |  |  | -0.01055 |  |  | 0.07484 |  | 1 | CAPACITY
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.01062 |  |  | 0.10478 |  | 1 | CAPACITY
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.01062 |  |  | 0.10478 |  | 1 | CAPACITY
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 192.53 |  |  | -0.01062 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 160.57 |  |  | -0.01062 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 160.57 |  |  | -0.01062 |  |  | 0.04435 |  | 1 | CAPACITY | LOWER MT BETHEL
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01092 |  |  | 0 |  | 1 | NEWENERGY | W4-097
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.01092 |  |  | 0 |  | 1 | CAPACITY | W4-097
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0 |  |  | -0.01097 |  |  | 0 |  | 1 | NEWENERGY | AD2-070
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 2.81 |  |  | -0.01097 |  |  | 0 |  | 1 | CAPACITY | AD2-070
207402 | 28AA2-082 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.01101 |  |  | 0.05 |  | 1 | MTX | AA2-082
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.01107 |  |  | 0 |  | 1 | NEWENERGY | W4-073
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.01107 |  |  | 0 |  | 1 | CAPACITY
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01108 |  |  | 0 |  | 1 | NEWENERGY | W1-127
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0 |  |  | -0.01108 |  |  | 0 |  | 1 | NEWENERGY | U2-059
925462 | AC1-018 E | 34.5 | 228 | 75 | 0 | 0.9 | 0 |  |  | -0.01108 |  |  | 0 |  | 1 | NEWENERGY | AC1-018
925461 | AC1-018 C | 34.5 | 228 | 75 | 0 | 0.5 | 0 |  |  | -0.01108 |  |  | 0 |  | 1 | NEW | AC1-018
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01108 |  |  | 0 |  | 1 | CAPACITY | W1-127
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.01108 |  |  | 0 |  | 1 | CAPACITY | U2-059
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 4 | 3.21 |  |  | -0.01136 |  |  | 0 |  | 1 | CAPACITY
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 120 |  |  |  | -0.0116
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 20 | 16.06 |  |  | -0.01162 |  |  | 0.08446 |  | 1 | CAPACITY
218780 | PRINCENTON_U | 26 | 231 | 2 | 0 | 31.56 | 25.34 |  |  | -0.01179 |  |  | 0 |  | 1 | CAPACITY
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0 |  |  | -0.01179 |  |  | 0 |  | 1 | NEWENERGY | Z1-096
219622 | TRENT_BIOGAS | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.01179 |  |  | 0 |  | 1 | CAPACITY
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 2.39 |  |  | -0.01179 |  |  | 0 |  | 1 | CAPACITY | Z1-096
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.01181 |  |  | 0 |  | 1 | NEWENERGY | W3-077
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 5.7 | 4.58 |  |  | -0.01181 |  |  | 0 |  | 1 | CAPACITY | W3-077
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.01181 |  |  | 0 |  | 1 | CAPACITY | W2-091
204651 | 27PORT CT | 13.8 | 227 | 56 | 4 | 35 | 28.1 |  |  | -0.01185 |  |  | 0.08446 |  | 1 | CAPACITY
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.01205 |  |  | 0 |  | 1 | NEWENERGY | W2-016
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.01205 |  |  | 0 |  | 1 | CAPACITY | W2-016
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 134 | 107.58 |  |  | -0.01215 |  |  | 0.08446 |  | 1 | CAPACITY
206747 | 28DSM_X3-029 | 34.5 | 228 | 29 | 0 | 11.15 | 0 |  |  | -0.0126 |  |  | 0.10478 |  | 1 | ENERGY
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | -0.0126 |  |  | 0.08446 |  | 1 | ENERGY
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01265 |  |  | 0 |  | 1 | NEWENERGY | Y2-018
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.01279 |  |  | 0.0316 |  | 1 | CAPACITY
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.01279 |  |  | 0.0316 |  | 1 | CAPACITY
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.01279 |  |  | 0.0316 |  | 1 | CAPACITY
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 0 |  |  | -0.0129 |  |  | 0 |  | 1 | NEWENERGY | W3-044
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 6.1 |  |  | -0.0129 |  |  | 0 |  | 1 | CAPACITY | W3-044
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.01316 |  |  | 0 |  | 1 | NEWENERGY | W4-046
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 1.93 |  |  | -0.01316 |  |  | 0 |  | 1 | CAPACITY | W4-046
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.01348 |  |  | 0 |  | 1 | NEWENERGY | V4-001
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.61 |  |  | -0.01348 |  |  | 0 |  | 1 | CAPACITY | V4-001
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 35.24 |  |  | -0.01371 |  |  | 0.10478 |  | 1 | CAPACITY
933322 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | -0.01386 |  |  | 0 |  | 1 | MTX | AC2-144
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0 |  |  | -0.01438 |  |  | 0 |  | 1 | NEWENERGY | V2-009 3
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0 |  |  | -0.01438 |  |  | 0 |  | 1 | NEWENERGY | V2-009 4
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 1.92 |  |  | -0.01438 |  |  | 0 |  | 1 | CAPACITY | V2-009 3
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 1.15 |  |  | -0.01438 |  |  | 0 |  | 1 | CAPACITY | V2-009 4
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0 |  |  | -0.01483 |  |  | 0 |  | 1 | NEWENERGY | W3-124
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0 |  |  | -0.01483 |  |  | 0 |  | 1 | NEWENERGY | V2-009 1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.87 |  |  | -0.01483 |  |  | 0 |  | 1 | CAPACITY | W3-124
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.01483 |  |  | 0 |  | 1 | CAPACITY | V2-009 1
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.01485 |  |  | 0 |  | 1 | NEWENERGY | V3-024
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0 |  |  | -0.01485 |  |  | 0 |  | 1 | NEWENERGY | V2-009 2
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0 |  |  | -0.01485 |  |  | 0 |  | 1 | NEWENERGY | X2-088
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.01485 |  |  | 0 |  | 1 | CAPACITY | V3-024
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 1.52 |  |  | -0.01485 |  |  | 0 |  | 1 | CAPACITY | V2-009 2
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.72 |  |  | -0.01485 |  |  | 0 |  | 1 | CAPACITY | X2-088
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0 |  |  | -0.01491 |  |  | 0 |  | 1 | NEWENERGY | W2-050
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01492 |  |  | 0 |  | 1 | NEWENERGY | W4-064
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.01492 |  |  | 0 |  | 1 | CAPACITY | W4-064
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.01512 |  |  | 0 |  | 1 | NEWENERGY | X1-012
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 2.97 |  |  | -0.01512 |  |  | 0 |  | 1 | CAPACITY | X1-012
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | -0.01516 |  |  | 0.05 |  | 1 | MTX | AA2-061
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | -0.01516 |  |  | 0.05 |  | 1 | MTX | AA2-060
206742 | 28SUX_V3-011 | 34.5 | 228 | 64 | 0 | 2 | 0 |  |  | -0.01518 |  |  | 0 |  | 1 | CAPACITY
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0 |  |  | -0.01522 |  |  | 0 |  | 1 | NEWENERGY | W3-106
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0 |  |  | -0.01526 |  |  | 0 |  | 1 | NEWENERGY | V3-070
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0 |  |  | -0.01526 |  |  | 0 |  | 1 | NEWENERGY | W3-110
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.01526 |  |  | 0 |  | 1 | CAPACITY | V3-070
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 2.29 |  |  | -0.01526 |  |  | 0 |  | 1 | CAPACITY | W3-110
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 2.99 |  |  | -0.01539 |  |  | 0 |  | 1 | CAPACITY | Y1-020
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0 |  |  | -0.01544 |  |  | 0 |  | 1 | NEWENERGY | W2-080
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.01544 |  |  | 0 |  | 1 | CAPACITY | W2-080
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0 |  |  | -0.01548 |  |  | 0 |  | 1 | NEWENERGY | AC2-175
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0 |  |  | -0.01548 |  |  | 0 |  | 1 | NEWENERGY | AE1-081
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.77 |  |  | -0.01548 |  |  | 0 |  | 1 | CAPACITY | AE1-081
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0 |  |  | -0.01559 |  |  | 0 |  | 1 | NEWENERGY | X2-075
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 1.83 |  |  | -0.01559 |  |  | 0 |  | 1 | CAPACITY | X2-075
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | W3-029
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | W3-003
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEW | AE1-156
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | AE1-156
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | W1-132
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | W2-061
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | V4-070
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.01562 |  |  | 0 |  | 1 | NEWENERGY | V4-069
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.01562 |  |  | 0 |  | 1 | CAPACITY | W3-029
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01562 |  |  | 0 |  | 1 | CAPACITY | V4-069
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01562 |  |  | 0 |  | 1 | CAPACITY | V4-070
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.01562 |  |  | 0 |  | 1 | CAPACITY | W2-061
218455 | CINNBAY_CGEN | 26.4 | 231 | 75 | 0 | 9 | 0 |  |  | -0.01636 |  |  | 0 |  | 1 | NEWENERGY
924132 | NEWROADSO E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.01636 |  |  | 0 |  | 1 | NEWENERGY | AB2-057
217198 | EDGEBORO_1E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.01636 |  |  | 0 |  | 1 | NEWENERGY | V3-058
217199 | EDGEBORO_2E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.01636 |  |  | 0 |  | 1 | NEWENERGY | V3-059
924131 | NEWROADSO C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.01636 |  |  | 0 |  | 1 | CAPACITY | AB2-057
218781 | BRIS_MYERS | 26 | 231 | 2 | 0 | 3 | 2.41 |  |  | -0.01636 |  |  | 0 |  | 1 | CAPACITY
933332 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | -0.01694 |  |  | 0 |  | 1 | MTX | AC2-145
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0 |  |  | -0.01703 |  |  | 0 |  | 1 | NEWENERGY | X2-089
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.61 |  |  | -0.01703 |  |  | 0 |  | 1 | CAPACITY | X2-089
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 538.72 |  |  | -0.01704 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-116
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0 |  |  | -0.01704 |  |  | 0 |  | 1 | NEWENERGY | AB1-139
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0 |  |  | -0.01704 |  |  | 0 |  | 1 | NEWENERGY | AE1-041
930901 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 2.01 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY | AB1-139
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0 |  |  | -0.01704 |  |  | 0 |  | 1 | NEWENERGY | W2-052
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY | W2-052
938281 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY | AE1-041
219001 | SEWAREN7GT | 25 | 231 | 58 | 101.5 | 324.6 | 260.61 |  |  | -0.01712 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-089
219002 | SEWAREN7ST | 18 | 231 | 58 | 96.3 | 216.4 | 173.74 |  |  | -0.01712 |  |  | 0 |  | 1 | CAPACITY | Z2-089
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | -0.01712 |  |  | 0 |  | 1 | ENERGY | Z2-089
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | -0.01712 |  |  | 0.04435 |  | 1 | ENERGY | Z2-089
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 309 | 248.08 |  |  | -0.01742 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.01742 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.01742 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.01742 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC2
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | -0.01742 |  |  | 0.08446 |  | 1 | CAPACITY
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | -0.01742 |  |  | 0.08446 |  | 1 | CAPACITY
218344 | TOSCO_G6 | 18 | 231 | 2 | 90 | 180 | 144.51 |  |  | -0.01746 |  |  | 0.04435 |  | 1 | CAPACITY | TOSCO
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  |  |  | -0.0175
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 309 | 248.08 |  |  | -0.01754 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 180 | 144.51 |  |  | -0.01754 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -0.01754 |  |  | 0.08446 |  | 1 | CAPACITY
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -0.01754 |  |  | 0.08446 |  | 1 | CAPACITY
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 30.03 |  |  | -0.01754 |  |  | 0.10478 |  | 1 | CAPACITY
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0 |  |  | -0.01763 |  |  | 0 |  | 1 | NEWENERGY | W1-101
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.43 |  |  | -0.01763 |  |  | 0 |  | 1 | CAPACITY | W1-101
900003 | DEANS E | 500 | 231 | 74 | 0 | 1779.4 | 0 |  |  | -0.01763 |  |  | 0 |  | 1 | NEWENERGY | OSW_DEANS
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 5.3 |  |  | -0.01763 |  |  | 0 |  | 1 | CAPACITY
200006 | DEANS C | 500 | 231 | 74 | 0 | 762.6 | 762.6 |  |  | -0.01763 |  |  | 0 |  | 1 | CAPACITY | OSW_DEANS
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0 |  |  | -0.01771 |  |  | 0 |  | 1 | NEWENERGY | V3-067
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0 |  |  | -0.01771 |  |  | 0 |  | 1 | NEWENERGY | V3-068
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.23 |  |  | -0.01771 |  |  | 0 |  | 1 | CAPACITY | V3-067
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.01771 |  |  | 0 |  | 1 | CAPACITY | V3-068
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 169.24 |  |  | -0.01773 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.01773 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.01773 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.01773 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.01773 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.01772 |  |  | 0.10478 |  | 1 | CAPACITY
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.01772 |  |  | 0.10478 |  | 1 | CAPACITY
217825 | UMD_NJ | 26 | 231 | 2 | 0 | 10.5 | 8.43 |  |  | -0.01773 |  |  | 0 |  | 1 | CAPACITY
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 202.48 |  |  | -0.01776 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 143.63 |  |  | -0.01776 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN2
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 143.63 |  |  | -0.01776 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
218092 | PRIMEENG_G | 26.4 | 231 | 29 | 10 | 70.3 | 56.44 |  |  | -0.01776 |  |  | 0.10478 |  | 1 | CAPACITY
217850 | MONTCLAIR_U | 26 | 231 | 2 | 0 | 10.6 | 8.51 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY
934302 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.01776 |  |  | 0 |  | 1 | NEWENERGY | AD1-054
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.74 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0 |  |  | -0.01776 |  |  | 0 |  | 1 | NEWENERGY | X1-072
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.01776 |  |  | 0 |  | 1 | CAPACITY | X1-072
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 207.94 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.01777 |  |  | 0.04435 |  | 1 | CAPACITY | DELANCY STREET
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 76.11 |  |  | -0.01777 |  |  | 0.08446 |  | 1 | CAPACITY
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.01777 |  |  | 0.08446 |  | 1 | CAPACITY
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.01777 |  |  | 0.08446 |  | 1 | CAPACITY
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.01777 |  |  | 0.08446 |  | 1 | CAPACITY
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.01777 |  |  | 0.08446 |  | 1 | CAPACITY
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 70.56 |  |  | -0.01777 |  |  | 0.08446 |  | 1 | CAPACITY
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.01777 |  |  | 0.04435 |  | 1 | CAPACITY | NEWARK BAY
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 27.46 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.01778 |  |  | 0 |  | 1 | NEWENERGY | V2-025
217831 | PB_NUTCLIF | 26 | 231 | 2 | 0 | 10.7 | 8.59 |  |  | -0.01778 |  |  | 0 |  | 1 | CAPACITY
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.85 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0 |  |  | -0.01777 |  |  | 0 |  | 1 | NEWENERGY | V3-065
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0 |  |  | -0.01777 |  |  | 0 |  | 1 | NEWENERGY | V3-066
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.17 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY | V3-065
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.01777 |  |  | 0 |  | 1 | CAPACITY | V3-066
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0 |  |  | -0.01779 |  |  | 0 |  | 1 | NEWENERGY | W4-059
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.18 |  |  | -0.01779 |  |  | 0 |  | 1 | CAPACITY | W4-059
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0 |  |  | -0.0178 |  |  | 0 |  | 1 | NEWENERGY | AB1-021
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.0178 |  |  | 0 |  | 1 | CAPACITY | AB1-021
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0 |  |  | -0.01802 |  |  | 0 |  | 1 | NEWENERGY | X2-087
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.01802 |  |  | 0 |  | 1 | CAPACITY | X2-087
937512 | AD2-210 E | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | -0.01819 |  |  | 0 |  | 1 | MTX | AD2-210
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.01834 |  |  | 0 |  | 1 | NEWENERGY | X1-095
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01834 |  |  | 0 |  | 1 | CAPACITY | X1-095
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0 |  |  | -0.02089 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0 |  |  | -0.02089 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
932032 | AC2-009 E | 13.2 | 231 | 75 | -0.5 | 0.49 | 0 |  |  | -0.02089 |  |  | 0 |  | 1 | NEWENERGY | AC2-009
932031 | AC2-009 C | 13.2 | 231 | 75 | -0.1 | 0.1 | 0 |  |  | -0.02089 |  |  | 0 |  | 1 | NEW | AC2-009
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.02089 |  |  | 0 |  | 1 | CAPACITY | AA2-058
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0 |  |  | -0.0223 |  |  | 0 |  | 1 | NEWENERGY | W2-036
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.0223 |  |  | 0 |  | 1 | CAPACITY | W2-036
219650 | TRENT_COLLEG | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.02321 |  |  | 0 |  | 1 | CAPACITY
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0 |  |  | -0.02321 |  |  | 0 |  | 1 | NEWENERGY | W4-058
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.22 |  |  | -0.02321 |  |  | 0 |  | 1 | CAPACITY | W4-058
900004 | SMITHBRG E | 500 | 228 | 74 | 0 | 820.4 | 0 |  |  | -0.02479 |  |  | 0 |  | 1 | NEWENERGY | OSW_SMITHB
200017 | SMITHBRG C | 500 | 228 | 74 | 0 | 327.6 | 327.6 |  |  | -0.02479 |  |  | 0 |  | 1 | CAPACITY | OSW_SMITHB
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  |  |  | -0.0427
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 245.67 |  |  | -0.04268 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.04268 |  |  | 0.04435 |  | 1 | CAPACITY | RARITAN RIVER
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.04268 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
207435 | AD1-113 CT2 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.04268 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207441 | AD1-113 ST | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.04268 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207434 | AD1-113 CT1 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.04268 |  |  | 0.04435 |  | 1 | NEW | RARITAN RIVER
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 97.1 | 111.6 | 97.21 |  |  | -0.04268 |  |  | 0.08446 |  | 1 | CAPACITY
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 90.9 | 104.5 | 91.03 |  |  | -0.04268 |  |  | 0.08446 |  | 1 | CAPACITY
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 199.11 |  |  | -0.04516 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.04516 |  |  | 0.04435 |  | 1 | CAPACITY | RED OAK
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.04582 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 141.3 |  |  | -0.04582 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 43.63 |  |  | -0.047 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 46.17 |  |  | -0.047 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0 |  |  | -0.04713 |  |  | 0 |  | 1 | NEWENERGY | W2-078
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.04713 |  |  | 0 |  | 1 | NEWENERGY | W1-113
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.04713 |  |  | 0 |  | 1 | CAPACITY | W2-078
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 2.25 |  |  | -0.04713 |  |  | 0 |  | 1 | CAPACITY | W1-113
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 66.1 | 98 | 78.68 |  |  | -0.04728 |  |  | 0.08446 |  | 1 | CAPACITY
206327 | 28S RIV G1 | 13.8 | 228 | 57 | 86.9 | 99.9 | 87.02 |  |  | -0.04728 |  |  | 0.08446 |  | 1 | CAPACITY
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 87.02 |  |  | -0.04728 |  |  | 0.08446 |  | 1 | CAPACITY
207419 | AB2-139 E | 34.5 | 228 | 76 | 0 | 0.21 | 0 |  |  | -0.04971 |  |  | 0 |  | 1 | ENERGY | AB2-139
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0 |  |  | -0.05064 |  |  | 0 |  | 1 | NEWENERGY | AC1-207
207420 | AC1-207 C | 34.5 | 228 | 75 | 0 | 4.9 | 3.93 |  |  | -0.05064 |  |  | 0 |  | 1 | CAPACITY | AC1-207
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.05087 |  |  | 0 |  | 1 | NEWENERGY | X1-085
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.05087 |  |  | 0 |  | 1 | CAPACITY | X1-085
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.05335 |  |  | 0.05 |  | 1 | MTX
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.05338 |  |  | 0 |  | 1 | NEWENERGY | W4-060
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.05338 |  |  | 0 |  | 1 | CAPACITY | W4-060
901032 | W1-024E OP1 | 34.5 | 228 | 0 | 0 | 0 | 0 |  |  | -0.05448 |  |  | 0 |  | 1 | NEW
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.05448 |  |  | 0 |  | 1 | CAPACITY | W1-024
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.05478 |  |  | 0 |  | 1 | NEWENERGY | W1-032
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.05478 |  |  | 0 |  | 1 | CAPACITY | W1-032
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0 |  |  | -0.057 |  |  | 0 |  | 1 | NEWENERGY | W2-019
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 1.85 |  |  | -0.057 |  |  | 0 |  | 1 | CAPACITY | W2-019
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.05754 |  |  | 0 |  | 1 | NEWENERGY | W4-025
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.05754 |  |  | 0 |  | 1 | NEWENERGY | W1-129
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.05754 |  |  | 0 |  | 1 | CAPACITY | W4-025
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.05754 |  |  | 0 |  | 1 | CAPACITY | W1-129
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.05781 |  |  | 0 |  | 1 | NEWENERGY | X4-015
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.05781 |  |  | 0 |  | 1 | CAPACITY | X4-015
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.05819 |  |  | 0 |  | 1 | NEWENERGY | W2-082
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.05819 |  |  | 0 |  | 1 | CAPACITY | W2-082
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0 |  |  | -0.06121 |  |  | 0 |  | 1 | NEWENERGY | Z2-102
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 3.97 |  |  | -0.06121 |  |  | 0 |  | 1 | CAPACITY | Z2-102
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.0613 |  |  | 0 |  | 1 | NEWENERGY | W1-120
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.0613 |  |  | 0 |  | 1 | NEWENERGY | W1-119
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.0613 |  |  | 0 |  | 1 | CAPACITY | W1-120
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.0613 |  |  | 0 |  | 1 | CAPACITY | W1-119
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0 |  |  | -0.06231 |  |  | 0 |  | 1 | NEWENERGY | W1-112
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.06231 |  |  | 0 |  | 1 | CAPACITY | W1-112
206201 | 28JERSVGEN | 34.5 | 228 | 2 | 0 | 2 | 1.61 |  |  | -0.06557 |  |  | 0 |  | 1 | CAPACITY
920732 | AA2-184 E | 34.5 | 228 | 75 | 0 | 20 | 0 |  |  | -0.06967 |  |  | 0 |  | 1 | NEWENERGY | AA2-184
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.07041 |  |  | 0 |  | 1 | NEWENERGY | W1-124
921743 | AA2-049 E | 34.5 | 228 | 76 | -3 | 3 | 0 |  |  | -0.07041 |  |  | 0 |  | 1 | MTX | AA2-049
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.07041 |  |  | 0 |  | 1 | CAPACITY | W1-124
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0 |  |  | -0.07061 |  |  | 0 |  | 1 | NEWENERGY | X1-037
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 3.37 |  |  | -0.07061 |  |  | 0 |  | 1 | CAPACITY | X1-037
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.07375 |  |  | 0 |  | 1 | NEWENERGY | X4-031
923463 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.08532 |  |  | 0 |  | 1 | NEWENERGY | AB1-163
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.08697 |  |  | 0 |  | 1 | NEWENERGY | W3-079
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.08697 |  |  | 0 |  | 1 | CAPACITY | W3-079
900005 | 28LARRABEE E | 230 | 228 | 74 | 0 | 840 | 0 |  |  | -0.09114 |  |  | 0 |  | 1 | NEWENERGY | OSW_LARRAB
206294 | 28LARRABEE C | 230 | 228 | 74 | 0 | 360 | 360 |  |  | -0.09114 |  |  | 0 |  | 1 | CAPACITY | OSW_LARRAB
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.0912 |  |  | 0 |  | 1 | NEWENERGY | Y2-051
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.0912 |  |  | 0 |  | 1 | CAPACITY | Y2-051
923293 | AB1-138 E | 34.5 | 228 | 75 | 0 | 6 | 0 |  |  | -0.10232 |  |  | 0 |  | 1 | NEWENERGY | AB1-138
206280 | 28LAKEHURS | 34.5 | 228 | 64 | 0 | 13.8 | 11.08 |  |  | -0.10232 |  |  | 0.08446 |  | 1 | CAPACITY
923292 | AB1-138 C | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.10232 |  |  | 0 |  | 1 | CAPACITY | AB1-138
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.11599 |  |  | 0.08446 |  | 1 | CAPACITY
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.11599 |  |  | 0.08446 |  | 1 | CAPACITY
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 61.6 | 88.4 | 70.97 |  |  | -0.11599 |  |  | 0.04435 |  | 1 | CAPACITY | LAKEWOOD
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 61.2 | 88.3 | 70.89 |  |  | -0.11599 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 76.92 |  |  | -0.11599 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD

## FG 28-GD-S2-S11
****** PJM Generator Deliverability Detailed Report ****** POWER-GEM [TARA Ver 2001.1a PJMGD RC3 64-bit - Wed Aug 18 16:48:38 2021]
FG Index | 11 | Monitored Facility:206302 28OYSTER C 230 206297 28MANITOU 230 2 / Contingency:JC-P2-3-JCC-230-11[Breaker]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
802 | 103.35 | 101.06 | AC | 114.63 | 698.67 | 1.23 | 17.21 | -2.87 | 828.87 | 810.5 | 0.001615 | 0 | 12822.9 | 0 | 10614.2 | 0.07479 | 2208.65 | 2208.7 | -0.05 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited?
900002 | 28OYSTER E | 230 | 228 | 74 | 0 | 586.7 | 0 | 586.7 | FiftyFifty | 0.66798 | 391.9058 |  | 0 | 0.7635 | 1 | NEWENERGY | OSW_OYSCK
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 27.3 | 34 | FiftyFifty | 0.66798 | 4.4775 |  | 0.12623 | 0.8738 | 1 | CAPACITY
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 27 | 31 | FiftyFifty | 0.66798 | 2.6693 |  | 0.12623 | 0.7635 | 1 | CAPACITY
206302 | 28OYSTER C | 230 | 228 | 74 | 0 | 229.3 | 229.3 | 229.3 | FiftyFifty | 0.66798 |  |  | 0 | 0.7635 | 1 | CAPACITY | OSW_OYSCK
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0 | 1.43 | FiftyFifty | 0.26554 | 0.3797 |  | 0 | 0.7635 | 1 | NEWENERGY | AB1-001
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.7 | 0.87 | FiftyFifty | 0.26554 | 0.0454 |  | 0 | 0.7635 | 1 | CAPACITY | AB1-001
900000 | CARDIFF E | 230 | 234 | 74 | 0 | 1235 | 0 | 1235 | FiftyFifty | 0.19605 | 242.1161 |  | 0 | 0.7635 | 1 | NEWENERGY | OSW_CARDIF
227900 | CARDIFF C | 230 | 234 | 74 | 0 | 275 | 275 | 275 | FiftyFifty | 0.19605 |  |  | 0 | 0.7635 | 1 | CAPACITY | OSW_CARDIF
227928 | V4-067E | 12.9 | 234 | 75 | 1.6 | 1.6 | 0 | 1.6 | FiftyFifty | 0.1834 | 0.2934 |  | 0 | 0.7635 | 1 | NEWENERGY | V4-067
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.79 | 0.98 | FiftyFifty | 0.1834 | 0.0356 |  | 0 | 0.7635 | 1 | CAPACITY | V4-067
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0 | 1.2 | FiftyFifty | 0.18337 | 0.22 |  | 0 | 0.7635 | 1 | NEWENERGY | AB2-122
924701 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.56 | 0.7 | FiftyFifty | 0.18337 | 0.0251 |  | 0 | 0.7635 | 1 | CAPACITY | AB2-122
228014 | PVILLEG | 0.48 | 234 | 65 | 1.7 | 3 | 1.04 | 3 | FiftyFifty | 0.17979 | 0.3517 |  | 0 | 0.7635 | 1 | CAPACITY
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 | 7.8 | FiftyFifty | 0.17832 | 1.3909 |  | 0.12623 | 0.6671 | 1 | ENERGY
227801 | ONTC&DCT | 13.8 | 234 | 56 | 38.6 | 38.6 | 0 | 38.6 | FiftyFifty | 0.17821 | 6.8791 |  | 0.08446 | 0.6108 | 1 | NEW
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 | 5.5 | FiftyFifty | 0.17821 | 0.9802 |  | 0.10478 | 0.5468 | 1 | ENERGY
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0 | 6 | FiftyFifty | 0.17461 | 1.0476 |  | 0 | 0.5468 | 1 | NEWENERGY | W2-030
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 2.93 | 3.65 | FiftyFifty | 0.17461 | 0.1254 |  | 0 | 0.5468 | 1 | CAPACITY | W2-030
900001 | BLE E | 138 | 234 | 74 | 0 | 310.6 | 0 | 310.6 | FiftyFifty | 0.14705 | 45.6733 |  | 0 | 0.5468 | 1 | NEWENERGY | OSW_BLE
228110 | BLE C | 138 | 234 | 74 | 0 | 121.4 | 121.4 | 121.4 | FiftyFifty | 0.14705 |  |  | 0 | 0.5468 | 1 | CAPACITY | OSW_BLE
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.61 | 2 | FiftyFifty | 0.12749 | 0.0502 |  | 0 | 0.5468 | 1 | CAPACITY
228712 | V2-041E | 13.2 | 234 | 75 | 2.5 | 2.48 | 0 | 2.11 | Adder/OL | 0.09697 | 0.2044 | 0.0034 | 0 |  | 1 | NEWENERGY | V2-041
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0 | 4.84 | Adder/OL | 0.09043 | 0.4381 | 0.0078 | 0 |  | 1 | NEWENERGY | W1-130
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  | 105 | LTF/CMTX NF | 0.04083 | 4.2868 | -0.1695
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  | 673 | LTF/CMTX NF | 0.01703 | 11.4629 | -1.0867
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  | 55.3 | CLTF | 0.01112 | 0.6149 | -0.0893
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.6 |  | 173.6 | CLTF | 0.00097 | 0.1675 | -0.2803
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 0.00097 | 0.0538 | -0.0899
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 0.00097 | 0.0527 | -0.0882
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  | 258.3 | CLTF | 0.00094 | 0.2423 | -0.4171
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  | 210 | CLTF | 0.00088 | 0.1849 | -0.3391
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 0.00083 | 0.0417 | -0.0808
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 0.00084 | 0.0416 | -0.0803
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  | 35 | CLTF | 0.00073 | 0.0255 | -0.0565
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  | 57.8 | CLTF | 0.00067 | 0.039 | -0.0932
919662 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 | -7 | Adder/NFTWR/OL | -0.08415 | 0.5891 | -0.0113 | 0.05 |  | 1 | MTX NFTWR | AA2-048
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 74.48 |  |  | 0.09913 |  |  | 0.08446 |  | 1 | CAPACITY
228203 | P06 | 13.8 | 234 | 57 | 80.6 | 92.7 | 80.75 |  |  | 0.09752 |  |  | 0.08446 |  | 1 | CAPACITY
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 1.22 |  |  | 0.09697 |  |  | 0 |  | 1 | CAPACITY | V2-041
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 73.09 |  |  | 0.0936 |  |  | 0.08446 |  | 1 | CAPACITY
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 2.57 |  |  | 0.09043 |  |  | 0 |  | 1 | CAPACITY | W1-130
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 48.35 |  |  | 0.08358 |  |  | 0.08446 |  | 1 | CAPACITY
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.5 | 18.87 |  |  | 0.08068 |  |  | 0.08446 |  | 1 | CAPACITY
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 49.65 |  |  | 0.07917 |  |  | 0.10478 |  | 1 | CAPACITY
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0 |  |  | 0.07252 |  |  | 0 |  | 1 | NEWENERGY | V4-054
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 3.05 |  |  | 0.07252 |  |  | 0 |  | 1 | CAPACITY | V4-054
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 4.8 | 0 |  |  | 0.0725 |  |  | 0 |  | 1 | NEW
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.6 | 39.8 | 34.67 |  |  | 0.0724 |  |  | 0.08446 |  | 1 | CAPACITY
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 32.75 |  |  | 0.0724 |  |  | 0.08446 |  | 1 | CAPACITY
228721 | V2-035E | 12.9 | 234 | 75 | 1.2 | 1.2 | 0 |  |  | 0.0637 |  |  | 0 |  | 1 | NEWENERGY | V2-035
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.61 |  |  | 0.0637 |  |  | 0 |  | 1 | CAPACITY | V2-035
228343 | QUINTN#1 | 12.9 | 234 | 64 | 0 | 1.7 | 0 |  |  | 0.05742 |  |  | 0 |  | 1 | CAPACITY
228357 | V2-046E | 12.9 | 234 | 75 | 12.9 | 12.9 | 0 |  |  | 0.04991 |  |  | 0 |  | 1 | NEWENERGY | V2-046
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 6.26 |  |  | 0.04991 |  |  | 0 |  | 1 | CAPACITY | V2-046
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 192.69 |  |  | 0.04923 |  |  | 0.10478 |  | 1 | CAPACITY
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 58.9 | 47.29 |  |  | 0.03871 |  |  | 0.04435 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 58.9 | 47.29 |  |  | 0.03871 |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 175.82 |  |  | 0.0351 |  |  | 0.10478 |  | 1 | CAPACITY
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | 0.03179 |  |  | 0 |  | 1 | ENERGY
228471 | VALERO1 | 13.8 | 234 | 2 | 19.1 | 22 | 19.16 |  |  | 0.03142 |  |  | 0 |  | 1 | CAPACITY
228473 | VALERO3 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.03142 |  |  | 0 |  | 1 | CAPACITY
228472 | VALERO2 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.03142 |  |  | 0 |  | 1 | CAPACITY
228484 | VALERO4 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.03142 |  |  | 0 |  | 1 | CAPACITY
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 55.49 |  |  | 0.02989 |  |  | 0.08446 |  | 1 | CAPACITY
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 271.13 |  |  | 0.02293 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.02293 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.02293 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 998.11 |  |  | 0.01909 |  |  | 0.01494 |  | 1 | CAPACITY
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 992.1 |  |  | 0.01909 |  |  | 0.01494 |  | 1 | CAPACITY
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | 0.01909 |  |  | 0.08446 |  | 1 | ENERGY
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1026.43 |  |  | 0.01895 |  |  | 0.01494 |  | 1 | CAPACITY
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 60.21 |  |  | 0.01807 |  |  | 0.10478 |  | 1 | CAPACITY
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0 |  |  | 0.01661 |  |  | 0 |  | 1 | NEWENERGY | Y2-081
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | 0.01661 |  |  | 0 |  | 1 | CAPACITY | Y2-081
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | 0.01638 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 33.72 |  |  | 0.01636 |  |  | 0.04435 |  | 1 | CAPACITY | EAGLE POINT
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 24.08 |  |  | 0.01636 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | 0.01635 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0 |  |  | 0.01586 |  |  | 0 |  | 1 | NEWENERGY | Y3-087
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 1.84 |  |  | 0.01586 |  |  | 0 |  | 1 | CAPACITY | Y3-087
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0 |  |  | 0.01482 |  |  | 0 |  | 1 | NEWENERGY | X3-075
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | 0.01419 |  |  | 0.04435 |  | 1 | NEW | AA2-069
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 154.95 |  |  | 0.01419 |  |  | 0.04435 |  | 1 | CAPACITY | Garrison
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 93.29 |  |  | 0.01419 |  |  | 0 |  | 1 | CAPACITY | Garrison
232901 | NORTHST | 69 | 235 | 56 | 5 | 46 | 36.93 |  |  | 0.01419 |  |  | 0.08446 |  | 1 | CAPACITY
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 12.2 |  |  | 0.01419 |  |  | 0.10478 |  | 1 | CAPACITY
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | 0.0142 |  |  | 0 |  | 1 | MTX | Z1-082
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 39.34 |  |  | 0.01407 |  |  | 0.08446 |  | 1 | CAPACITY
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 38.54 |  |  | 0.01407 |  |  | 0.08446 |  | 1 | CAPACITY
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 64.31 |  |  | 0.01401 |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 52.35 |  |  | 0.01401 |  |  | 0.04435 |  | 1 | CAPACITY | CAMDEN COGEN TECH
925391 | AC1-010 C | 26.4 | 231 | 75 | 0 | 6 | 0 |  |  | 0.01401 |  |  | 0 |  | 1 | NEW | AC1-010
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 19.27 |  |  | 0.01401 |  |  | 0.10478 |  | 1 | CAPACITY
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | 0.01401 |  |  | 0 |  | 1 | NEWENERGY | AC1-010
219765 | PARADISE E | 26.4 | 231 | 75 | 0 | 3.2 | 0 |  |  | 0.01401 |  |  | 0 |  | 1 | NEWENERGY | U4-036
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.3 | 9.07 |  |  | 0.01401 |  |  | 0.10478 |  | 1 | CAPACITY
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | 0.01401 |  |  | 0 |  | 1 | MTX | X2-013
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | 0.01401 |  |  | 0 |  | 1 | CAPACITY | U4-036
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 0 |  |  | 0.01367 |  |  | 0 |  | 1 | NEWENERGY | AB1-056
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 330.7 |  |  | 0.01367 |  |  | 0.10478 |  | 1 | CAPACITY
930201 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 51.71 |  |  | 0.01367 |  |  | 0 |  | 1 | CAPACITY | AB1-056
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 152.54 |  |  | 0.01367 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01367 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC2
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01367 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01367 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
232920 | IR10 | 13.2 | 235 | 55 | 12.6 | 16.1 | 12.93 |  |  | 0.01366 |  |  | 0.08446 |  | 1 | CAPACITY
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0 |  |  | 0.01366 |  |  | 0 |  | 1 | NEWENERGY | AB1-137
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 3.37 |  |  | 0.01366 |  |  | 0 |  | 1 | CAPACITY | AB1-137
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | 0.01364 |  |  | 0.10478 |  | 1 | ENERGY
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.01363 |  |  | 0 |  | 1 | NEWENERGY | Z2-077
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.01363 |  |  | 0 |  | 1 | NEWENERGY | Z2-076
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.01363 |  |  | 0 |  | 1 | CAPACITY | Z2-077
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.01363 |  |  | 0 |  | 1 | CAPACITY | Z2-076
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.41 |  |  | 0.01363 |  |  | 0 |  | 1 | CAPACITY
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.01359 |  |  | 0.08446 |  | 1 | CAPACITY
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.01359 |  |  | 0.08446 |  | 1 | CAPACITY
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.05 |  |  | 0.0136 |  |  | 0 |  | 1 | CAPACITY
917082 | CHERRYDALE E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01354 |  |  | 0 |  | 1 | NEWENERGY | Z2-012
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01354 |  |  | 0 |  | 1 | NEWENERGY | W1-004
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01354 |  |  | 0 |  | 1 | NEWENERGY | W1-003
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01354 |  |  | 0 |  | 1 | NEWENERGY | W1-005
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01354 |  |  | 0 |  | 1 | NEWENERGY | W1-006
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.01354 |  |  | 0.08446 |  | 1 | CAPACITY
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.01354 |  |  | 0.08446 |  | 1 | CAPACITY
232915 | OH NUG4 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.01354 |  |  | 0.08446 |  | 1 | CAPACITY
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.01354 |  |  | 0.08446 |  | 1 | CAPACITY
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 39.03 |  |  | 0.01354 |  |  | 0.08446 |  | 1 | CAPACITY
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 38.94 |  |  | 0.01354 |  |  | 0.08446 |  | 1 | CAPACITY
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 38.68 |  |  | 0.01354 |  |  | 0.08446 |  | 1 | CAPACITY
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 26.05 |  |  | 0.01354 |  |  | 0.08446 |  | 1 | CAPACITY
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.01354 |  |  | 0 |  | 1 | CAPACITY | W1-003
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.01354 |  |  | 0 |  | 1 | CAPACITY | W1-004
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.01354 |  |  | 0 |  | 1 | CAPACITY | W1-005
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.01354 |  |  | 0 |  | 1 | CAPACITY | W1-006
232905 | BAYVIEW1 | 24.9 | 235 | 65 | 0 | 12.5 | 10.04 |  |  | 0.01354 |  |  | 0.12623 |  | 1 | CAPACITY
917081 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.01354 |  |  | 0 |  | 1 | CAPACITY | Z2-012
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 0 |  |  | 0.01351 |  |  | 0 |  | 1 | NEWENERGY | AA1-102
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 45.76 |  |  | 0.01351 |  |  | 0 |  | 1 | CAPACITY | AA1-102
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0 |  |  | 0.01352 |  |  | 0 |  | 1 | NEWENERGY | X1-032
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 8.03 |  |  | 0.01351 |  |  | 0 |  | 1 | CAPACITY
293670 | O-025 C | 25 | 235 | 64 | 0 | 6 | 4.82 |  |  | 0.01351 |  |  | 0 |  | 1 | CAPACITY
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0 |  |  | 0.01349 |  |  | 0 |  | 1 | NEWENERGY | Y3-058
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 5.7 | 4.58 |  |  | 0.01349 |  |  | 0 |  | 1 | CAPACITY | Y3-058
232919 | VN10 | 13.2 | 235 | 55 | 12.4 | 14.3 | 12.46 |  |  | 0.01339 |  |  | 0 |  | 1 | CAPACITY
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 122.84 |  |  | 0.01336 |  |  | 0.10478 |  | 1 | CAPACITY
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0 |  |  | 0.01336 |  |  | 0 |  | 1 | NEWENERGY | Y1-080
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 1.03 |  |  | 0.01336 |  |  | 0 |  | 1 | CAPACITY | Y1-080
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01328 |  |  | 0 |  | 1 | NEWENERGY | X3-008
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.01328 |  |  | 0 |  | 1 | CAPACITY | X3-008
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 55.4 |  |  | 0.01301 |  |  | 0.12623 |  | 1 | CAPACITY
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0 |  |  | 0.01285 |  |  | 0 |  | 1 | NEWENERGY | Y1-079
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.01285 |  |  | 0 |  | 1 | CAPACITY | Y1-079
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 57.24 |  |  | 0.01279 |  |  | 0.10478 |  | 1 | CAPACITY
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 45.76 |  |  | 0.01279 |  |  | 0.08446 |  | 1 | CAPACITY
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 44.16 |  |  | 0.01279 |  |  | 0.04435 |  | 1 | CAPACITY | DELAWARE CITY
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 14.29 |  |  | 0.01279 |  |  | 0.08446 |  | 1 | CAPACITY
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0 |  |  | 0.01276 |  |  | 0 |  | 1 | NEWENERGY | X3-066
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 2.28 | 1.83 |  |  | 0.01276 |  |  | 0 |  | 1 | CAPACITY | X3-066
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 19.11 |  |  | 0.01275 |  |  | 0.12623 |  | 1 | CAPACITY
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.01265 |  |  | 0 |  | 1 | NEWENERGY | AB1-141
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.01265 |  |  | 0 |  | 1 | NEWENERGY | AB1-142
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.01265 |  |  | 0 |  | 1 | CAPACITY | AB1-141
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.01265 |  |  | 0 |  | 1 | CAPACITY | AB1-142
219647 | COOPERSOLA E | 13.2 | 231 | 75 | 0 | 0.4 | 0 |  |  | 0.01258 |  |  | 0 |  | 1 | NEWENERGY | AB1-063
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.01202 |  |  | 0 |  | 1 | NEWENERGY | AB2-179
233931 | AB2-179 C | 0.38 | 235 | 75 | 0 | 38 | 30.51 |  |  | 0.01202 |  |  | 0 |  | 1 | CAPACITY | AB2-179
219913 | PENNSAU2 E | 26.4 | 231 | 75 | 0 | 8.2 | 0 |  |  | 0.01187 |  |  | 0 |  | 1 | NEWENERGY | AD2-042
219915 | CINNAMSOL E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | 0.01187 |  |  | 0 |  | 1 | NEWENERGY | AD2-027
219912 | PENNSAU2 C | 26.4 | 231 | 75 | 0 | 5 | 0 |  |  | 0.01187 |  |  | 0 |  | 1 | NEW | AD2-042
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.63 | 3.72 |  |  | 0.01187 |  |  | 0 |  | 1 | CAPACITY
219914 | CINNAMSOL C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | 0.01187 |  |  | 0 |  | 1 | CAPACITY | AD2-027
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.4 |  |  | 0.01187 |  |  | 0 |  | 1 | CAPACITY
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.09 |  |  | 0.01163 |  |  | 0 |  | 1 | CAPACITY
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 18.47 |  |  | 0.01132 |  |  | 0.08446 |  | 1 | CAPACITY
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 18.39 |  |  | 0.01132 |  |  | 0.08446 |  | 1 | CAPACITY
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 13.81 |  |  | 0.0113 |  |  | 0.08446 |  | 1 | CAPACITY
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 139.7 |  |  | 0.0111 |  |  | 0.10478 |  | 1 | CAPACITY
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.0111 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.0111 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.01107 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 69.05 |  |  | 0.01107 |  |  | 0.10478 |  | 1 | CAPACITY
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 11.4 |  |  | 0.01107 |  |  | 0.08446 |  | 1 | CAPACITY
925112 | AB2-168 E | 34.5 | 235 | 75 | 0 | 5.2 | 0 |  |  | 0.01099 |  |  | 0 |  | 1 | NEWENERGY | AB2-168
925111 | AB2-168 C | 34.5 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.01099 |  |  | 0 |  | 1 | CAPACITY | AB2-168
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 361.29 |  |  | 0.01021 |  |  | 0.10478 |  | 1 | CAPACITY
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 148.77 |  |  | 0.01021 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC1
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.00946 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.00946 |  |  | 0.04435 |  | 1 | CAPACITY | PHILLIPS ISLAND
213893 | PHLISST1 | 20 | 230 | 58 | 184 | 267 | 214.36 |  |  | 0.00946 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | 0.00946 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.5 | 0 |  |  | 0.00892 |  |  | 0 |  | 1 | NEWENERGY | AC1-030
925561 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | 0.00892 |  |  | 0 |  | 1 | CAPACITY | AC1-030
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0 |  |  | 0.00889 |  |  | 0 |  | 1 | NEWENERGY | X1-071
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.28 |  |  | 0.00889 |  |  | 0 |  | 1 | CAPACITY | X1-071
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | 0.00869 |  |  | 0.08446 |  | 1 | CAPACITY
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | 0.00869 |  |  | 0.08446 |  | 1 | CAPACITY
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 31.31 |  |  | 0.00755 |  |  | 0.08446 |  | 1 | CAPACITY
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | 0.00754 |  |  | 0.08446 |  | 1 | CAPACITY
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | 0.00754 |  |  | 0.08446 |  | 1 | CAPACITY
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | 0.00742 |  |  | 0.10478 |  | 1 | CAPACITY
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 27.3 |  |  | 0.00741 |  |  | 0.08446 |  | 1 | CAPACITY
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | 0.00741 |  |  | 0.10478 |  | 1 | CAPACITY
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 238 | 191.08 |  |  | 0.00736 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | 0.00737 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | 0.00736 |  |  | 0.04435 |  | 1 | CAPACITY | LIBERTY EDDY
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | 0.0073 |  |  | 0.08446 |  | 1 | CAPACITY
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | 0.00685 |  |  | 0.08446 |  | 1 | CAPACITY
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 130.87 |  |  | 0.00606 |  |  | 0.04435 |  | 1 | CAPACITY | GRAYS FERRY
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | 0.00603 |  |  | 0.08446 |  | 1 | CAPACITY
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | 0.00602 |  |  | 0.08446 |  | 1 | CAPACITY
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | 0.00602 |  |  | 0.08446 |  | 1 | CAPACITY
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0 |  |  | 0.00584 |  |  | 0 |  | 1 | NEWENERGY | W2-071
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.85 |  |  | 0.00584 |  |  | 0 |  | 1 | CAPACITY | W2-071
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | 0.00567 |  |  | 0.08446 |  | 1 | CAPACITY
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | 0.00567 |  |  | 0.08446 |  | 1 | CAPACITY
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0 |  |  | 0.00567 |  |  | 0 |  | 1 | NEWENERGY | AC1-017
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0 |  |  | 0.00567 |  |  | 0 |  | 1 | NEWENERGY | X1-070
925451 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 1.12 |  |  | 0.00567 |  |  | 0 |  | 1 | CAPACITY | AC1-017
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.96 |  |  | 0.00567 |  |  | 0 |  | 1 | CAPACITY | X1-070
214030 | WAYNEJCT | 13.8 | 230 | 2 | 0 | 8.8 | 7.07 |  |  | 0.00565 |  |  | 0 |  | 1 | CAPACITY
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | 0.00506 |  |  | 0.07484 |  | 1 | CAPACITY
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | 0.00506 |  |  | 0.07484 |  | 1 | CAPACITY
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 77.07 |  |  | 0.00506 |  |  | 0.07484 |  | 1 | CAPACITY
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | 0.00506 |  |  | 0.07484 |  | 1 | CAPACITY
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | 0.00506 |  |  | 0.07484 |  | 1 | CAPACITY
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 38.54 |  |  | 0.00506 |  |  | 0.07484 |  | 1 | CAPACITY
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 369.31 |  |  | 0.00501 |  |  | 0.04435 |  | 1 | CAPACITY | Y1-065
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00501 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | 0.00501 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200055 | ROCKSP 4 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00501 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 4
200054 | ROCKSP 3 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | 0.00501 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 3
200052 | ROCKSP 1 | 18 | 225 | 57 | 145.7 | 167.5 | 145.91 |  |  | 0.00501 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 1
200053 | ROCKSP 2 | 18 | 225 | 57 | 144.9 | 166.5 | 145.04 |  |  | 0.00501 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 2
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0 |  |  | 0.00478 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 S
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 0.00478 |  |  | 0 |  | 1 | CAPACITY | AB1-025 S
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0 |  |  | 0.00476 |  |  | 0 |  | 1 | NEWENERGY | Y1-075
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 0.00476 |  |  | 0 |  | 1 | CAPACITY | Y1-075
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | 0.00457 |  |  | 0 |  | 1 | ENERGY
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0 |  |  | 0.00359 |  |  | 0 |  | 1 | NEWENERGY | V4-005
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.88 |  |  | 0.00359 |  |  | 0 |  | 1 | CAPACITY | V4-005
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 0 |  |  | 0.0033 |  |  | 0 |  | 1 | NEWENERGY | W3-080
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.0033 |  |  | 0.08446 |  | 1 | CAPACITY
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.0033 |  |  | 0.08446 |  | 1 | CAPACITY
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.0033 |  |  | 0.08446 |  | 1 | CAPACITY
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.0033 |  |  | 0.08446 |  | 1 | CAPACITY
925442 | AC1-016 E | 26.4 | 231 | 75 | 0 | 5.45 | 0 |  |  | 0.0033 |  |  | 0 |  | 1 | NEWENERGY | AC1-016
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | 0.0033 |  |  | 0 |  | 1 | NEWENERGY | W2-102
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | 0.0033 |  |  | 0 |  | 1 | NEWENERGY | W4-103
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | 0.0033 |  |  | 0 |  | 1 | NEWENERGY | Y3-026
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | 0.0033 |  |  | 0 |  | 1 | CAPACITY | Y3-026
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 2.97 |  |  | 0.0033 |  |  | 0 |  | 1 | CAPACITY | W3-080
925441 | AC1-016 C | 26.4 | 231 | 75 | 0 | 3.34 | 2.68 |  |  | 0.0033 |  |  | 0 |  | 1 | CAPACITY | AC1-016
219685 | NATIONAL_GYP | 26 | 231 | 2 | 0 | 2.8 | 2.25 |  |  | 0.0033 |  |  | 0 |  | 1 | CAPACITY
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | 0.0033 |  |  | 0 |  | 1 | CAPACITY | W2-102
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | 0.0033 |  |  | 0 |  | 1 | CAPACITY | W4-103
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00322 |  |  | 0.08446 |  | 1 | CAPACITY
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00322 |  |  | 0.08446 |  | 1 | CAPACITY
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00322 |  |  | 0.08446 |  | 1 | CAPACITY
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00322 |  |  | 0.08446 |  | 1 | CAPACITY
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00322 |  |  | 0.08446 |  | 1 | CAPACITY
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00322 |  |  | 0.08446 |  | 1 | CAPACITY
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00322 |  |  | 0.08446 |  | 1 | CAPACITY
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 38.54 |  |  | 0.00322 |  |  | 0.08446 |  | 1 | CAPACITY
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | 0.0031 |  |  | 0.0316 |  | 1 | CAPACITY
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | 0.0031 |  |  | 0.0316 |  | 1 | CAPACITY
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | 0.0031 |  |  | 0.0316 |  | 1 | CAPACITY
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | 0.0031 |  |  | 0.0316 |  | 1 | CAPACITY
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1034.24 |  |  | 0.00281 |  |  | 0.01494 |  | 1 | CAPACITY
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 306.69 |  |  | 0.00279 |  |  | 0 |  | 1 | CAPACITY | DELTA2
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 260.3 | 208.98 |  |  | 0.00279 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00279 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | 0.00279 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA2
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 154.95 |  |  | 0.00279 |  |  | 0 |  | 1 | CAPACITY | DELTA
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | 0.00279 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | 0.00279 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill B
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00279 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00279 |  |  | 0 |  | 1 | CAPACITY | DELTA
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | 0.00279 |  |  | 0 |  | 1 | CAPACITY | DELTA
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 205.69 |  |  | 0.00279 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | 0.00279 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill A
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | 0.00279 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1049.33 |  |  | 0.00271 |  |  | 0.01494 |  | 1 | CAPACITY
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 22.48 |  |  | 0.00215 |  |  | 0.10478 |  | 1 | CAPACITY
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0 |  |  | 0.00072 |  |  | 0 |  | 1 | NEWENERGY | AA2-072
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 140.6 | 112.88 |  |  | 0.00067 |  |  | 0.08446 |  | 1 | CAPACITY
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 91.2 |  |  | 0.00067 |  |  | 0.08446 |  | 1 | CAPACITY
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 83.5 |  |  | 0.00067 |  |  | 0.08446 |  | 1 | CAPACITY
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 41.75 |  |  | 0.00067 |  |  | 0.08446 |  | 1 | CAPACITY
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.21 |  |  | 0.00067 |  |  | 0 |  | 1 | CAPACITY
220904 | CRANE G2 | 20 | 232 | 12 | 60 | 195 | 0 |  |  | 0.00059 |  |  | 0.10478 |  | 1 | NEW
220905 | CRANE GT | 4.16 | 232 | 55 | 0 | 14 | 0 |  |  | 0.00059 |  |  | 0.08446 |  | 1 | NEW
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | 0.00056 |  |  | 0 |  | 1 | ENERGY
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 256.27 |  |  | 0.00056 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | 0.00056 |  |  | 0.04435 |  | 1 | CAPACITY | HUNTERSTOWN
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | 0.00056 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 134.08 |  |  | 0.00056 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.5 | 24.49 |  |  | 0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 30 | 24.08 |  |  | 0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 45.76 |  |  | 0.00053 |  |  | 0.10478 |  | 1 | CAPACITY
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 246 |  |  | 0.00051 |  |  | 0.10478 |  | 1 | CAPACITY
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 102.85 |  |  | 0.00051 |  |  | 0.10478 |  | 1 | CAPACITY
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | 0.00051 |  |  | 0.08446 |  | 1 | ENERGY
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 10.68 |  |  | 0.00051 |  |  | 0.08446 |  | 1 | CAPACITY
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 516 |  |  | 0.0005 |  |  | 0.10478 |  | 1 | CAPACITY
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 512.95 |  |  | 0.0005 |  |  | 0.10478 |  | 1 | CAPACITY
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 318.73 |  |  | 0.0005 |  |  | 0.10478 |  | 1 | CAPACITY
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.49 |  |  | 0.00036 |  |  | 0 |  | 1 | CAPACITY
226895 | WOAKV2-037 E | 69 | 233 | 65 | 0 | 4.5 | 0 |  |  | 0.00029 |  |  | 0 |  | 1 | ENERGY
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 695.27 |  |  | 0.00023 |  |  | 0.01494 |  | 1 | CAPACITY
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 675.85 |  |  | 0.00023 |  |  | 0.01494 |  | 1 | CAPACITY
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | 0.00022 |  |  | 0.08446 |  | 1 | ENERGY
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0 |  |  | 0.00021 |  |  | 0 |  | 1 | NEWENERGY | AB2-157
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.76 |  |  | 0.00022 |  |  | 0 |  | 1 | CAPACITY
925011 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.64 |  |  | 0.00021 |  |  | 0 |  | 1 | CAPACITY | AB2-157
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.69 |  |  | 0.00021 |  |  | 0 |  | 1 | CAPACITY
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 477.7 |  |  | 0.0002 |  |  | 0.10478 |  | 1 | CAPACITY
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 469.91 |  |  | 0.0002 |  |  | 0.10478 |  | 1 | CAPACITY
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | 0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | 0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 0 |  |  | 0.00019 |  |  | 0 |  | 1 | NEWENERGY | AC2-101
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 0 |  |  | 0.00019 |  |  | 0 |  | 1 | NEWENERGY | AC2-120
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | 0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | 0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
227024 | SMECOCT | 13.8 | 238 | 57 | 30 | 80.2 | 64.39 |  |  | 0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 19.59 |  |  | 0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 14.45 |  |  | 0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
226915 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 9.92 |  |  | 0.00019 |  |  | 0 |  | 1 | CAPACITY | AC2-101
226912 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 8.39 |  |  | 0.00019 |  |  | 0 |  | 1 | CAPACITY | AC2-120
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 497.29 |  |  | 0.00019 |  |  | 0.10478 |  | 1 | CAPACITY
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 492.39 |  |  | 0.00019 |  |  | 0.10478 |  | 1 | CAPACITY
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 272.01 |  |  | 0.00019 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | 0.00019 |  |  | 0.04435 |  | 1 | CAPACITY | WALDORF
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | 0.00019 |  |  | 0 |  | 1 | CAPACITY | WALDORF
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00019 |  |  | 0.08446 |  | 1 | CAPACITY
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00019 |  |  | 0.08446 |  | 1 | CAPACITY
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00019 |  |  | 0.08446 |  | 1 | CAPACITY
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | 0.00019 |  |  | 0.08446 |  | 1 | CAPACITY
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | 0.00019 |  |  | 0.08446 |  | 1 | CAPACITY
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | 0.00019 |  |  | 0.08446 |  | 1 | CAPACITY
910861 | X3-087 C | 230 | 233 | 58 | 0 | 744 | 597.33 |  |  | 0.00014 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
917371 | Z2-060 | 230 | 233 | 58 | 0 | 116 | 93.13 |  |  | 0.00014 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
920642 | AA2-170 E | 230 | 233 | 58 | 0 | 19.1 | 0 |  |  | 0.00014 |  |  | 0.04435 |  | 1 | NEW | AA2-170
920641 | AA2-170 C | 230 | 233 | 58 | 0 | 92 | 73.86 |  |  | 0.00014 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-170
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 64.23 |  |  | 0.00014 |  |  | 0 |  | 1 | CAPACITY | PANDA
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | 0.00014 |  |  | 0.04435 |  | 1 | CAPACITY | PANDA
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | 0.00014 |  |  | 0 |  | 1 | CAPACITY | PANDA
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 330 | 264.94 |  |  | 0.00013 |  |  | 0 |  | 1 | CAPACITY | X4-035
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | 0.00013 |  |  | 0.04435 |  | 1 | CAPACITY | X4-035
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | 0.00013 |  |  | 0 |  | 1 | CAPACITY | X4-035
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | 0.00011 |  |  | 0.10478 |  | 1 | ENERGY
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 41.75 |  |  | 1e-05 |  |  | 0.10478 |  | 1 | CAPACITY
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 14.45 |  |  | 1e-05 |  |  | 0.08446 |  | 1 | CAPACITY
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 0 |  |  | -7e-05 |  |  | 0 |  | 1 | NEWENERGY | AB2-129
924771 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 0 |  |  | -7e-05 |  |  | 0 |  | 1 | NEW | AB2-129
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 245.67 |  |  | -0.00012 |  |  | 0 |  | 1 | CAPACITY | X4-039
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.00012 |  |  | 0.04435 |  | 1 | CAPACITY | X4-039
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.00012 |  |  | 0 |  | 1 | CAPACITY | X4-039
313821 | 6PACIFIC | 230 | 345 | 75 | 0 | 0.09 | 0 |  |  | -0.00013 |  |  | 0 |  | 1 | NEWENERGY
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 201.52 |  |  | -0.00016 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00016 |  |  | 0.04435 |  | 1 | CAPACITY | POSSUM POINT
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00016 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00016 |  |  | 0.10478 |  | 1 | CAPACITY
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00016 |  |  | 0.10478 |  | 1 | CAPACITY
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 28.74 |  |  | -0.00016 |  |  | 0.10478 |  | 1 | CAPACITY
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 28.66 |  |  | -0.00016 |  |  | 0.10478 |  | 1 | CAPACITY
314088 | 6VANDORN | 230 | 345 | 2 | 7 | 21 | 16.86 |  |  | -0.00016 |  |  | 0 |  | 1 | CAPACITY
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00019 |  |  | 0 |  | 1 | NEWENERGY | AC2-072
932521 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00019 |  |  | 0 |  | 1 | CAPACITY | AC2-072
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 0.68 | 0 |  |  | -0.0002 |  |  | 0 |  | 1 | NEWENERGY
235002 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0 |  |  | -0.00021 |  |  | 0 |  | 1 | NEW | AC1-039
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0 |  |  | -0.00021 |  |  | 0 |  | 1 | NEWENERGY | AC1-039
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0 |  |  | -0.00021 |  |  | 0 |  | 1 | NEWENERGY | AA1-109
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 3.61 |  |  | -0.00021 |  |  | 0 |  | 1 | CAPACITY | AA1-109
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.00022 |  |  | 0 |  | 1 | NEWENERGY | W1-116
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 4.27 |  |  | -0.00022 |  |  | 0 |  | 1 | CAPACITY | W1-116
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 1.61 |  |  | -0.00023 |  |  | 0 |  | 1 | CAPACITY
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00025 |  |  | 0.08446 |  | 1 | CAPACITY
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00025 |  |  | 0.08446 |  | 1 | CAPACITY
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 128.86 |  |  | -0.00025 |  |  | 0.08446 |  | 1 | CAPACITY
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 152.3 | 122.28 |  |  | -0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 120.19 |  |  | -0.00025 |  |  | 0.10478 |  | 1 | CAPACITY
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00025 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
923213 | AB1-125 E OP | 34.5 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.00025 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
923202 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.00025 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0 |  |  | -0.00025 |  |  | 0 |  | 1 | NEWENERGY | AB1-096
923212 | AB1-125 C OP | 34.5 | 201 | 75 | 0 | 5.7 | 0 |  |  | -0.00025 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
930521 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | AB1-096
315033 | 1BIRCHWDA | 18 | 345 | 13 | 85 | 238 | 191.08 |  |  | -0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 0 |  |  | -0.00025 |  |  | 0 |  | 1 | NEWENERGY | AB2-029
314078 | 3REMNGTN | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00025 |  |  | 0 |  | 1 | CAPACITY | AB2-029
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.00027 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 1
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.00027 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 2
926737 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.00027 |  |  | 0 |  | 1 | CAPACITY | AC1-158 1
926738 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.00027 |  |  | 0 |  | 1 | CAPACITY | AC1-158 2
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 6.98 |  |  | -0.00027 |  |  | 0 |  | 1 | CAPACITY
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 128.94 |  |  | -0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 128.54 |  |  | -0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 128.3 |  |  | -0.00027 |  |  | 0.08446 |  | 1 | CAPACITY
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0 |  |  | -0.00028 |  |  | 0 |  | 1 | NEWENERGY | AC2-136
933251 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 4.41 |  |  | -0.00028 |  |  | 0 |  | 1 | CAPACITY | AC2-136
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 761.83 |  |  | -0.00028 |  |  | 0.01494 |  | 1 | CAPACITY
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 761.51 |  |  | -0.00028 |  |  | 0.01494 |  | 1 | CAPACITY
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.00028 |  |  | 0.08446 |  | 1 | CAPACITY
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00028 |  |  | 0 |  | 1 | CAPACITY | T20
923872 | AB2-027 E | 34.5 | 201 | 75 | 0 | 5.5 | 0 |  |  | -0.00029 |  |  | 0 |  | 1 | NEWENERGY | AB2-027
235006 | AB2-027 C | 34.5 | 201 | 75 | 0 | 3.3 | 0 |  |  | -0.00029 |  |  | 0 |  | 1 | NEW | AB2-027
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY
316149 | AD1-046 E | 230 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | AD1-044
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | AE1-124
316148 | AD1-046 C | 230 | 345 | 75 | 0 | 30.7 | 24.65 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY | AD1-044
938961 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY | AE1-124
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 0 |  |  | -0.00032 |  |  | 0 |  | 1 | NEWENERGY | AB2-158
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | W4-102
925021 | AB2-158 C | 230 | 345 | 75 | 0 | 61 | 48.97 |  |  | -0.00032 |  |  | 0 |  | 1 | CAPACITY | AB2-158
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | AB2-097
237799 | 01AA2-159 C | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
920562 | AA2-159 E | 34.5 | 201 | 75 | 0 | 7.3 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 0 |  |  | -0.00032 |  |  | 0 |  | 1 | NEWENERGY | AC1-118
314766 | 6LOUISA | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00032 |  |  | 0 |  | 1 | NEWENERGY
314190 | 6WESTMOR | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00032 |  |  | 0 |  | 1 | CAPACITY | AC1-118
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00031 |  |  | 0 |  | 1 | CAPACITY | W4-102
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 2.09 |  |  | -0.00032 |  |  | 0 |  | 1 | CAPACITY
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.88 |  |  | -0.00032 |  |  | 0 |  | 1 | CAPACITY
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0 |  |  | -0.00033 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
923192 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0 |  |  | -0.00033 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0 |  |  | -0.00033 |  |  | 0 |  | 1 | NEWENERGY | AA1-095
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 2.33 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | AA1-095
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 136.49 |  |  | -0.00033 |  |  | 0.08446 |  | 1 | CAPACITY
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.00034 |  |  | 0.08446 |  | 1 | CAPACITY
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.00034 |  |  | 0.08446 |  | 1 | CAPACITY
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 126.85 |  |  | -0.00034 |  |  | 0.08446 |  | 1 | CAPACITY
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.00034 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.00034 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00034 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00034 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 6
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00034 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00034 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 5
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00034 |  |  | 0.08446 |  | 1 | CAPACITY
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00034 |  |  | 0.08446 |  | 1 | CAPACITY
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00034 |  |  | 0.08446 |  | 1 | CAPACITY
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 61.9 |  |  | -0.00034 |  |  | 0.08446 |  | 1 | CAPACITY
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00033 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00033 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 2
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00034 |  |  | 0 |  | 1 | NEWENERGY | AC2-138
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 19.99 |  |  | -0.00034 |  |  | 0.10478 |  | 1 | CAPACITY
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | South Anna 1
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00033 |  |  | 0 |  | 1 | CAPACITY | South Anna 2
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 19.27 |  |  | -0.00034 |  |  | 0.10478 |  | 1 | CAPACITY
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 6.3 | 5.06 |  |  | -0.00034 |  |  | 0 |  | 1 | CAPACITY | AC2-138
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0 |  |  | -0.00034 |  |  | 0 |  | 1 | NEWENERGY | AA1-092
314172 | 6DUNNSVL | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00034 |  |  | 0 |  | 1 | NEWENERGY
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 6.42 |  |  | -0.00034 |  |  | 0 |  | 1 | CAPACITY | AA1-092
314734 | 6CASHSCORNER | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00035 |  |  | 0 |  | 1 | NEWENERGY
314222 | 6HANOVER | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00035 |  |  | 0 |  | 1 | NEWENERGY
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | AC1-112
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | AB1-027
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | AC2-070
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 8.83 |  |  | -0.00037 |  |  | 0.12623 |  | 1 | CAPACITY
314241 | 6OLDCHRC | 230 | 345 | 75 | 0 | 1.82 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | AB1-027
932501 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 7.39 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | AC2-070
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 3.21 |  |  | -0.00036 |  |  | 0 |  | 1 | CAPACITY
314213 | 3CARVER | 115 | 345 | 75 | 0 | 0 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEW | AC1-107
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00037 |  |  | 0.04435 |  | 1 | NEW | AC1-107
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEW | AC1-107
926785 | AC1-164 E | 0.44 | 345 | 75 | 0 | 99.2 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | AC1-164
316114 | AB2-068 ST | 22 | 345 | 58 | 0 | 492 | 395.01 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316112 | AB2-068 CT1 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00037 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-068
316113 | AB2-068 CT2 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | AB2-068
926784 | AC1-164 C | 0.44 | 345 | 75 | 0 | 220.8 | 177.27 |  |  | -0.00037 |  |  | 0 |  | 1 | NEW | AC1-164
315085 | 1SPRUNCC | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00038 |  |  | 0.10478 |  | 1 | NEW
315086 | 1SPRUNCD | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00038 |  |  | 0.10478 |  | 1 | NEW
314189 | 6PAPERMILL | 230 | 345 | 1 | 12 | 37 | 0 |  |  | -0.00037 |  |  | 0.10478 |  | 1 | ENERGY
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | AC1-065
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 104.93 |  |  | -0.00038 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 7
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 103.25 |  |  | -0.00038 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 8
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 69.05 |  |  | -0.00037 |  |  | 0.10478 |  | 1 | CAPACITY
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 68.97 |  |  | -0.00037 |  |  | 0.10478 |  | 1 | CAPACITY
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 68.72 |  |  | -0.00037 |  |  | 0.10478 |  | 1 | CAPACITY
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 68.64 |  |  | -0.00037 |  |  | 0.10478 |  | 1 | CAPACITY
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 53.15 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 48.17 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7
925863 | AC1-065 C | 0.39 | 345 | 75 | 0 | 41.8 | 33.56 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | AC1-065
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | AC2-137
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | AD2-030
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00038 |  |  | 0 |  | 1 | NEWENERGY | AE1-074
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | AB2-024
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY | AD1-063
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 16.06 |  |  | -0.00037 |  |  | 0.12623 |  | 1 | CAPACITY
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.3 | 13.09 |  |  | -0.00037 |  |  | 0.12623 |  | 1 | CAPACITY
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 11.96 |  |  | -0.00038 |  |  | 0.12623 |  | 1 | CAPACITY
938551 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00038 |  |  | 0 |  | 1 | CAPACITY | AE1-074
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | AD2-030
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 11.4 | 9.15 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | AC2-137
314375 | 6CORRCTN | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | AB2-024
314187 | 3WAN 176 | 115 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY
934391 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY | AD1-063
314176 | 6HARMONY | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00037 |  |  | 0 |  | 1 | NEWENERGY
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 4.98 |  |  | -0.00037 |  |  | 0 |  | 1 | CAPACITY
314294 | 6ENON | 230 | 345 | 75 | 0 | 0.23 | 0 |  |  | -0.00038 |  |  | 0 |  | 1 | NEWENERGY
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | ENERGY
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 106.94 |  |  | -0.00039 |  |  | 0.07484 |  | 1 | CAPACITY
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 101.16 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00039 |  |  | 0.04435 |  | 1 | CAPACITY | HOPEWELL HCF
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
208904 | HOLT 696 | 13.2 | 229 | 60 | 23 | 58.4 | 46.89 |  |  | -0.00039 |  |  | 0.07484 |  | 1 | CAPACITY
208903 | HOLT 695 | 13.2 | 229 | 60 | 26 | 53.2 | 42.71 |  |  | -0.00039 |  |  | 0.07484 |  | 1 | CAPACITY
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
919535 | V4-027 E | 0 | 229 | 75 | 0 | 3.1 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY | V4-027
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 3.93 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | V4-027
208474 | KINZ 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY
314177 | 3HAYES89 | 115 | 345 | 75 | 0 | 0.31 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY
313828 | 3WHITEMARSH | 115 | 345 | 75 | 0 | 0.05 | 0 |  |  | -0.00038 |  |  | 0 |  | 1 | NEWENERGY
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 788.9 | 633.38 |  |  | -0.00039 |  |  | 0.10478 |  | 1 | CAPACITY
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 422.86 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AB2-134
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00039 |  |  | 0.04435 |  | 1 | CAPACITY | WARREN COUNTY CC
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AB2-160
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY | AB2-190
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 89.92 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | AB2-190
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 57.65 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AB2-134
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 24.41 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AB2-160
316158 | AD2-164 | 230 | 345 | 57 | 0 | 26.7 | 21.44 |  |  | -0.0004 |  |  | 0.08446 |  | 1 | CAPACITY
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 12.04 |  |  | -0.00039 |  |  | 0.12623 |  | 1 | CAPACITY
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 8.03 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 3.61 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY
313812 | 6ROCKLANDING | 230 | 345 | 75 | 0 | 0.11 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 678.09 |  |  | -0.0004 |  |  | 0.01494 |  | 1 | CAPACITY
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 677.21 |  |  | -0.0004 |  |  | 0.01494 |  | 1 | CAPACITY
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AB2-161
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 69.77 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 69.69 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
314331 | 6POE | 230 | 345 | 75 | 0 | 12.27 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.0004 |  |  | 0 |  | 1 | NEWENERGY | AD1-060
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AE1-162
935212 | AD1-156 E | 230 | 345 | 75 | 0 | 7.92 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AD1-156
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 23.76 |  |  | -0.0004 |  |  | 0.10478 |  | 1 | CAPACITY
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AB2-161
316258 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AE1-162
935211 | AD1-156 C | 230 | 345 | 75 | 0 | 11.82 | 9.49 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AD1-156
314533 | 6SMITFLD | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
934362 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 4.58 |  |  | -0.0004 |  |  | 0 |  | 1 | CAPACITY | AD1-060
314453 | 6CHRHLND | 230 | 345 | 75 | 0 | 0.08 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | AA1-139
314525 | 6KINGFORK | 230 | 345 | 75 | 0 | 24.3 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
314550 | 6HICKORY | 230 | 345 | 75 | 0 | 22.93 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 88.96 |  |  | -0.00041 |  |  | 0.10478 |  | 1 | CAPACITY
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 87.83 |  |  | -0.00041 |  |  | 0.10478 |  | 1 | CAPACITY
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 86.31 |  |  | -0.00041 |  |  | 0.10478 |  | 1 | CAPACITY
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 63.18 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | AA1-139
314466 | 6FENTRES | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
314632 | 6AYDLETOLD | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY
313717 | 6SLIGO L2192 | 230 | 345 | 75 | 0 | 12.34 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | Z1-068
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AC1-147
316145 | AE1-027 E | 230 | 345 | 75 | 0 | 6.9 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AE1-027
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AC2-196
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AC1-027
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AB2-026
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | Z2-030
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | AC2-174
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AE1-075
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AD1-144
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AD2-215
316147 | AE1-028 E | 230 | 345 | 75 | 0 | 4.4 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | AE1-028
314333 | 6POWHATN | 230 | 345 | 75 | 0 | 3.97 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AB2-026
933571 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEW | AC2-174
314645 | 6SLIGO L269 | 230 | 345 | 75 | 0 | 3.22 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 12.2 |  |  | -0.00041 |  |  | 0.10478 |  | 1 | CAPACITY
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 12.04 |  |  | -0.00042 |  |  | 0.12623 |  | 1 | CAPACITY
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 11.96 |  |  | -0.00041 |  |  | 0.10478 |  | 1 | CAPACITY
316144 | AE1-027 C | 230 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AE1-027
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 10.36 |  |  | -0.00041 |  |  | 0.10478 |  | 1 | CAPACITY
926661 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 10.12 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AC1-147
938561 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AE1-075
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 9.55 |  |  | -0.00041 |  |  | 0.10478 |  | 1 | CAPACITY
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 9.05 |  |  | -0.00041 |  |  | 0.12623 |  | 1 | CAPACITY
933731 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 8.03 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AC2-196
316150 | AD2-215 C | 230 | 345 | 76 | 0 | 9.8 | 7.87 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AD2-215
935111 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 7.79 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AD1-144
314491 | 3PENDLTN | 115 | 345 | 75 | 0 | 1.89 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AC1-027
316146 | AE1-028 C | 230 | 345 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | AE1-028
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | Z2-030
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.2 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | Z1-068
314640 | 6KITTY HAWK | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY
314487 | 3MCLAUGH | 115 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY
901082 | W1-029 E | 230 | 345 | 74 | 0 | 261 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY | W1-029
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | Y1-086
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY | W1-029
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | AB2-022
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY | Z2-027
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 10.44 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | AB2-022
314648 | 6SUNBURY | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 3.93 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY
314638 | 6ELIZ CT | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | Y1-086
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 1.61 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY
314639 | 6TANGLEW | 230 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY | Z2-027
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.56 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 0 |  |  | -0.00044 |  |  | 0 |  | 1 | NEWENERGY | Z1-036
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00044 |  |  | 0 |  | 1 | CAPACITY | Z1-036
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00044 |  |  | 0 |  | 1 | NEWENERGY | AB2-025
314651 | 6WINFALL | 230 | 345 | 75 | 0 | 3.35 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY
314435 | 6SAPONY | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00044 |  |  | 0 |  | 1 | CAPACITY | AB2-025
942852 | AE2-304 E | 230 | 345 | 75 | 0 | 1.4 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY | AE2-304
942851 | AE2-304 C | 230 | 345 | 75 | 0 | 3.3 | 2.65 |  |  | -0.00043 |  |  | 0 |  | 1 | CAPACITY | AE2-304
314662 | 6S HERTFORD | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00043 |  |  | 0 |  | 1 | NEWENERGY
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 480.11 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00045 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-086
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | Z1-086
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 0 |  |  | -0.00045 |  |  | 0 |  | 1 | NEW | AB2-015
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 0 |  |  | -0.00045 |  |  | 0 |  | 1 | NEWENERGY | AB2-015
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | -0.00045 |  |  | 0.10478 |  | 1 | ENERGY
314637 | 6EDENTON | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00044 |  |  | 0 |  | 1 | NEWENERGY | AA2-059
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 452.01 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00045 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00045 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY | AA2-178
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | AA2-178
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00045 |  |  | 0.10478 |  | 1 | CAPACITY
314541 | 3WATKINS | 115 | 345 | 1 | 0 | 4 | 0 |  |  | -0.00045 |  |  | 0 |  | 1 | ENERGY
314566 | 3CRESWEL | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 322.35 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AA2-088
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 198.31 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00046 |  |  | 0.04435 |  | 1 | CAPACITY | BEAR GARDEN
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00046 |  |  | 0.04435 |  | 1 | CAPACITY | FLUVANNA
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00046 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 2
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 1
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AB1-128
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AB1-127
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AC1-116
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 30.51 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AA2-088
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AB2-100 2
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AB2-100 1
235041 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AB1-128
235040 | 01AB1-127 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AB1-127
926451 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 3.77 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AC1-116
314594 | 6PLYMOTH | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00046 |  |  | 0 |  | 1 | NEWENERGY
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AA1-065
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 53.6 | 43.03 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | AA1-065
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 40.14 |  |  | -0.00048 |  |  | 0.19858 |  | 1 | CAPACITY
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AC2-071
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | AB2-045
314589 | 3MURPHYS | 115 | 345 | 75 | 0 | 4.66 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | V4-068
932511 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AC2-071
314617 | 3TUNIS | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
314677 | 6BUCKING | 230 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | AB2-045
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY | V4-068
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AB2-099
314620 | 6CASHIE | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00047 |  |  | 0 |  | 1 | NEWENERGY
314551 | 3AHOSKIE | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | AB2-099
313826 | 6HYDRAULIC | 230 | 345 | 75 | 0 | 0.04 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
923262 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
923991 | AB2-040 C O1 | 115 | 345 | 75 | 0 | 44 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEW | AB2-040
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AB2-174
923992 | AB2-040 E O1 | 115 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AB2-040
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY | AA1-063A
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.00049 |  |  | 0.07484 |  | 1 | CAPACITY
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.00049 |  |  | 0.07484 |  | 1 | CAPACITY
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 40.87 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | AA1-063A
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 33.72 |  |  | -0.00048 |  |  | 0 |  | 1 | CAPACITY | AB2-174
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 32.44 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AB1-173
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AB1-173
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEW
314266 | 6NORTHAMPTON | 230 | 345 | 75 | 0 | 2.47 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
314568 | 3EARLEYS | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
314626 | 3WOODLND | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
314604 | 3SEABORD | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00048 |  |  | 0 |  | 1 | NEWENERGY
314762 | 3JAMES R | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.5 | 354.46 |  |  | -0.00049 |  |  | 0.10478 |  | 1 | CAPACITY
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 350.93 |  |  | -0.00049 |  |  | 0.10478 |  | 1 | CAPACITY
925122 | AB2-169 E | 115 | 345 | 75 | 0 | 35 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AB2-169
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AA2-053
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | AD1-085
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 76.6 | 61.5 |  |  | -0.00049 |  |  | 0.04435 |  | 1 | CAPACITY | ROSEMARY
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 44 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AA2-053
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 40.38 |  |  | -0.00049 |  |  | 0.07484 |  | 1 | CAPACITY
314807 | 3MT JACK | 115 | 345 | 75 | 0 | 9.7 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 38.54 |  |  | -0.00049 |  |  | 0.07484 |  | 1 | CAPACITY
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 47.5 | 38.13 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
925121 | AB2-169 C | 115 | 345 | 75 | 0 | 39 | 31.31 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AB2-169
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 35.9 | 28.82 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | AC2-074
314578 | 3HORNRTN | 115 | 345 | 75 | 0 | 5.15 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY
314579 | 6HORNRTN | 230 | 345 | 75 | 0 | 3.91 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 9.88 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | AD1-085
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 8.83 |  |  | -0.00049 |  |  | 0.12623 |  | 1 | CAPACITY
932541 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | AC2-074
314559 | 3CAROLNA | 115 | 345 | 75 | 0 | 1.21 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
314596 | 3POPLR C | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY
314582 | 3KELFORD | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | Z2-043
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 1.04 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.64 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY
314713 | 3PAMPLIN | 115 | 345 | 75 | 0 | 9.73 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY
316143 | AD1-160 E | 115 | 345 | 75 | 0 | 9.1 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | AD1-160
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | AD1-157
313853 | 3PONTONDP | 115 | 345 | 2 | 0 | 4 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | ENERGY
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 16 | 12.85 |  |  | -0.0005 |  |  | 0.12623 |  | 1 | CAPACITY
314603 | 3SCOT NK | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY
935221 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | AD1-157
316142 | AD1-160 C | 115 | 345 | 75 | 0 | 6.6 | 5.3 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | AD1-160
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AC1-054
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY | AC1-036
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 35.73 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | AC1-054
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00051 |  |  | 0.08446 |  | 1 | CAPACITY
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00051 |  |  | 0.08446 |  | 1 | CAPACITY
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY | AE1-098
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY | AE1-099
314593 | 3PARMELE | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | AE1-099
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | AE1-098
925611 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 6.9 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | AC1-036
314629 | 3MARTNCO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY
314798 | 3MERCK5 | 115 | 345 | 75 | 0 | 0.16 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AB2-043
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AB2-060
919702 | AA2-057 E OP | 115 | 345 | 75 | 0 | 21.1 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY | AA2-057
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 43.67 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | AB2-060
313719 | 3CHESTNUT | 115 | 345 | 75 | 0 | 44.7 | 35.89 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | AA2-057
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY | AB2-078
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY | AB2-079
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY | AB2-077
314574 | 6EVERETS | 230 | 345 | 75 | 0 | 5.89 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | AA1-067
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 15.17 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | AB2-043
924311 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00053 |  |  | 0 |  | 1 | NEW | AB2-078
924301 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00053 |  |  | 0 |  | 1 | NEW | AB2-077
924321 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00053 |  |  | 0 |  | 1 | NEW | AB2-079
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY | Z2-088
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 53 | 42.55 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | Z2-088
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
314608 | 3TARBORO | 115 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY | Z2-044
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 12.04 |  |  | -0.00053 |  |  | 0.07484 |  | 1 | CAPACITY
314623 | 3WITAKRS | 115 | 345 | 75 | 0 | 2.51 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | Z2-044
314557 | 3BETHELC | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY
314549 | 3TOT1 | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY
314607 | 3TAR RVR | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY
314545 | 3TOT5 | 115 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY
314560 | 3CNETO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY | AB2-059
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY | AB1-081
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 52.99 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | AB2-059
922922 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | AB1-081
314554 | 3BTLEBRO | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY
314205 | 3HEARTS | 115 | 345 | 75 | 0 | 0.41 | 0 |  |  | -0.00054 |  |  | 0 |  | 1 | NEWENERGY
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 0 |  |  | -0.00055 |  |  | 0 |  | 1 | NEWENERGY | T157
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 0 |  |  | -0.00055 |  |  | 0 |  | 1 | NEWENERGY | AC1-105
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 36.61 |  |  | -0.00055 |  |  | 0.10478 |  | 1 | CAPACITY
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 27.7 |  |  | -0.00055 |  |  | 0 |  | 1 | CAPACITY | AC1-105
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 16.46 |  |  | -0.00055 |  |  | 0 |  | 1 | CAPACITY | T157
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 404.48 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 403.68 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 403.27 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 403.2 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00058 |  |  | 0.0316 |  | 1 | CAPACITY
315616 | AA1-038 C | 230 | 345 | 74 | 0 | 76.6 | 0 |  |  | -0.00057 |  |  | 0 |  | 1 | NEW | AA1-038
918232 | AA1-038 E | 230 | 345 | 74 | 0 | 66.7 | 0 |  |  | -0.00057 |  |  | 0 |  | 1 | NEWENERGY | AA1-038
314860 | 4E MILL | 138 | 345 | 2 | 0 | 50 | 0 |  |  | -0.00057 |  |  | 0.10478 |  | 1 | ENERGY
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 20.23 |  |  | -0.00057 |  |  | 0.10478 |  | 1 | CAPACITY
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 20.15 |  |  | -0.00057 |  |  | 0.10478 |  | 1 | CAPACITY
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00057 |  |  | 0 |  | 1 | CAPACITY
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 0 |  |  | -0.00058 |  |  | 0 |  | 1 | NEWENERGY | K11
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 30.67 |  |  | -0.00058 |  |  | 0 |  | 1 | CAPACITY | K11
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 443.98 |  |  | -0.00059 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM2
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 440.13 |  |  | -0.00059 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 419.81 |  |  | -0.00059 |  |  | 0.10478 |  | 1 | CAPACITY
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 9.55 |  |  | -0.00059 |  |  | 0.08446 |  | 1 | CAPACITY
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 0 |  |  | -0.00062 |  |  | 0 |  | 1 | NEWENERGY | AC1-075
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 30.75 |  |  | -0.00062 |  |  | 0 |  | 1 | CAPACITY | AC1-075
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 0 |  |  | -0.00062 |  |  | 0 |  | 1 | NEWENERGY | AC1-080
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 23.68 |  |  | -0.00062 |  |  | 0.12623 |  | 1 | CAPACITY
926023 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 10.28 |  |  | -0.00062 |  |  | 0 |  | 1 | CAPACITY | AC1-080
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 68.3 |  |  |  | -0.0006
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 91.93 |  |  | -0.00064 |  |  | 0.07484 |  | 1 | CAPACITY
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 61.42 |  |  | -0.00064 |  |  | 0.07484 |  | 1 | CAPACITY
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 77.88 |  |  | -0.00068 |  |  | 0.07484 |  | 1 | CAPACITY
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 51.78 |  |  | -0.00068 |  |  | 0.07484 |  | 1 | CAPACITY
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 51.38 |  |  | -0.00068 |  |  | 0.07484 |  | 1 | CAPACITY
244012 | 05PINNACLE | 4 | 205 | 1 | 0 | 11 | 0 |  |  | -0.00069 |  |  | 0.10478 |  | 1 | ENERGY
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 42.07 |  |  | -0.00068 |  |  | 0.10478 |  | 1 | CAPACITY
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.00069 |  |  | 0.08446 |  | 1 | CAPACITY
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00069 |  |  | 0 |  | 1 | NEWENERGY | AC1-145
926645 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.00069 |  |  | 0 |  | 1 | CAPACITY | AC1-145
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.9 | 40.06 |  |  | -0.0007 |  |  | 0.07484 |  | 1 | CAPACITY
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 1044 |  |  |  | -0.0007
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 154.95 |  |  | -0.00071 |  |  | 0.0316 |  | 1 | CAPACITY
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 152.54 |  |  | -0.00071 |  |  | 0.0316 |  | 1 | CAPACITY
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 97.14 |  |  | -0.00071 |  |  | 0.0316 |  | 1 | CAPACITY
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 59.41 |  |  | -0.00071 |  |  | 0.0316 |  | 1 | CAPACITY
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 57 |  |  | -0.00071 |  |  | 0.0316 |  | 1 | CAPACITY
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 3.21 |  |  | -0.00072 |  |  | 0 |  | 1 | CAPACITY
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | AC1-048
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEW | AC1-048
205910 | AC2-053 E | 0.39 | 227 | 74 | 0 | 12.4 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEWENERGY | AC2-053
205909 | AC2-053 C | 0.39 | 227 | 74 | 0 | 7.6 | 0 |  |  | -0.00074 |  |  | 0 |  | 1 | NEW | AC2-053
208876 | WLAN | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00074 |  |  | 0 |  | 1 | CAPACITY
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 144.51 |  |  | -0.00076 |  |  | 0.10478 |  | 1 | CAPACITY
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00075 |  |  | 0 |  | 1 | NEWENERGY | AC1-117
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | -0.00076 |  |  | 0.05 |  | 1 | MTX | AA1-100
926461 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00075 |  |  | 0 |  | 1 | NEW | AC1-117
208769 | SISO | 12.5 | 229 | 2 | 0 | 2.48 | 0 |  |  | -0.00076 |  |  | 0 |  | 1 | ENERGY
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 6.42 |  |  | -0.00076 |  |  | 0 |  | 1 | CAPACITY
235520 | 01WVACO_S38 | 13.8 | 201 | 2 | 0 | 60 | 0 |  |  | -0.0008 |  |  | 0 |  | 1 | NEW
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00079 |  |  | 0 |  | 1 | NEWENERGY | AD1-018
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.00079 |  |  | 0 |  | 1 | NEW | AD1-018
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00079 |  |  | 0 |  | 1 | CAPACITY | N47
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 0 |  |  | -0.00081 |  |  | 0 |  | 1 | NEWENERGY | U2-073 A
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 0 |  |  | -0.00081 |  |  | 0 |  | 1 | NEWENERGY | U2-073 B
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.0008 |  |  | 0.07484 |  | 1 | CAPACITY
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.0008 |  |  | 0.07484 |  | 1 | CAPACITY
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 25.9 | 20.79 |  |  | -0.00081 |  |  | 0 |  | 1 | CAPACITY | U2-073 A
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00081 |  |  | 0 |  | 1 | CAPACITY | U2-073 B
270148 | AE1-018 E | 138 | 205 | 75 | 0 | 2.2 | 0 |  |  | -0.00081 |  |  | 0 |  | 1 | NEWENERGY | AE1-018
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 3.29 |  |  | -0.00081 |  |  | 0 |  | 1 | CAPACITY
270147 | AE1-018 C | 138 | 205 | 75 | 0 | 2.8 | 2.25 |  |  | -0.00081 |  |  | 0 |  | 1 | CAPACITY | AE1-018
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 0 |  |  | -0.00082 |  |  | 0 |  | 1 | NEWENERGY | S14
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | MTX | AD2-205
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 14.1 | 11.32 |  |  | -0.00083 |  |  | 0.07484 |  | 1 | CAPACITY
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 11.24 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY | S14
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.7 | 7.79 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | NEWENERGY | Y1-006
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | NEWENERGY | U2-030
913034 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 0 |  |  | -0.00083 |  |  | 0 |  | 1 | NEW | Y1-006
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | -0.00083 |  |  | 0.07484 |  | 1 | ENERGY
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 6.26 |  |  | -0.00083 |  |  | 0 |  | 1 | CAPACITY | U2-030
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0 |  |  | -0.00086 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 N
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00086 |  |  | 0 |  | 1 | CAPACITY | AB1-025 N
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00086 |  |  | 0.08446 |  | 1 | CAPACITY
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00086 |  |  | 0.08446 |  | 1 | CAPACITY
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00086 |  |  | 0.08446 |  | 1 | CAPACITY
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00087 |  |  | 0.08446 |  | 1 | CAPACITY
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00087 |  |  | 0.08446 |  | 1 | CAPACITY
242677 | 05INDDRV | 138 | 205 | 64 | 0 | 45 | 36.13 |  |  | -0.00086 |  |  | 0.12623 |  | 1 | CAPACITY
923772 | AB2-011 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00087 |  |  | 0 |  | 1 | NEWENERGY | AB2-011
923761 | AB2-010 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00087 |  |  | 0 |  | 1 | NEW | AB2-010
923762 | AB2-010 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00087 |  |  | 0 |  | 1 | NEWENERGY | AB2-010
923771 | AB2-011 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00087 |  |  | 0 |  | 1 | NEW | AB2-011
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  |  |  | -0.0009
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 489.98 |  |  | -0.00088 |  |  | 0.10478 |  | 1 | CAPACITY
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 127.4 | 102.28 |  |  | -0.00088 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 101.08 |  |  | -0.00088 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 106.7 | 85.67 |  |  | -0.00088 |  |  | 0 |  | 1 | CAPACITY
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 84.78 |  |  | -0.00088 |  |  | 0 |  | 1 | CAPACITY
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  |  |  | -0.0009
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 38 |  |  |  | -0.0009
903052 | W2-094 E | 115 | 227 | 75 | 0 | 1.9 | 0 |  |  | -0.00089 |  |  | 0 |  | 1 | NEWENERGY | W2-094
205911 | 27W2-094 | 115 | 227 | 75 | 0 | 1.1 | 0 |  |  | -0.00089 |  |  | 0 |  | 1 | NEWENERGY | W2-094
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 0 |  |  | -0.0009 |  |  | 0 |  | 1 | NEWENERGY | K28
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 0 |  |  | -0.0009 |  |  | 0 |  | 1 | NEWENERGY | K28
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0 |  |  | -0.0009 |  |  | 0 |  | 1 | NEWENERGY | W2-056
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.4 | 13.97 |  |  | -0.0009 |  |  | 0 |  | 1 | CAPACITY | K28
209030 | FRFA O01 | 12.5 | 229 | 2 | 0 | 3.2 | 0 |  |  | -0.00091 |  |  | 0 |  | 1 | NEW
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 3.36 |  |  | -0.0009 |  |  | 0 |  | 1 | CAPACITY | W2-056
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 1.3 | 1.04 |  |  | -0.0009 |  |  | 0 |  | 1 | CAPACITY
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 0.4 | 0.32 |  |  | -0.00091 |  |  | 0 |  | 1 | CAPACITY | V3-051
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 896 |  |  |  | -0.0009
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 64.23 |  |  | -0.00092 |  |  | 0.07484 |  | 1 | CAPACITY
342442 | 2W GLASGOW | 69 | 320 | 2 | 0 | 1 | 0.8 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 180.64 |  |  | -0.00092 |  |  | 0.10478 |  | 1 | CAPACITY
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 93.13 |  |  | -0.00092 |  |  | 0.10478 |  | 1 | CAPACITY
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 56.2 |  |  | -0.00092 |  |  | 0.07484 |  | 1 | CAPACITY
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00092 |  |  | 0.07484 |  | 1 | CAPACITY
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00093 |  |  | 0.07484 |  | 1 | CAPACITY
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY
342070 | 2PINE GROVE | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00092 |  |  | 0 |  | 1 | CAPACITY
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | M24
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 0 |  |  | -0.00093 |  |  | 0 |  | 1 | NEWENERGY | AB1-150
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | -0.00093 |  |  | 0.05 |  | 1 | MTX | M24 BAT
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | M24
931011 | AB1-150 C | 138 | 201 | 74 | 0 | 6.7 | 5.38 |  |  | -0.00093 |  |  | 0 |  | 1 | CAPACITY | AB1-150
918472 | AA1-062 E | 138 | 201 | 74 | 0 | 195 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | NEWENERGY | AA1-062
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | NEWENERGY | P59
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 244.87 |  |  | -0.00094 |  |  | 0.10478 |  | 1 | CAPACITY
247225 | 05FTHLG2 | 18 | 205 | 57 | 120 | 173.8 | 139.54 |  |  | -0.00094 |  |  | 0.08446 |  | 1 | CAPACITY
247224 | 05FTHLG1 | 18 | 205 | 57 | 120 | 173.7 | 139.46 |  |  | -0.00094 |  |  | 0.08446 |  | 1 | CAPACITY
247230 | 05RIVRG1 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00094 |  |  | 0.08446 |  | 1 | CAPACITY
247231 | 05RIVRG2 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00094 |  |  | 0.08446 |  | 1 | CAPACITY
247232 | 05RIVRG3 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00094 |  |  | 0.08446 |  | 1 | CAPACITY
292981 | N-007 E | 138 | 201 | 74 | 0 | 30.4 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | NEWENERGY | N07
235801 | 01WM_AA1_062 | 138 | 201 | 74 | 0 | 29 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | NEW | AA1-062
920072 | AA2-103 E | 138 | 201 | 76 | -20 | 20 | 0 |  |  | -0.00095 |  |  | 0.05 |  | 1 | MTX | AA2-103
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
925972 | AC1-073 E | 138 | 201 | 74 | 0 | 5.9 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | NEWENERGY | AC1-073
925971 | AC1-073 C | 138 | 201 | 74 | 0 | 5.8 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | NEW | AC1-073
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 9.39 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | P59
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | K19
235000 | N-007 C | 138 | 201 | 74 | 0 | 7.6 | 6.1 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | N07
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.55 |  |  | -0.00094 |  |  | 0 |  | 1 | CAPACITY
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1067.8 |  |  | -0.00095 |  |  | 0.10478 |  | 1 | CAPACITY | AMG3
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  |  |  | -0.001
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 642.29 |  |  | -0.00095 |  |  | 0.10478 |  | 1 | CAPACITY
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 642.29 |  |  | -0.00095 |  |  | 0.10478 |  | 1 | CAPACITY
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | NEWENERGY | U2-061
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00095 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00095 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 2
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 109.5 | 87.91 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 60.94 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 60.78 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 60.7 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 60.53 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 72.9 | 58.53 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 72.6 | 58.29 |  |  | -0.00095 |  |  | 0.08446 |  | 1 | CAPACITY
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | -0.001
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 11.88 |  |  | -0.00095 |  |  | 0.07484 |  | 1 | CAPACITY
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | -0.00095 |  |  | 0 |  | 1 | MTX | AB1-055
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 5.22 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY | U2-061
341329 | 2COLESBURG | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00095 |  |  | 0 |  | 1 | CAPACITY
342031 | 2PACTOLUS | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00096 |  |  | 0 |  | 1 | CAPACITY
237085 | AD2-192 GEN | 23 | 201 | 57 | 0 | 600 | 0 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | NEW
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 62.8 |  |  |  | -0.001
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 55 | 44.16 |  |  | -0.00096 |  |  | 0.10478 |  | 1 | CAPACITY
341200 | 2BROMLEYEK | 69 | 320 | 2 | 0 | 2 | 1.61 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY
293798 | W4-005 E | 0.69 | 222 | 74 | 0 | 305.37 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | NEWENERGY | W4-005
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1396 | 1120.79 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY | GVG2
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1371 | 1100.72 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY | GVG1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1088.67 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY | RKG1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1356 | 1088.67 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | MTG1
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1043.71 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY | RKG2
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | NEWENERGY | X2-022
274663 | QUAD CITI;2U | 18 | 222 | 48 | 150 | 911.7 | 731.97 |  |  | -0.00097 |  |  | 0.01494 |  | 1 | CAPACITY
274662 | QUAD CITI;1U | 18 | 222 | 48 | 150 | 911.1 | 731.48 |  |  | -0.00097 |  |  | 0.01494 |  | 1 | CAPACITY
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | S27
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | S28
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 570.03 |  |  | -0.00097 |  |  | 0.10478 |  | 1 | CAPACITY
235586 | 01HARRN2 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
235587 | 01HARRN3 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
235585 | 01HARRN1 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 124 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | ENERGY | L05_CE22
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 443.18 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 437.96 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | P36 2
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | P36 1
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | O29 1
293516 | O-009 E1 | 0.69 | 222 | 74 | 0 | 82.04 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | O09 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | P11 2
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | P11 1
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 0 |  |  | -0.00097 |  |  | 0 |  | 1 | NEWENERGY | W2-048
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 240.86 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | O29 2
293518 | O-009 E3 | 0.57 | 222 | 74 | 0 | 45.89 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | O09 3
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | O29 3
293517 | O-009 E2 | 0.6 | 222 | 74 | 0 | 41.67 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | O09 2
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 144.51 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 136.16 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | NELSON
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 135.12 |  |  | -0.00098 |  |  | 0.04435 |  | 1 | CAPACITY | NELSON
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 134.32 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 134.16 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00097 |  |  | 0.04435 |  | 1 | CAPACITY | CORDOVA
919221 | AA1-146 | 345 | 222 | 58 | 0 | 157 | 126.05 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | CLIF4
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF2
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | CLIF1
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | CLIF5
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | CLIF6
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | CLIF3
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 99.47 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | NELSON
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 98.59 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | NELSON
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | NQ72
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 67.52 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | CLIF2
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF6
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF3
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF1
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF5
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF4
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 52.91 |  |  | -0.00097 |  |  | 0.07484 |  | 1 | CAPACITY
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 36.93 |  |  | -0.00098 |  |  | 0.07484 |  | 1 | CAPACITY
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 36.61 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | W4-005
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 28.74 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | S28
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 27.94 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | S27
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | L05_CE22
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | O29 1
293513 | O-009 C1 | 0.69 | 222 | 74 | 0 | 20.5 | 16.46 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | O09 1
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | P11 1
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | P11 2
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 19.5 | 15.66 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | P36 1
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | P36 2
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 9.64 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | O29 2
293515 | O-009 C3 | 0.57 | 222 | 74 | 0 | 11.5 | 9.23 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | O09 3
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 8.91 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | O29 3
293514 | O-009 C2 | 0.6 | 222 | 74 | 0 | 10.4 | 8.35 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | O09 2
342550 | 4BAVARIAN LF | 138 | 320 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY
341584 | 2GRIFFIN | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY
295110 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 2.57 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | NQ72
274656 | BYRON ;1U | 25 | 222 | 45 | 700 | 1168.5 | 938.14 |  |  | -0.00098 |  |  | 0.01494 |  | 1 | CAPACITY
274657 | BYRON ;2U | 25 | 222 | 45 | 700 | 1141.5 | 916.46 |  |  | -0.00098 |  |  | 0.01494 |  | 1 | CAPACITY
274661 | LASCO STA;2U | 25 | 222 | 49 | 150 | 1135.9 | 911.97 |  |  | -0.00099 |  |  | 0.01494 |  | 1 | CAPACITY
274660 | LASCO STA;1U | 25 | 222 | 49 | 150 | 1131.2 | 908.19 |  |  | -0.00099 |  |  | 0.01494 |  | 1 | CAPACITY
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 200 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | Q57
274658 | DRESDEN ;2U | 18 | 222 | 48 | 150 | 902.5 | 724.58 |  |  | -0.00099 |  |  | 0.01494 |  | 1 | CAPACITY
274659 | DRESDEN ;3U | 18 | 222 | 48 | 150 | 895.5 | 718.96 |  |  | -0.00099 |  |  | 0.01494 |  | 1 | CAPACITY
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | Z2-087
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | O50
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | Q01 3
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | O22 2
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | P10
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 589.3 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | ZIMM
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | AA1-018
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | Q01 4
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | O51 1
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | O51 2
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | N15
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 470.47 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | ZIMM
927091 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-204
927093 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | AC1-204
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 415.88 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 415.88 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 409.46 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
274687 | WILL CNTY;4U | 20 | 222 | 15 | 0 | 510 | 409.46 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | WILL4
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | AC1-089
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | P26
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | Q01 21
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 81.6 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | O22 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | P46
247903 | 05FR-22G E | 0.69 | 205 | 75 | 0 | 78.8 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | Q01 22
247900 | 05FR-11G E | 0.6 | 205 | 75 | 0 | 78.3 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | Q01 11
930062 | AB1-014 E | 138 | 212 | 75 | 0 | 77.5 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | AB1-014
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 522.66 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | Q01 12
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 284.53 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK8
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 263.34 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK7
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-169
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | AB1-169
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | O35
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 294 | 236.04 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-079
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 225.6 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | NQ71
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 45.5 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | Z1-073
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | AB1-169
916211 | Z1-072 E | 0.6 | 222 | 74 | 0 | 44.8 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | NEWENERGY | Z1-072
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 219 | 175.82 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Z1-079
274708 | KENDALL ;3C | 18 | 222 | 58 | 140 | 184.3 | 147.97 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 3
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 146.36 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 1
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 146.36 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 2
274710 | KENDALL ;4C | 18 | 222 | 58 | 138 | 182.3 | 146.36 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 4
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 1
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 2
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 132.47 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 31.5 |  |  |  | -0.001
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | ENERGY
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 99.72 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | KYG1
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | KYG2
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | KYG4
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | KYG3
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | KYG5
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 97.87 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Kendall 1
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 97.87 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Kendall 2
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 97.87 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Kendall 3
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 97.87 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Kendall 4
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 96.42 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 115.4 | 92.65 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | EQUISTAR MORRIS
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 75.6 | 104 | 83.5 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 72.7 | 101.6 | 81.57 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00098 |  |  | 0.05 |  | 1 | MTX | AA2-123
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00098 |  |  | 0.05 |  | 1 | MTX | Z1-108
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00099 |  |  | 0.05 |  | 1 | MTX | Z1-107
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 80.93 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 71.2 | 100.6 | 80.77 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 133.1 | 153 | 133.28 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 129.7 | 149.1 | 129.88 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 128.6 | 147.8 | 128.75 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 65.51 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 81.5 | 65.43 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.8 | 64.87 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 64.31 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 62.14 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
250166 | HLCRST AB114 | 138 | 212 | 75 | 0 | 76 | 61.02 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | AB1-014
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 58.77 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 58.45 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | KYG1
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | KYG3
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | KYG4
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00098 |  |  | 0.10478 |  | 1 | CAPACITY | KYG2
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | KYG5
251957 | 08MADSN6 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251959 | 08MADSN8 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251955 | 08MADSN4 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251956 | 08MADSN5 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251958 | 08MADSN7 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251952 | 08MADSN1 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251953 | 08MADSN2 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251954 | 08MADSN3 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 55.4 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251828 | CLNTESP1 | 34.5 | 212 | 76 | 0 | 12 | 0 |  |  | -0.00099 |  |  | 0.05 |  | 1 | MTX | Z1-080
926103 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 45.76 |  |  | -0.00098 |  |  | 0.05 |  | 1 | NEW | AC1-089
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00099 |  |  | 0.05 |  | 1 | MTX | Z1-106
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00099 |  |  | 0.05 |  | 1 | MTX | Z1-106
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 40.54 |  |  | -0.00099 |  |  | 0.04435 |  | 1 | CAPACITY | MIDDLETOWN COKE
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | Q57
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | O50
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00098 |  |  | 0.07484 |  | 1 | CAPACITY
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00098 |  |  | 0.07484 |  | 1 | CAPACITY
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00098 |  |  | 0.07484 |  | 1 | CAPACITY
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 28.18 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | O22 2
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -0.00099 |  |  | 0.05 |  | 1 | MTX | Z1-065
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 24.08 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 23.36 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Q01 4
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 20.3 | 27.6 | 22.16 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 22 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | N15
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 21.68 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274889 | BRIGHTSTK;1U | 0.7 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | Z2-087
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 20.63 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Q01 11
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 20.07 |  |  | -0.00098 |  |  | 0.08446 |  | 1 | CAPACITY
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | O51 2
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | O51 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 17.58 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | P26
274891 | OTTER CRK;1U | 0.69 | 222 | 74 | 0 | 19.5 | 15.66 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | AA1-018
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 15.58 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | P46
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 14.77 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | O22 1
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | Z1-073
276173 | Z2-081 | 138 | 222 | 2 | 0 | 13.3 | 10.68 |  |  | -0.00099 |  |  | 0.12623 |  | 1 | CAPACITY
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Q01 22
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Q01 21
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 10.36 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Q01 12
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Q01 3
904211 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 9.71 |  |  | -0.00099 |  |  | 0.07484 |  | 1 | CAPACITY
904201 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 8.51 |  |  | -0.00099 |  |  | 0.07484 |  | 1 | CAPACITY
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 10.3 | 8.27 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | O35
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 8.19 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | P10
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | MTX | Y3-099
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00098 |  |  | 0 |  | 1 | MTX | Y3-100
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 10 | 8.03 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | Z1-072
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.6 | 7.71 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY
295108 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 5.7 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY | NQ71
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00098 |  |  | 0 |  | 1 | CAPACITY
276159 | W4-082 | 138 | 222 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 949.78 |  |  | -0.00099 |  |  | 0.01494 |  | 1 | CAPACITY
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 926.5 |  |  | -0.00099 |  |  | 0.01494 |  | 1 | CAPACITY
930042 | AB1-006 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | AB1-006
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | U3-002 2
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | U2-090
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | V3-007
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 159.7 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | S06
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | S37
293799 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | S36
253314 | AC1-085 A_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 A
253317 | AC1-085 B_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 B
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | S71
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | T126 2
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | T126 3
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | T127 4
247943 | T-127 E | 0.74 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | T127 5
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 131.75 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 130.06 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
276592 | O-012 C | 138 | 222 | 64 | 0 | 20 | 0 |  |  | -0.00099 |  |  | 0.12623 |  | 1 | ENERGY
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 80.21 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
243415 | 05WWVSTA | 69 | 205 | 61 | 60 | 96 | 77.08 |  |  | -0.00099 |  |  | 0.07484 |  | 1 | CAPACITY
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 64.23 |  |  | -0.00099 |  |  | 0.10478 |  | 1 | CAPACITY
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | AC1-085 B
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | AC1-085 A
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 56.84 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 43.03 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 37.49 |  |  | -0.00099 |  |  | 0.07484 |  | 1 | CAPACITY
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | S37
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | S36
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 42.68 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 42.6 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 42.51 |  |  | -0.00099 |  |  | 0.08446 |  | 1 | CAPACITY
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | X3-005
930041 | AB1-006 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | AB1-006
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | U2-090
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | V3-007
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 20.79 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | S06
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 19.27 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | S71
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 16.22 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | T127 5
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 12.28 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | T126 3
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | T126 2
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 10.6 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | U3-002 1
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 10.28 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | U3-002 2
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 9.47 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | T127 4
247968 | Z2-115 E | 12 | 205 | 74 | 0 | 1.25 | 0 |  |  | -0.00099 |  |  | 0 |  | 1 | NEWENERGY | Z2-115
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 2.73 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | X3-005
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.76 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 1 |  |  | -0.00099 |  |  | 0 |  | 1 | CAPACITY | Z2-115
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1402 |  |  |  | -0.001
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1148 | 921.68 |  |  | -0.001 |  |  | 0.01494 |  | 1 | CAPACITY
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | AC2-176
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 268.96 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 201.52 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | X2-052
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 193.49 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.001 |  |  | 0.04435 |  | 1 | CAPACITY | X2-052
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | X2-052
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 162.9 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | AC2-067
902531 | W2-040 C | 69 | 209 | 75 | 0 | 20 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEW | W2-040
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 80.69 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | AC1-165
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | AC1-166
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | AC1-068
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | AC1-069
902532 | W2-040 E | 69 | 209 | 75 | 0 | 12.4 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | W2-040
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 60 | 48.17 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 48.09 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 47.93 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 46.65 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 46.41 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | AC1-068
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | AC1-069
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | AC1-165
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | AC1-166
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 21.28 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AC2-067
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 22.91 |  |  | -0.001 |  |  | 0.08446 |  | 1 | CAPACITY
933594 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 13.57 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | AC2-176
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.001 |  |  | 0.12623 |  | 1 | CAPACITY
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 8.03 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0 |  |  | -0.001 |  |  | 0 |  | 1 | NEWENERGY | V4-073
247969 | Z2-116 E | 138 | 205 | 76 | 0 | 1.3 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Z2-116
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 3.13 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.8 | 2.25 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 2.09 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Z2-116
904721 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.76 |  |  | -0.001 |  |  | 0 |  | 1 | CAPACITY | V4-073
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 814.5 |  |  | -0.00101 |  |  | 0.01494 |  | 1 | CAPACITY
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00101 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-116
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | AA2-116
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 267.35 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | AA2-116
927184 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -0.00102 |  |  | 0.05 |  | 1 | MTX | AC1-212
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 65.03 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 64.23 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 63.43 |  |  | -0.00101 |  |  | 0.08446 |  | 1 | CAPACITY
932312 | AC2-045 E | 69 | 205 | 75 | 0 | 6.2 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | AC2-045
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00102 |  |  | 0.07484 |  | 1 | CAPACITY
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00102 |  |  | 0.07484 |  | 1 | CAPACITY
932311 | AC2-045 C | 69 | 205 | 75 | 0 | 3.8 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEW | AC2-045
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00102 |  |  | 0.12623 |  | 1 | CAPACITY
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0 |  |  | -0.00101 |  |  | 0 |  | 1 | NEWENERGY | Z2-113
AC1-212 | BATTERY_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | -0.001
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 4.82 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY
247604 | X1-042 | 12 | 205 | 64 | 0 | 3 | 2.41 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 1.85 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY | Z2-113
927183 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.53 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | AC1-212
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.5 | 1.2 |  |  | -0.00101 |  |  | 0 |  | 1 | CAPACITY
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 120.8 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | R49
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | T131
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 0 |  |  | -0.00102 |  |  | 0 |  | 1 | NEWENERGY | AC1-173
247528 | 05COVRT1 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00102 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 1
247530 | 05COVRT3 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00102 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 3
247529 | 05COVRT2 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00102 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 2
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00102 |  |  | 0.08446 |  | 1 | CAPACITY
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 120.19 |  |  | -0.00103 |  |  | 0.08446 |  | 1 | CAPACITY
247533 | 05COVRT6 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | Covert 3
247531 | 05COVRT4 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | Covert 1
247532 | 05COVRT5 | 16.5 | 205 | 58 | 90 | 131.2 | 105.33 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | Covert 2
247521 | T131 | 0.69 | 205 | 74 | 22.4 | 30 | 24.08 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | T131
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 18.39 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | R49
294740 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | ENERGY
926865 | AC1-173 C | 0.65 | 205 | 75 | 0 | 9.9 | 7.95 |  |  | -0.00102 |  |  | 0 |  | 1 | CAPACITY | AC1-173
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEWENERGY | U2-072
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 94.4 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | R60 3
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | R60 2
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | R60 1
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | NEWENERGY | V1-011
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 31.31 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | U2-072
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00103 |  |  | 0 |  | 1 | MTX
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 13.25 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | R60 3
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | R60 2
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | R60 1
247607 | V1-011 C | 34.5 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00103 |  |  | 0 |  | 1 | CAPACITY | V1-011
247919 | U2-041 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEWENERGY | U2-041
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00104 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-044
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00104 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-067
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | AB2-067
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 292.88 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 318.8 | 255.95 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY | RONCO
247506 | U2-041 C | 345 | 205 | 74 | 0 | 39 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | U2-041
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00105 |  |  | 0.04435 |  | 1 | CAPACITY | RONCO
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY | RONCO
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00104 |  |  | 0.04435 |  | 1 | CAPACITY | WATERFORD
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | NEWENERGY | V3-028
247549 | V3-028 C | 345 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00104 |  |  | 0 |  | 1 | CAPACITY | V3-028
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 618.28 |  |  | -0.00105 |  |  | 0.10478 |  | 1 | CAPACITY
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 533.66 |  |  | -0.00105 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-173
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 238.45 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00105 |  |  | 0.04435 |  | 1 | CAPACITY | WASHINGTON
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00105 |  |  | 0 |  | 1 | CAPACITY
245413 | 05S FULTHA | 69 | 205 | 65 | 0 | 0.85 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | ENERGY
893022 | V2-006 E | 138 | 205 | 74 | 0 | 130.5 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | V2-006
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 225.4 | 180.96 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 0 |  |  | -0.00107 |  |  | 0 |  | 1 | NEWENERGY | U1-059
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.00107 |  |  | 0.04435 |  | 1 | CAPACITY | DRESDEN
893021 | V2-006 C | 138 | 205 | 74 | 0 | 19.5 | 0 |  |  | -0.00106 |  |  | 0 |  | 1 | NEWENERGY | V2-006
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 0 |  |  | -0.00107 |  |  | 0 |  | 1 | NEWENERGY | W1-056
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 0 |  |  | -0.00107 |  |  | 0 |  | 1 | NEWENERGY | U1-059
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.93 |  |  | -0.00107 |  |  | 0 |  | 1 | CAPACITY | W1-056
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.00108 |  |  | 0.08446 |  | 1 | CAPACITY
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.00108 |  |  | 0.08446 |  | 1 | CAPACITY
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.66 | 96.07 |  |  | -0.00108 |  |  | 0.08446 |  | 1 | CAPACITY
930262 | AB1-065 E | 34.5 | 201 | 75 | 0 | 6.8 | 0 |  |  | -0.00107 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 17.66 |  |  | -0.00108 |  |  | 0.08446 |  | 1 | CAPACITY
235013 | 01AB1-065 C | 34.5 | 201 | 75 | 0 | 4.1 | 0 |  |  | -0.00107 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 8.83 |  |  | -0.00108 |  |  | 0.10478 |  | 1 | CAPACITY
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00109 |  |  | 0.07484 |  | 1 | CAPACITY
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00109 |  |  | 0.07484 |  | 1 | CAPACITY
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 10.19 |  |  | -0.0011 |  |  | 0.10478 |  | 1 | CAPACITY
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 634.42 |  |  | -0.00111 |  |  | 0.10478 |  | 1 | CAPACITY
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00111 |  |  | 0.08446 |  | 1 | CAPACITY
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00111 |  |  | 0.08446 |  | 1 | CAPACITY
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 15.25 |  |  | -0.0011 |  |  | 0.07484 |  | 1 | CAPACITY
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00112 |  |  | 0 |  | 1 | NEWENERGY | U4-028
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00112 |  |  | 0 |  | 1 | NEWENERGY | U4-029
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 0 |  |  | -0.00112 |  |  | 0 |  | 1 | NEWENERGY
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00112 |  |  | 0 |  | 1 | NEW | U4-028
247552 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00112 |  |  | 0 |  | 1 | NEW | U4-029
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00112 |  |  | 0 |  | 1 | NEWENERGY | V4-010
924440 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 389.39 |  |  | -0.00113 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-093
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 261.89 |  |  | -0.00112 |  |  | 0 |  | 1 | CAPACITY | OREGON
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 248.73 |  |  | -0.00112 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00112 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00112 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-107
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00112 |  |  | 0.04435 |  | 1 | CAPACITY | OREGON
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00112 |  |  | 0 |  | 1 | CAPACITY | OREGON
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00112 |  |  | 0.10478 |  | 1 | CAPACITY
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00112 |  |  | 0.10478 |  | 1 | CAPACITY
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00112 |  |  | 0.08446 |  | 1 | CAPACITY
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00112 |  |  | 0.08446 |  | 1 | CAPACITY
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 109.19 |  |  | -0.00113 |  |  | 0.10478 |  | 1 | CAPACITY
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 0 |  |  | -0.00112 |  |  | 0 |  | 1 | NEW | V4-010
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 10.68 |  |  | -0.00113 |  |  | 0.10478 |  | 1 | CAPACITY
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | -0.00115 |  |  | 0 |  | 1 | NEW | AB1-069
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00115 |  |  | 0.04435 |  | 1 | NEW | AB1-069
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00115 |  |  | 0 |  | 1 | NEW | AB1-069
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 364.2 | 292.4 |  |  | -0.00115 |  |  | 0 |  | 1 | CAPACITY | FREMONT
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 170 | 136.49 |  |  | -0.00115 |  |  | 0.04435 |  | 1 | CAPACITY | FREMONT
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 166.4 | 133.6 |  |  | -0.00115 |  |  | 0 |  | 1 | CAPACITY | FREMONT
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 4.41 |  |  | -0.00114 |  |  | 0 |  | 1 | CAPACITY | N32
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 780.51 |  |  | -0.00115 |  |  | 0.01494 |  | 1 | CAPACITY
936011 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 16.06 |  |  | -0.00118 |  |  | 0.10478 |  | 1 | CAPACITY
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 8.03 |  |  | -0.00117 |  |  | 0 |  | 1 | CAPACITY
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 7.95 |  |  | -0.00117 |  |  | 0 |  | 1 | CAPACITY
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 19.6 | 15.74 |  |  | -0.0012 |  |  | 0.08446 |  | 1 | CAPACITY
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 1.85 |  |  | -0.0012 |  |  | 0 |  | 1 | CAPACITY
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0 |  |  | -0.00121 |  |  | 0 |  | 1 | NEWENERGY | W1-045
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.5 |  |  | -0.00121 |  |  | 0 |  | 1 | CAPACITY
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.13 | 4.12 |  |  | -0.00121 |  |  | 0 |  | 1 | CAPACITY | W1-045
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 498.09 |  |  | -0.00123 |  |  | 0.10478 |  | 1 | CAPACITY
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00122 |  |  | 0.10478 |  | 1 | CAPACITY
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00123 |  |  | 0.10478 |  | 1 | CAPACITY
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 272 | 218.38 |  |  | -0.00123 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00123 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00123 |  |  | 0.04435 |  | 1 | CAPACITY | Y2-050
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 11.24 |  |  | -0.00123 |  |  | 0.12623 |  | 1 | CAPACITY
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00124 |  |  | 0.08446 |  | 1 | CAPACITY
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 41.03 |  |  | -0.00124 |  |  | 0.12623 |  | 1 | CAPACITY
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 39.82 |  |  | -0.00124 |  |  | 0.12623 |  | 1 | CAPACITY
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 62.22 |  |  | -0.00124 |  |  | 0.08446 |  | 1 | CAPACITY
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00124 |  |  | 0.08446 |  | 1 | CAPACITY
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 60.86 |  |  | -0.00124 |  |  | 0.08446 |  | 1 | CAPACITY
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 60.29 |  |  | -0.00124 |  |  | 0.08446 |  | 1 | CAPACITY
237082 | AA2-121 | 345 | 201 | 58 | 0 | 830 | 666.37 |  |  | -0.00126 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-121
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 503.47 |  |  | -0.00127 |  |  | 0.04435 |  | 1 | CAPACITY | AVON LAKE
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 39.5 | 31.71 |  |  | -0.00127 |  |  | 0.08446 |  | 1 | CAPACITY
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 3.21 |  |  | -0.00126 |  |  | 0 |  | 1 | CAPACITY
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 898.96 |  |  | -0.00129 |  |  | 0.01494 |  | 1 | CAPACITY
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00129 |  |  | 0.10478 |  | 1 | CAPACITY
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00129 |  |  | 0.10478 |  | 1 | CAPACITY
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 455.62 |  |  | -0.00129 |  |  | 0.10478 |  | 1 | CAPACITY
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.0013 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.0013 |  |  | 0 |  | 1 | CAPACITY | AA1-123
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 233.87 |  |  | -0.00129 |  |  | 0.10478 |  | 1 | CAPACITY
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.0013 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-123
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.0013 |  |  | 0 |  | 1 | CAPACITY | AA1-123
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 81.57 |  |  | -0.00129 |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND
253970 | 15BI2 | 13.8 | 215 | 58 | 60 | 96.2 | 77.24 |  |  | -0.00129 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.0013 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.0013 |  |  | 0 |  | 1 | CAPACITY | Y3-103
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.7 | 39.1 |  |  | -0.00129 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0 |  |  | -0.00129 |  |  | 0 |  | 1 | NEWENERGY | AC2-168
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 28.1 |  |  | -0.00129 |  |  | 0.10478 |  | 1 | CAPACITY
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.0013 |  |  | 0.04435 |  | 1 | CAPACITY | Y3-103
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.0013 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.0013 |  |  | 0 |  | 1 | CAPACITY | Y3-103
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 21 | 16.86 |  |  | -0.00129 |  |  | 0.12623 |  | 1 | CAPACITY
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 14.53 |  |  | -0.00129 |  |  | 0.08446 |  | 1 | CAPACITY
933531 | AC2-168 C | 138 | 215 | 75 | 0 | 7.55 | 6.06 |  |  | -0.00129 |  |  | 0 |  | 1 | CAPACITY | AC2-168
253900 | 15BVRVL1 | 22 | 215 | 44 | 843.9 | 970 | 844.97 |  |  | -0.0013 |  |  | 0.01494 |  | 1 | CAPACITY
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 783.39 |  |  | -0.0013 |  |  | 0.01494 |  | 1 | CAPACITY
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 300.6 | 241.34 |  |  | -0.00131 |  |  | 0 |  | 1 | CAPACITY | Z2-028
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00131 |  |  | 0 |  | 1 | CAPACITY | Z2-028
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00131 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-028
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | -0.00131 |  |  | 0.10478 |  | 1 | ENERGY
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 24.6 | 19.75 |  |  | -0.00131 |  |  | 0.12623 |  | 1 | CAPACITY
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 329.17 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00133 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-044
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY | AA1-044
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 38.7 | 31.07 |  |  | -0.00133 |  |  | 0.08446 |  | 1 | CAPACITY
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 3.21 |  |  | -0.00133 |  |  | 0 |  | 1 | CAPACITY
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 0 |  |  | -0.00135 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 16.46 |  |  | -0.00134 |  |  | 0.12623 |  | 1 | CAPACITY
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 0 |  |  | -0.00135 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
204555 | 27QUEEN ST | 115 | 227 | 74 | 0 | 5 | 0 |  |  | -0.00135 |  |  | 0 |  | 1 | NEWENERGY
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 261.73 |  |  | -0.00138 |  |  | 0 |  | 1 | CAPACITY | T-174
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00138 |  |  | 0 |  | 1 | CAPACITY | T-174
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00138 |  |  | 0.04435 |  | 1 | CAPACITY | T-174
239024 | 02NWCAG5 | 16.5 | 202 | 58 | 23 | 141 | 113.2 |  |  | -0.00138 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
239023 | 02NWCAG4 | 14.4 | 202 | 58 | 20 | 92 | 73.86 |  |  | -0.00137 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
204638 | 27CAT TRAC | 13.2 | 227 | 58 | 0 | 32.3 | 25.93 |  |  | -0.00138 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
204706 | 27CAT TRC2 | 13.2 | 227 | 58 | 0 | 13.9 | 11.16 |  |  | -0.00138 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 2.01 |  |  | -0.00137 |  |  | 0 |  | 1 | CAPACITY
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 1.37 |  |  | -0.00137 |  |  | 0 |  | 1 | CAPACITY | K20
239022 | 02NWCAG3 | 14.4 | 202 | 58 | 20 | 92.3 | 74.11 |  |  | -0.00138 |  |  | 0.04435 |  | 1 | CAPACITY | NEW CASTLE
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 24.08 |  |  | -0.00142 |  |  | 0.10478 |  | 1 | CAPACITY
920571 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 411.86 |  |  | -0.00143 |  |  | 0.04435 |  | 1 | NEW | AA2-161
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.82 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1086.27 |  |  | -0.00148 |  |  | 0.01494 |  | 1 | CAPACITY
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 3.05 |  |  | -0.00155 |  |  | 0 |  | 1 | CAPACITY
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 353.26 |  |  | -0.00158 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00158 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00158 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-076
913142 | Y1-033 E OP1 | 115 | 226 | 74 | 0 | 34.02 | 0 |  |  | -0.00157 |  |  | 0 |  | 1 | NEWENERGY | Y1-033
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 4.01 |  |  | -0.00157 |  |  | 0 |  | 1 | CAPACITY | Y1-033
213798 | MERCK 3 | 13.8 | 230 | 2 | 13 | 35 | 28.1 |  |  | -0.0016 |  |  | 0 |  | 1 | CAPACITY
213797 | MERCK 2 | 13.8 | 230 | 2 | 4 | 25 | 20.07 |  |  | -0.0016 |  |  | 0 |  | 1 | CAPACITY
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 3.29 |  |  | -0.0016 |  |  | 0 |  | 1 | CAPACITY
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 16.55 |  |  | -0.00164 |  |  | 0.07484 |  | 1 | CAPACITY
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 140 | 182.2 | 146.28 |  |  | -0.00165 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 118.7 | 175.2 | 140.66 |  |  | -0.00166 |  |  | 0.04435 |  | 1 | CAPACITY | AE SPRINGDALE
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 118.7 | 172.2 | 138.25 |  |  | -0.00165 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.00166 |  |  | 0.08446 |  | 1 | CAPACITY
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.00166 |  |  | 0.08446 |  | 1 | CAPACITY
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 5.54 |  |  | -0.00175 |  |  | 0 |  | 1 | CAPACITY
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00179 |  |  | 0 |  | 1 | NEWENERGY | K23
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 0 |  |  | -0.00179 |  |  | 0 |  | 1 | NEWENERGY | L13
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 0 |  |  | -0.00179 |  |  | 0 |  | 1 | NEWENERGY | O48
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | -0.00179 |  |  | 0.05 |  | 1 | MTX
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | -0.00179 |  |  | 0.05 |  | 1 | MTX
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 0 |  |  | -0.00179 |  |  | 0 |  | 1 | NEWENERGY | R40
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 5.06 |  |  | -0.00179 |  |  | 0 |  | 1 | CAPACITY | O48
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 4.74 |  |  | -0.00179 |  |  | 0 |  | 1 | CAPACITY | L13
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 5.1 | 4.09 |  |  | -0.00179 |  |  | 0 |  | 1 | CAPACITY | K23
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 682.91 |  |  | -0.00181 |  |  | 0.10478 |  | 1 | CAPACITY | Cone1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 682.43 |  |  | -0.00181 |  |  | 0.10478 |  | 1 | CAPACITY | Cone2
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 400 | 321.14 |  |  | -0.00183 |  |  | 0.04435 |  | 1 | CAPACITY | AD2-114
235620 | 01SBEND2 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00183 |  |  | 0.08446 |  | 1 | CAPACITY
235621 | 01SBEND3 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00183 |  |  | 0.08446 |  | 1 | CAPACITY
235622 | 01SBEND4 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00183 |  |  | 0.08446 |  | 1 | CAPACITY
235619 | 01SBEND1 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00183 |  |  | 0.08446 |  | 1 | CAPACITY
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 853.3 | 685.08 |  |  | -0.00184 |  |  | 0.10478 |  | 1 | CAPACITY | Keys1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 853.1 | 684.92 |  |  | -0.00184 |  |  | 0.10478 |  | 1 | CAPACITY | Keys2
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 6.1 |  |  | -0.00185 |  |  | 0 |  | 1 | CAPACITY
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00195 |  |  | 0 |  | 1 | CAPACITY
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.45 |  |  | -0.00196 |  |  | 0 |  | 1 | CAPACITY
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.72 |  |  | -0.00196 |  |  | 0 |  | 1 | CAPACITY | K22
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 5.46 |  |  | -0.00197 |  |  | 0 |  | 1 | CAPACITY
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | P60
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00203 |  |  | 0.12623 |  | 1 | CAPACITY
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 6.82 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | P60
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 601.34 |  |  | -0.00204 |  |  | 0.10478 |  | 1 | CAPACITY
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 293.93 |  |  | -0.00204 |  |  | 0.10478 |  | 1 | CAPACITY | Bris2
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 248.4 |  |  | -0.00204 |  |  | 0.10478 |  | 1 | CAPACITY | Bris1
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 68.24 |  |  | -0.00205 |  |  | 0.10478 |  | 1 | CAPACITY
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00206 |  |  | 0.08446 |  | 1 | CAPACITY
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00206 |  |  | 0.08446 |  | 1 | CAPACITY
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 42.95 |  |  | -0.00206 |  |  | 0.08446 |  | 1 | CAPACITY
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 42.95 |  |  | -0.00206 |  |  | 0.08446 |  | 1 | CAPACITY
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00206 |  |  | 0.08446 |  | 1 | CAPACITY
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00206 |  |  | 0 |  | 1 | CAPACITY
219123 | BCRR_COGEN | 13.8 | 231 | 64 | 0 | 6 | 0 |  |  | -0.00207 |  |  | 0.12623 |  | 1 | CAPACITY
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.02 |  |  | -0.00207 |  |  | 0 |  | 1 | CAPACITY
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 23.2 | 0 |  |  | -0.00208 |  |  | 0 |  | 1 | NEWENERGY | K13
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 2.57 |  |  | -0.00208 |  |  | 0 |  | 1 | CAPACITY | K13
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 24.24 |  |  | -0.0021 |  |  | 0.07484 |  | 1 | CAPACITY
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 10.44 |  |  | -0.00209 |  |  | 0.12623 |  | 1 | CAPACITY
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00211 |  |  | 0.12623 |  | 1 | CAPACITY
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 422.06 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 60 | 0 |  |  | -0.00215 |  |  | 0 |  | 1 | NEWENERGY | R32
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 52 | 0 |  |  | -0.00215 |  |  | 0 |  | 1 | NEWENERGY | O18
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 10.19 |  |  | -0.00215 |  |  | 0 |  | 1 | CAPACITY | R32
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00215 |  |  | 0 |  | 1 | CAPACITY | O18
200805 | 26COLVER13 | 13.2 | 226 | 12 | 77 | 110 | 88.31 |  |  | -0.00216 |  |  | 0.10478 |  | 1 | CAPACITY
903644 | W3-099 E OP1 | 230 | 226 | 74 | 0 | 87 | 0 |  |  | -0.00217 |  |  | 0 |  | 1 | NEWENERGY | W3-099
201144 | W3-099 C OP1 | 230 | 226 | 74 | 0 | 13 | 0 |  |  | -0.00217 |  |  | 0 |  | 1 | NEW | W3-099
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 497.77 |  |  | -0.00219 |  |  | 0.10478 |  | 1 | CAPACITY
200809 | 26SITHE | 138 | 226 | 15 | 0 | 36 | 28.9 |  |  | -0.00219 |  |  | 0.10478 |  | 1 | CAPACITY
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 0 |  |  | -0.00223 |  |  | 0 |  | 1 | NEWENERGY | V3-030
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 4.25 |  |  | -0.00223 |  |  | 0 |  | 1 | CAPACITY | V3-030
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 900.89 |  |  | -0.00224 |  |  | 0.01494 |  | 1 | CAPACITY
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 48 | 0 |  |  | -0.00228 |  |  | 0 |  | 1 | NEWENERGY | Q53
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 5.14 |  |  | -0.00228 |  |  | 0 |  | 1 | CAPACITY | Q53
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 0 |  |  | -0.0023 |  |  | 0 |  | 1 | NEWENERGY | N39
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 0 |  |  | -0.0023 |  |  | 0 |  | 1 | NEWENERGY | O38
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 10.7 | 8.59 |  |  | -0.0023 |  |  | 0 |  | 1 | CAPACITY | N39
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.4 | 7.55 |  |  | -0.0023 |  |  | 0 |  | 1 | CAPACITY | O38
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 521.86 |  |  | -0.00233 |  |  | 0.10478 |  | 1 | CAPACITY
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 492.95 |  |  | -0.00233 |  |  | 0.10478 |  | 1 | CAPACITY
208947 | WSHO CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00235 |  |  | 0.08446 |  | 1 | CAPACITY
208348 | EELI | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00247 |  |  | 0 |  | 1 | CAPACITY
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 57 | 45.76 |  |  | -0.00248 |  |  | 0.08446 |  | 1 | CAPACITY
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | -0.00251 |  |  | 0 |  | 1 | ENERGY
208942 | HARR CT | 12.5 | 229 | 55 | 0 | 42 | 33.72 |  |  | -0.00252 |  |  | 0.08446 |  | 1 | CAPACITY
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 9.64 |  |  | -0.00252 |  |  | 0.12623 |  | 1 | CAPACITY
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 8.19 |  |  | -0.00252 |  |  | 0.10478 |  | 1 | CAPACITY
210022 | LING 2 | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00251 |  |  | 0 |  | 1 | CAPACITY
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 24.08 |  |  | -0.00253 |  |  | 0.10478 |  | 1 | CAPACITY
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 40 | 0 |  |  | -0.00253 |  |  | 0 |  | 1 | NEWENERGY | Q36
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 6.66 |  |  | -0.00253 |  |  | 0 |  | 1 | CAPACITY | Q36
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 16.86 |  |  | -0.00255 |  |  | 0.07484 |  | 1 | CAPACITY
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 187.87 |  |  | -0.00263 |  |  | 0.0316 |  | 1 | CAPACITY
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 177.43 |  |  | -0.00263 |  |  | 0.0316 |  | 1 | CAPACITY
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 26.13 |  |  | -0.00263 |  |  | 0.07484 |  | 1 | CAPACITY
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | -0.00266 |  |  | 0.12623 |  | 1 | ENERGY
208885 | WNHO | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00266 |  |  | 0 |  | 1 | CAPACITY
208697 | PRIN B34 | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00266 |  |  | 0 |  | 1 | CAPACITY
210319 | WCAR 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00268 |  |  | 0 |  | 1 | CAPACITY
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4.82 |  |  | -0.00279 |  |  | 0 |  | 1 | CAPACITY
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 33.96 |  |  | -0.00282 |  |  | 0.10478 |  | 1 | CAPACITY
200722 | 26SHAWVL 2 | 18 | 226 | 12 | 62 | 124.7 | 100.12 |  |  | -0.00287 |  |  | 0.10478 |  | 1 | CAPACITY
200715 | 26SHAWVL 1 | 18 | 226 | 12 | 62 | 122 | 97.95 |  |  | -0.00287 |  |  | 0.10478 |  | 1 | CAPACITY
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | -0.00293 |  |  | 0 |  | 1 | MTX | AC1-025
200665 | 26SHAWVL 3 | 22 | 226 | 12 | 120 | 174.2 | 139.86 |  |  | -0.00295 |  |  | 0.10478 |  | 1 | CAPACITY
200666 | 26SHAWVL 4 | 22 | 226 | 12 | 120 | 171 | 137.29 |  |  | -0.00294 |  |  | 0.10478 |  | 1 | CAPACITY
236828 | 01GRAYMONT | 46 | 201 | 2 | 0 | 4 | 0 |  |  | -0.00294 |  |  | 0 |  | 1 | ENERGY
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | -0.00301 |  |  | 0 |  | 1 | ENERGY
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.61 |  |  | -0.00301 |  |  | 0 |  | 1 | CAPACITY
204662 | 27AES GEN1 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00306 |  |  | 0.04435 |  | 1 | CAPACITY | IRONWOOD
204664 | 27AES GEN3 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00306 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204663 | 27AES GEN2 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00306 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | -0.00325 |  |  | 0 |  | 1 | ENERGY
208580 | MGTN 2 | 12.5 | 229 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00325 |  |  | 0 |  | 1 | CAPACITY
922932 | AB1-082 OP | 46 | 201 | 55 | 0 | 19.9 | 0 |  |  | -0.00332 |  |  | 0.08446 |  | 1 | NEW
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY | Z1-069
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00369 |  |  | 0 |  | 1 | CAPACITY | Z1-069
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 389.39 |  |  | -0.00419 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-115
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 30.1 | 24.17 |  |  | -0.00423 |  |  | 0.08446 |  | 1 | CAPACITY
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 4.82 |  |  | -0.00428 |  |  | 0 |  | 1 | CAPACITY
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 6 | 4.82 |  |  | -0.00436 |  |  | 0 |  | 1 | CAPACITY
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 19 | 15.25 |  |  | -0.00448 |  |  | 0.08446 |  | 1 | CAPACITY
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 0 |  |  | -0.00463 |  |  | 0 |  | 1 | NEWENERGY | P47
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00463 |  |  | 0 |  | 1 | NEWENERGY | K02
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.8 | 12.69 |  |  | -0.00463 |  |  | 0 |  | 1 | CAPACITY | P47
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 64.23 |  |  | -0.00466 |  |  | 0.10478 |  | 1 | CAPACITY
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 152.86 |  |  | -0.00474 |  |  | 0.04435 |  | 1 | CAPACITY | ONTELAUNEE
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 152.86 |  |  | -0.00474 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 139.94 |  |  | -0.00474 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 17.18 |  |  | -0.00483 |  |  | 0.12623 |  | 1 | CAPACITY
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 16.86 |  |  | -0.00483 |  |  | 0.12623 |  | 1 | CAPACITY
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 16.86 |  |  | -0.00486 |  |  | 0.12623 |  | 1 | CAPACITY
920341 | AA2-132 | 34.5 | 226 | 55 | 0 | 19.9 | 0 |  |  | -0.00524 |  |  | 0.08446 |  | 1 | NEW
919201 | AA1-144 OP | 230 | 226 | 58 | 0 | 163 | 130.87 |  |  | -0.00546 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-144
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00551 |  |  | 0 |  | 1 | CAPACITY | X1-109
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00551 |  |  | 0.04435 |  | 1 | CAPACITY | X1-109
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.04 |  |  | -0.00555 |  |  | 0 |  | 1 | CAPACITY
203932 | AA2-133 GEN | 13.8 | 226 | 55 | 0 | 19.89 | 0 |  |  | -0.00595 |  |  | 0.08446 |  | 1 | NEW
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 317.93 |  |  | -0.00595 |  |  | 0 |  | 1 | CAPACITY | Hummel
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 194.29 |  |  | -0.00595 |  |  | 0 |  | 1 | CAPACITY | Hummel
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.00595 |  |  | 0.04435 |  | 1 | CAPACITY | Hummel
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.00595 |  |  | 0 |  | 1 | CAPACITY | Hummel
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 0 |  |  | -0.00643 |  |  | 0 |  | 1 | NEWENERGY | P28
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | -0.00643 |  |  | 0.10478 |  | 1 | NEW
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 47.37 |  |  | -0.00643 |  |  | 0.10478 |  | 1 | CAPACITY
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00643 |  |  | 0 |  | 1 | CAPACITY | P28
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 17.18 |  |  | -0.00643 |  |  | 0.12623 |  | 1 | CAPACITY
209018 | SUNBIPCT | 12.5 | 229 | 55 | 0 | 36 | 28.9 |  |  | -0.00671 |  |  | 0.08446 |  | 1 | CAPACITY
212345 | PENS | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00671 |  |  | 0 |  | 1 | CAPACITY
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00686 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00686 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00686 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00686 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00686 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200044 | BETH CT1 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00686 |  |  | 0.04435 |  | 1 | CAPACITY | BETH1234
200048 | BETH CT5 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00686 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0 |  |  | -0.00688 |  |  | 0 |  | 1 | NEWENERGY | W1-121 Z
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00688 |  |  | 0 |  | 1 | CAPACITY | W1-121 Z
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00688 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.46 |  |  | -0.00688 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
212435 | SMIL | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00695 |  |  | 0 |  | 1 | CAPACITY
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 11.24 |  |  | -0.00701 |  |  | 0.08446 |  | 1 | CAPACITY
208948 | WILL CT | 12.5 | 229 | 55 | 0 | 27.4 | 22 |  |  | -0.00706 |  |  | 0.08446 |  | 1 | CAPACITY
212005 | ALWD | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00706 |  |  | 0 |  | 1 | CAPACITY
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00715 |  |  | 0.04435 |  | 1 | CAPACITY | MOXIE PATRIOT
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00715 |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 18.3 | 14.69 |  |  | -0.00722 |  |  | 0.12623 |  | 1 | CAPACITY
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 608.97 |  |  | -0.00724 |  |  | 0.10478 |  | 1 | CAPACITY
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 608.49 |  |  | -0.00724 |  |  | 0.10478 |  | 1 | CAPACITY
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 34.28 |  |  | -0.0073 |  |  | 0.10478 |  | 1 | CAPACITY
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 26.09 |  |  | -0.0073 |  |  | 0.10478 |  | 1 | CAPACITY
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 6.42 |  |  | -0.0073 |  |  | 0 |  | 1 | CAPACITY
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 4.9 |  |  | -0.0073 |  |  | 0 |  | 1 | CAPACITY
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1090.36 |  |  | -0.00759 |  |  | 0.01494 |  | 1 | CAPACITY
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 69.05 |  |  | -0.0076 |  |  | 0.10478 |  | 1 | CAPACITY
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 65.83 |  |  | -0.0076 |  |  | 0.10478 |  | 1 | CAPACITY
208941 | FISH CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.0076 |  |  | 0.08446 |  | 1 | CAPACITY
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.4 | 9.15 |  |  | -0.0076 |  |  | 0 |  | 1 | CAPACITY | Q27
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.81 |  |  | -0.0076 |  |  | 0 |  | 1 | CAPACITY | N14
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00768 |  |  | 0 |  | 1 | CAPACITY | Z2-046
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00768 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-046
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1091.76 |  |  | -0.00797 |  |  | 0.01494 |  | 1 | CAPACITY
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 35.57 |  |  | -0.00821 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 23.44 |  |  | -0.00821 |  |  | 0.04435 |  | 1 | CAPACITY | HUNLOCK
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 39.1 |  |  | -0.00823 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 38.86 |  |  | -0.00823 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
211375 | BEAC | 69 | 229 | 2 | 0 | 20 | 0 |  |  | -0.00826 |  |  | 0.10478 |  | 1 | ENERGY
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 47.77 |  |  | -0.00826 |  |  | 0.08446 |  | 1 | CAPACITY
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 47.21 |  |  | -0.00826 |  |  | 0.08446 |  | 1 | CAPACITY
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 23.76 |  |  | -0.00826 |  |  | 0.08446 |  | 1 | CAPACITY
208943 | HARW CT | 12.5 | 229 | 55 | 0 | 27.2 | 21.84 |  |  | -0.00826 |  |  | 0.08446 |  | 1 | CAPACITY
211591 | HARW | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00826 |  |  | 0 |  | 1 | CAPACITY
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.00831 |  |  | 0.05 |  | 1 | MTX | AB1-182
208944 | JENK CT | 12.5 | 229 | 55 | 0 | 28 | 22.48 |  |  | -0.00831 |  |  | 0.08446 |  | 1 | CAPACITY
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.65 |  |  | -0.00831 |  |  | 0 |  | 1 | CAPACITY | L18
211374 | AVOC | 12.5 | 229 | 2 | 0 | 17.4 | 13.97 |  |  | -0.00849 |  |  | 0 |  | 1 | CAPACITY
208940 | ALLE CT | 12.5 | 229 | 55 | 0 | 56 | 44.96 |  |  | -0.00868 |  |  | 0.08446 |  | 1 | CAPACITY
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.0087 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00878 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G3
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00878 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G1
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00878 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G2
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | -0.00878 |  |  | 0.05 |  | 1 | MTX | Z2-107
209009 | PEIP 2 | 13.8 | 229 | 56 | 0 | 43.7 | 35.08 |  |  | -0.00878 |  |  | 0.08446 |  | 1 | CAPACITY
209010 | PEIP 1 | 13.8 | 229 | 29 | 0 | 26.7 | 21.43 |  |  | -0.00878 |  |  | 0.10478 |  | 1 | CAPACITY
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 7.23 |  |  | -0.00878 |  |  | 0 |  | 1 | CAPACITY | K21
209003 | KSTN IPP | 13.8 | 229 | 65 | 0 | 4.9 | 3.93 |  |  | -0.00878 |  |  | 0 |  | 1 | CAPACITY
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 0 |  |  | -0.0088 |  |  | 0 |  | 1 | NEWENERGY | AC1-071
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 7.02 |  |  | -0.0088 |  |  | 0 |  | 1 | NEW | AC1-071
209007 | NOEN IPP | 13.8 | 229 | 12 | 80 | 111.4 | 89.44 |  |  | -0.00883 |  |  | 0.10478 |  | 1 | CAPACITY
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 0 |  |  | -0.00892 |  |  | 0 |  | 1 | NEWENERGY | AA2-017
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 0 |  |  | -0.00892 |  |  | 0 |  | 1 | NEW | AA2-017
211065 | PSPA IPP | 13.8 | 229 | 75 | 0 | 18.4 | 6.74 |  |  | -0.00915 |  |  | 0 |  | 1 | NEWENERGY | U4-014
208946 | MACR CT | 12.5 | 229 | 55 | 0 | 72 | 57.81 |  |  | -0.00974 |  |  | 0.08446 |  | 1 | CAPACITY
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.33 |  |  | -0.00986 |  |  | 0 |  | 1 | CAPACITY
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 152 | 122.03 |  |  | -0.01 |  |  | 0.08446 |  | 1 | CAPACITY
206341 | 28GIL 8 | 13.8 | 228 | 58 | 69.9 | 90 | 72.26 |  |  | -0.01 |  |  | 0.04435 |  | 1 | CAPACITY | GILBERT
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 87 | 100 | 87.11 |  |  | -0.01 |  |  | 0 |  | 1 | CAPACITY | GILBERT
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 85.3 | 98 | 85.37 |  |  | -0.01 |  |  | 0 |  | 1 | CAPACITY | GILBERT
208920 | WLPK | 12.5 | 229 | 60 | 0 | 40.9 | 32.84 |  |  | -0.01013 |  |  | 0.07484 |  | 1 | CAPACITY
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.0102 |  |  | 0.10478 |  | 1 | CAPACITY
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.0102 |  |  | 0.10478 |  | 1 | CAPACITY
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 192.53 |  |  | -0.0102 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 160.57 |  |  | -0.0102 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 160.57 |  |  | -0.0102 |  |  | 0.04435 |  | 1 | CAPACITY | LOWER MT BETHEL
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01049 |  |  | 0 |  | 1 | NEWENERGY | W4-097
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.01049 |  |  | 0 |  | 1 | CAPACITY | W4-097
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0 |  |  | -0.01054 |  |  | 0 |  | 1 | NEWENERGY | AD2-070
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 2.81 |  |  | -0.01054 |  |  | 0 |  | 1 | CAPACITY | AD2-070
207402 | 28AA2-082 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.01057 |  |  | 0.05 |  | 1 | MTX | AA2-082
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.01063 |  |  | 0 |  | 1 | NEWENERGY | W4-073
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.01063 |  |  | 0 |  | 1 | CAPACITY
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01065 |  |  | 0 |  | 1 | NEWENERGY | W1-127
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0 |  |  | -0.01065 |  |  | 0 |  | 1 | NEWENERGY | U2-059
925462 | AC1-018 E | 34.5 | 228 | 75 | 0 | 0.9 | 0 |  |  | -0.01065 |  |  | 0 |  | 1 | NEWENERGY | AC1-018
925461 | AC1-018 C | 34.5 | 228 | 75 | 0 | 0.5 | 0 |  |  | -0.01065 |  |  | 0 |  | 1 | NEW | AC1-018
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01065 |  |  | 0 |  | 1 | CAPACITY | W1-127
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.01065 |  |  | 0 |  | 1 | CAPACITY | U2-059
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 4 | 3.21 |  |  | -0.01091 |  |  | 0 |  | 1 | CAPACITY
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 120 |  |  |  | -0.0111
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 20 | 16.06 |  |  | -0.01115 |  |  | 0.08446 |  | 1 | CAPACITY
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.01134 |  |  | 0 |  | 1 | NEWENERGY | W3-077
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 5.7 | 4.58 |  |  | -0.01134 |  |  | 0 |  | 1 | CAPACITY | W3-077
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.01134 |  |  | 0 |  | 1 | CAPACITY | W2-091
204651 | 27PORT CT | 13.8 | 227 | 56 | 4 | 35 | 28.1 |  |  | -0.01137 |  |  | 0.08446 |  | 1 | CAPACITY
218780 | PRINCENTON_U | 26 | 231 | 2 | 0 | 31.56 | 25.34 |  |  | -0.01141 |  |  | 0 |  | 1 | CAPACITY
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0 |  |  | -0.01141 |  |  | 0 |  | 1 | NEWENERGY | Z1-096
219622 | TRENT_BIOGAS | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.01141 |  |  | 0 |  | 1 | CAPACITY
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 2.39 |  |  | -0.01141 |  |  | 0 |  | 1 | CAPACITY | Z1-096
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.01158 |  |  | 0 |  | 1 | NEWENERGY | W2-016
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.01158 |  |  | 0 |  | 1 | CAPACITY | W2-016
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 134 | 107.58 |  |  | -0.01166 |  |  | 0.08446 |  | 1 | CAPACITY
206747 | 28DSM_X3-029 | 34.5 | 228 | 29 | 0 | 11.15 | 0 |  |  | -0.0121 |  |  | 0.10478 |  | 1 | ENERGY
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | -0.0121 |  |  | 0.08446 |  | 1 | ENERGY
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01215 |  |  | 0 |  | 1 | NEWENERGY | Y2-018
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.01227 |  |  | 0.0316 |  | 1 | CAPACITY
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.01227 |  |  | 0.0316 |  | 1 | CAPACITY
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.01227 |  |  | 0.0316 |  | 1 | CAPACITY
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 0 |  |  | -0.01238 |  |  | 0 |  | 1 | NEWENERGY | W3-044
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 6.1 |  |  | -0.01238 |  |  | 0 |  | 1 | CAPACITY | W3-044
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.01263 |  |  | 0 |  | 1 | NEWENERGY | W4-046
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 1.93 |  |  | -0.01263 |  |  | 0 |  | 1 | CAPACITY | W4-046
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.01293 |  |  | 0 |  | 1 | NEWENERGY | V4-001
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.61 |  |  | -0.01293 |  |  | 0 |  | 1 | CAPACITY | V4-001
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 35.24 |  |  | -0.01323 |  |  | 0.10478 |  | 1 | CAPACITY
933322 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | -0.0133 |  |  | 0 |  | 1 | MTX | AC2-144
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0 |  |  | -0.01385 |  |  | 0 |  | 1 | NEWENERGY | V2-009 3
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0 |  |  | -0.01385 |  |  | 0 |  | 1 | NEWENERGY | V2-009 4
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 1.92 |  |  | -0.01385 |  |  | 0 |  | 1 | CAPACITY | V2-009 3
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 1.15 |  |  | -0.01385 |  |  | 0 |  | 1 | CAPACITY | V2-009 4
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0 |  |  | -0.01427 |  |  | 0 |  | 1 | NEWENERGY | W3-124
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0 |  |  | -0.01427 |  |  | 0 |  | 1 | NEWENERGY | V2-009 1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.87 |  |  | -0.01427 |  |  | 0 |  | 1 | CAPACITY | W3-124
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.01427 |  |  | 0 |  | 1 | CAPACITY | V2-009 1
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.01429 |  |  | 0 |  | 1 | NEWENERGY | V3-024
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0 |  |  | -0.01429 |  |  | 0 |  | 1 | NEWENERGY | V2-009 2
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0 |  |  | -0.01429 |  |  | 0 |  | 1 | NEWENERGY | X2-088
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.01429 |  |  | 0 |  | 1 | CAPACITY | V3-024
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 1.52 |  |  | -0.01429 |  |  | 0 |  | 1 | CAPACITY | V2-009 2
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.72 |  |  | -0.01429 |  |  | 0 |  | 1 | CAPACITY | X2-088
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0 |  |  | -0.01431 |  |  | 0 |  | 1 | NEWENERGY | W2-050
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.01431 |  |  | 0 |  | 1 | NEWENERGY | W4-064
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.01431 |  |  | 0 |  | 1 | CAPACITY | W4-064
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.0145 |  |  | 0 |  | 1 | NEWENERGY | X1-012
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 2.97 |  |  | -0.0145 |  |  | 0 |  | 1 | CAPACITY | X1-012
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | -0.01454 |  |  | 0.05 |  | 1 | MTX | AA2-061
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | -0.01454 |  |  | 0.05 |  | 1 | MTX | AA2-060
206742 | 28SUX_V3-011 | 34.5 | 228 | 64 | 0 | 2 | 0 |  |  | -0.01456 |  |  | 0 |  | 1 | CAPACITY
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0 |  |  | -0.0146 |  |  | 0 |  | 1 | NEWENERGY | W3-106
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0 |  |  | -0.01464 |  |  | 0 |  | 1 | NEWENERGY | W3-110
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 2.29 |  |  | -0.01464 |  |  | 0 |  | 1 | CAPACITY | W3-110
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0 |  |  | -0.01465 |  |  | 0 |  | 1 | NEWENERGY | V3-070
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.01465 |  |  | 0 |  | 1 | CAPACITY | V3-070
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 2.99 |  |  | -0.01476 |  |  | 0 |  | 1 | CAPACITY | Y1-020
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0 |  |  | -0.01481 |  |  | 0 |  | 1 | NEWENERGY | W2-080
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.01481 |  |  | 0 |  | 1 | CAPACITY | W2-080
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0 |  |  | -0.01484 |  |  | 0 |  | 1 | NEWENERGY | AC2-175
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0 |  |  | -0.01484 |  |  | 0 |  | 1 | NEWENERGY | AE1-081
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.77 |  |  | -0.01484 |  |  | 0 |  | 1 | CAPACITY | AE1-081
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0 |  |  | -0.01496 |  |  | 0 |  | 1 | NEWENERGY | X2-075
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 1.83 |  |  | -0.01496 |  |  | 0 |  | 1 | CAPACITY | X2-075
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.01499 |  |  | 0 |  | 1 | NEWENERGY | W3-029
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0 |  |  | -0.01499 |  |  | 0 |  | 1 | NEWENERGY | W3-003
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0 |  |  | -0.01499 |  |  | 0 |  | 1 | NEW | AE1-156
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0 |  |  | -0.01499 |  |  | 0 |  | 1 | NEWENERGY | AE1-156
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.01499 |  |  | 0 |  | 1 | NEWENERGY | W1-132
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.01499 |  |  | 0 |  | 1 | NEWENERGY | V4-069
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.01499 |  |  | 0 |  | 1 | NEWENERGY | W2-061
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.01499 |  |  | 0 |  | 1 | NEWENERGY | V4-070
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.01499 |  |  | 0 |  | 1 | CAPACITY | W3-029
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01499 |  |  | 0 |  | 1 | CAPACITY | V4-069
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01499 |  |  | 0 |  | 1 | CAPACITY | V4-070
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.01499 |  |  | 0 |  | 1 | CAPACITY | W2-061
218455 | CINNBAY_CGEN | 26.4 | 231 | 75 | 0 | 9 | 0 |  |  | -0.01571 |  |  | 0 |  | 1 | NEWENERGY
924132 | NEWROADSO E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.01571 |  |  | 0 |  | 1 | NEWENERGY | AB2-057
217199 | EDGEBORO_2E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.01571 |  |  | 0 |  | 1 | NEWENERGY | V3-059
217198 | EDGEBORO_1E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.01571 |  |  | 0 |  | 1 | NEWENERGY | V3-058
924131 | NEWROADSO C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.01571 |  |  | 0 |  | 1 | CAPACITY | AB2-057
218781 | BRIS_MYERS | 26 | 231 | 2 | 0 | 3 | 2.41 |  |  | -0.01571 |  |  | 0 |  | 1 | CAPACITY
933332 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | -0.01624 |  |  | 0 |  | 1 | MTX | AC2-145
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0 |  |  | -0.01634 |  |  | 0 |  | 1 | NEWENERGY | X2-089
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.61 |  |  | -0.01634 |  |  | 0 |  | 1 | CAPACITY | X2-089
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 538.72 |  |  | -0.01635 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-116
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0 |  |  | -0.01635 |  |  | 0 |  | 1 | NEWENERGY | AB1-139
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0 |  |  | -0.01635 |  |  | 0 |  | 1 | NEWENERGY | AE1-041
930901 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 2.01 |  |  | -0.01635 |  |  | 0 |  | 1 | CAPACITY | AB1-139
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0 |  |  | -0.01635 |  |  | 0 |  | 1 | NEWENERGY | W2-052
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.01635 |  |  | 0 |  | 1 | CAPACITY | W2-052
938281 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.01635 |  |  | 0 |  | 1 | CAPACITY | AE1-041
219001 | SEWAREN7GT | 25 | 231 | 58 | 101.5 | 324.6 | 260.61 |  |  | -0.01643 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-089
219002 | SEWAREN7ST | 18 | 231 | 58 | 96.3 | 216.4 | 173.74 |  |  | -0.01643 |  |  | 0 |  | 1 | CAPACITY | Z2-089
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | -0.01643 |  |  | 0.04435 |  | 1 | ENERGY | Z2-089
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | -0.01643 |  |  | 0 |  | 1 | ENERGY | Z2-089
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 309 | 248.08 |  |  | -0.01671 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.01671 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.01671 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC2
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.01671 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC1
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | -0.01671 |  |  | 0.08446 |  | 1 | CAPACITY
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | -0.01671 |  |  | 0.08446 |  | 1 | CAPACITY
218344 | TOSCO_G6 | 18 | 231 | 2 | 90 | 180 | 144.51 |  |  | -0.01674 |  |  | 0.04435 |  | 1 | CAPACITY | TOSCO
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  |  |  | -0.0168
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 309 | 248.08 |  |  | -0.01682 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 180 | 144.51 |  |  | -0.01682 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -0.01682 |  |  | 0.08446 |  | 1 | CAPACITY
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -0.01682 |  |  | 0.08446 |  | 1 | CAPACITY
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 30.03 |  |  | -0.01682 |  |  | 0.10478 |  | 1 | CAPACITY
900003 | DEANS E | 500 | 231 | 74 | 0 | 1779.4 | 0 |  |  | -0.01689 |  |  | 0 |  | 1 | NEWENERGY | OSW_DEANS
200006 | DEANS C | 500 | 231 | 74 | 0 | 762.6 | 762.6 |  |  | -0.01689 |  |  | 0 |  | 1 | CAPACITY | OSW_DEANS
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0 |  |  | -0.01691 |  |  | 0 |  | 1 | NEWENERGY | W1-101
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.43 |  |  | -0.01691 |  |  | 0 |  | 1 | CAPACITY | W1-101
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 5.3 |  |  | -0.01691 |  |  | 0 |  | 1 | CAPACITY
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0 |  |  | -0.01699 |  |  | 0 |  | 1 | NEWENERGY | V3-067
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0 |  |  | -0.01699 |  |  | 0 |  | 1 | NEWENERGY | V3-068
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.23 |  |  | -0.01699 |  |  | 0 |  | 1 | CAPACITY | V3-067
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.01699 |  |  | 0 |  | 1 | CAPACITY | V3-068
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 169.24 |  |  | -0.017 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.017 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.017 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.017 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.017 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.017 |  |  | 0.10478 |  | 1 | CAPACITY
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.017 |  |  | 0.10478 |  | 1 | CAPACITY
217825 | UMD_NJ | 26 | 231 | 2 | 0 | 10.5 | 8.43 |  |  | -0.017 |  |  | 0 |  | 1 | CAPACITY
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 202.48 |  |  | -0.01703 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 143.63 |  |  | -0.01703 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 143.63 |  |  | -0.01703 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN2
218092 | PRIMEENG_G | 26.4 | 231 | 29 | 10 | 70.3 | 56.44 |  |  | -0.01703 |  |  | 0.10478 |  | 1 | CAPACITY
217850 | MONTCLAIR_U | 26 | 231 | 2 | 0 | 10.6 | 8.51 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY
934302 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.01704 |  |  | 0 |  | 1 | NEWENERGY | AD1-054
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.74 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0 |  |  | -0.01703 |  |  | 0 |  | 1 | NEWENERGY | X1-072
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.01703 |  |  | 0 |  | 1 | CAPACITY | X1-072
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 207.94 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.01704 |  |  | 0.04435 |  | 1 | CAPACITY | DELANCY STREET
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 76.11 |  |  | -0.01704 |  |  | 0.08446 |  | 1 | CAPACITY
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.01704 |  |  | 0.08446 |  | 1 | CAPACITY
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.01704 |  |  | 0.08446 |  | 1 | CAPACITY
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.01704 |  |  | 0.08446 |  | 1 | CAPACITY
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.01704 |  |  | 0.08446 |  | 1 | CAPACITY
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 70.56 |  |  | -0.01704 |  |  | 0.08446 |  | 1 | CAPACITY
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.01704 |  |  | 0.04435 |  | 1 | CAPACITY | NEWARK BAY
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 27.46 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.01705 |  |  | 0 |  | 1 | NEWENERGY | V2-025
217831 | PB_NUTCLIF | 26 | 231 | 2 | 0 | 10.7 | 8.59 |  |  | -0.01705 |  |  | 0 |  | 1 | CAPACITY
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.85 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0 |  |  | -0.01704 |  |  | 0 |  | 1 | NEWENERGY | V3-065
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0 |  |  | -0.01704 |  |  | 0 |  | 1 | NEWENERGY | V3-066
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.17 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY | V3-065
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.01704 |  |  | 0 |  | 1 | CAPACITY | V3-066
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0 |  |  | -0.01706 |  |  | 0 |  | 1 | NEWENERGY | W4-059
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.18 |  |  | -0.01706 |  |  | 0 |  | 1 | CAPACITY | W4-059
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0 |  |  | -0.01707 |  |  | 0 |  | 1 | NEWENERGY | AB1-021
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.01707 |  |  | 0 |  | 1 | CAPACITY | AB1-021
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0 |  |  | -0.01728 |  |  | 0 |  | 1 | NEWENERGY | X2-087
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.01728 |  |  | 0 |  | 1 | CAPACITY | X2-087
937512 | AD2-210 E | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | -0.01744 |  |  | 0 |  | 1 | MTX | AD2-210
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.01758 |  |  | 0 |  | 1 | NEWENERGY | X1-095
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.01758 |  |  | 0 |  | 1 | CAPACITY | X1-095
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0 |  |  | -0.02005 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0 |  |  | -0.02005 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
932032 | AC2-009 E | 13.2 | 231 | 75 | -0.5 | 0.49 | 0 |  |  | -0.02005 |  |  | 0 |  | 1 | NEWENERGY | AC2-009
932031 | AC2-009 C | 13.2 | 231 | 75 | -0.1 | 0.1 | 0 |  |  | -0.02005 |  |  | 0 |  | 1 | NEW | AC2-009
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.02005 |  |  | 0 |  | 1 | CAPACITY | AA2-058
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0 |  |  | -0.02137 |  |  | 0 |  | 1 | NEWENERGY | W2-036
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.02137 |  |  | 0 |  | 1 | CAPACITY | W2-036
219650 | TRENT_COLLEG | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.02226 |  |  | 0 |  | 1 | CAPACITY
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0 |  |  | -0.02226 |  |  | 0 |  | 1 | NEWENERGY | W4-058
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.22 |  |  | -0.02226 |  |  | 0 |  | 1 | CAPACITY | W4-058
900004 | SMITHBRG E | 500 | 228 | 74 | 0 | 820.4 | 0 |  |  | -0.02373 |  |  | 0 |  | 1 | NEWENERGY | OSW_SMITHB
200017 | SMITHBRG C | 500 | 228 | 74 | 0 | 327.6 | 327.6 |  |  | -0.02373 |  |  | 0 |  | 1 | CAPACITY | OSW_SMITHB
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  |  |  | -0.0408
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 245.67 |  |  | -0.04083 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.04083 |  |  | 0.04435 |  | 1 | CAPACITY | RARITAN RIVER
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.04083 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
207435 | AD1-113 CT2 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.04083 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207434 | AD1-113 CT1 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.04083 |  |  | 0.04435 |  | 1 | NEW | RARITAN RIVER
207441 | AD1-113 ST | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.04083 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 97.1 | 111.6 | 97.21 |  |  | -0.04083 |  |  | 0.08446 |  | 1 | CAPACITY
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 90.9 | 104.5 | 91.03 |  |  | -0.04083 |  |  | 0.08446 |  | 1 | CAPACITY
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 199.11 |  |  | -0.0432 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.0432 |  |  | 0.04435 |  | 1 | CAPACITY | RED OAK
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 141.3 |  |  | -0.04383 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.04383 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 43.63 |  |  | -0.04496 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 46.17 |  |  | -0.04496 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0 |  |  | -0.04519 |  |  | 0 |  | 1 | NEWENERGY | W2-078
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.04519 |  |  | 0 |  | 1 | NEWENERGY | W1-113
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.04519 |  |  | 0 |  | 1 | CAPACITY | W2-078
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 2.25 |  |  | -0.04519 |  |  | 0 |  | 1 | CAPACITY | W1-113
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 66.1 | 98 | 78.68 |  |  | -0.04522 |  |  | 0.08446 |  | 1 | CAPACITY
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 87.02 |  |  | -0.04522 |  |  | 0.08446 |  | 1 | CAPACITY
206327 | 28S RIV G1 | 13.8 | 228 | 57 | 86.9 | 99.9 | 87.02 |  |  | -0.04522 |  |  | 0.08446 |  | 1 | CAPACITY
207419 | AB2-139 E | 34.5 | 228 | 76 | 0 | 0.21 | 0 |  |  | -0.04763 |  |  | 0 |  | 1 | ENERGY | AB2-139
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0 |  |  | -0.04849 |  |  | 0 |  | 1 | NEWENERGY | AC1-207
207420 | AC1-207 C | 34.5 | 228 | 75 | 0 | 4.9 | 3.93 |  |  | -0.04849 |  |  | 0 |  | 1 | CAPACITY | AC1-207
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.05107 |  |  | 0 |  | 1 | NEWENERGY | W4-060
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.05107 |  |  | 0 |  | 1 | CAPACITY | W4-060
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.05179 |  |  | 0 |  | 1 | NEWENERGY | X1-085
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.05179 |  |  | 0 |  | 1 | CAPACITY | X1-085
901032 | W1-024E OP1 | 34.5 | 228 | 0 | 0 | 0 | 0 |  |  | -0.05214 |  |  | 0 |  | 1 | NEW
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.05214 |  |  | 0 |  | 1 | CAPACITY | W1-024
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.05238 |  |  | 0 |  | 1 | NEWENERGY | W1-032
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.05238 |  |  | 0 |  | 1 | CAPACITY | W1-032
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.05478 |  |  | 0.05 |  | 1 | MTX
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0 |  |  | -0.0592 |  |  | 0 |  | 1 | NEWENERGY | W2-019
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 1.85 |  |  | -0.0592 |  |  | 0 |  | 1 | CAPACITY | W2-019
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0 |  |  | -0.05961 |  |  | 0 |  | 1 | NEWENERGY | W1-112
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.05961 |  |  | 0 |  | 1 | CAPACITY | W1-112
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.05999 |  |  | 0 |  | 1 | NEWENERGY | W4-025
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.05999 |  |  | 0 |  | 1 | NEWENERGY | W1-129
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.05999 |  |  | 0 |  | 1 | CAPACITY | W4-025
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.05999 |  |  | 0 |  | 1 | CAPACITY | W1-129
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.06038 |  |  | 0 |  | 1 | NEWENERGY | X4-015
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.06038 |  |  | 0 |  | 1 | CAPACITY | X4-015
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.06093 |  |  | 0 |  | 1 | NEWENERGY | W2-082
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.06093 |  |  | 0 |  | 1 | CAPACITY | W2-082
206201 | 28JERSVGEN | 34.5 | 228 | 2 | 0 | 2 | 1.61 |  |  | -0.06294 |  |  | 0 |  | 1 | CAPACITY
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0 |  |  | -0.06531 |  |  | 0 |  | 1 | NEWENERGY | Z2-102
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 3.97 |  |  | -0.06531 |  |  | 0 |  | 1 | CAPACITY | Z2-102
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.06543 |  |  | 0 |  | 1 | NEWENERGY | W1-119
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.06543 |  |  | 0 |  | 1 | NEWENERGY | W1-120
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.06543 |  |  | 0 |  | 1 | CAPACITY | W1-120
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.06543 |  |  | 0 |  | 1 | CAPACITY | W1-119
920732 | AA2-184 E | 34.5 | 228 | 75 | 0 | 20 | 0 |  |  | -0.0667 |  |  | 0 |  | 1 | NEWENERGY | AA2-184
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.06741 |  |  | 0 |  | 1 | NEWENERGY | W1-124
921743 | AA2-049 E | 34.5 | 228 | 76 | -3 | 3 | 0 |  |  | -0.06741 |  |  | 0 |  | 1 | MTX | AA2-049
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.06741 |  |  | 0 |  | 1 | CAPACITY | W1-124
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0 |  |  | -0.06785 |  |  | 0 |  | 1 | NEWENERGY | X1-037
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 3.37 |  |  | -0.06785 |  |  | 0 |  | 1 | CAPACITY | X1-037
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.07087 |  |  | 0 |  | 1 | NEWENERGY | X4-031
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.08415 |  |  | 0 |  | 1 | NEWENERGY | W3-079
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.08415 |  |  | 0 |  | 1 | CAPACITY | W3-079
900005 | 28LARRABEE E | 230 | 228 | 74 | 0 | 840 | 0 |  |  | -0.08705 |  |  | 0 |  | 1 | NEWENERGY | OSW_LARRAB
206294 | 28LARRABEE C | 230 | 228 | 74 | 0 | 360 | 360 |  |  | -0.08705 |  |  | 0 |  | 1 | CAPACITY | OSW_LARRAB
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.08805 |  |  | 0 |  | 1 | NEWENERGY | Y2-051
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.08805 |  |  | 0 |  | 1 | CAPACITY | Y2-051
923463 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.08832 |  |  | 0 |  | 1 | NEWENERGY | AB1-163
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.10848 |  |  | 0.08446 |  | 1 | CAPACITY
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.10848 |  |  | 0.08446 |  | 1 | CAPACITY
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 61.6 | 88.4 | 70.97 |  |  | -0.10848 |  |  | 0.04435 |  | 1 | CAPACITY | LAKEWOOD
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 61.2 | 88.3 | 70.89 |  |  | -0.10848 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 76.92 |  |  | -0.10848 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
923293 | AB1-138 E | 34.5 | 228 | 75 | 0 | 6 | 0 |  |  | -0.11097 |  |  | 0 |  | 1 | NEWENERGY | AB1-138
206280 | 28LAKEHURS | 34.5 | 228 | 64 | 0 | 13.8 | 11.08 |  |  | -0.11097 |  |  | 0.08446 |  | 1 | CAPACITY
923292 | AB1-138 C | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.11097 |  |  | 0 |  | 1 | CAPACITY | AB1-138

## FG 28-GD-S2-S139
****** PJM Generator Deliverability Detailed Report ****** POWER-GEM [TARA Ver 2001.1a PJMGD RC3 64-bit - Wed Aug 18 16:49:16 2021]
FG Index | 139 | Monitored Facility:227900 CARDIFF C 230 219100 NEWFRDM 230 1 / Contingency:JC-P7-1-JCC-230-13[Tower]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
692 | 103.3 | 101 | AC | -146.23 | 856.31 | 2.29 | 5.41 | -2.96 | 714.82 | 698.9 | 0.001682 | 0 | 12817.4 | 0 | 10597.7 | 0.07461 | 2238.49 | 2219.72 | 18.77 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited?
900000 | CARDIFF E | 230 | 234 | 74 | 0 | 1235 | 0 | 1235 | FiftyFifty | 0.41686 | 514.8251 |  | 0 | 1 | 1 | NEWENERGY | OSW_CARDIF
227900 | CARDIFF C | 230 | 234 | 74 | 0 | 275 | 275 | 275 | FiftyFifty | 0.41686 |  |  | 0 | 1 | 1 | CAPACITY | OSW_CARDIF
900002 | 28OYSTER E | 230 | 228 | 74 | 0 | 586.7 | 0 | 586.7 | FiftyFifty | 0.38613 | 226.5413 |  | 0 | 0.7635 | 1 | NEWENERGY | OSW_OYSCK
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 27.3 | 34 | FiftyFifty | 0.38613 | 2.5882 |  | 0.12623 | 0.8738 | 1 | CAPACITY
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 27 | 31 | FiftyFifty | 0.38613 | 1.543 |  | 0.12623 | 0.7635 | 1 | CAPACITY
206302 | 28OYSTER C | 230 | 228 | 74 | 0 | 229.3 | 229.3 | 229.3 | FiftyFifty | 0.38613 |  |  | 0 | 0.7635 | 1 | CAPACITY | OSW_OYSCK
227928 | V4-067E | 12.9 | 234 | 75 | 1.6 | 1.6 | 0 | 1.6 | FiftyFifty | 0.36859 | 0.5897 |  | 0 | 0.7635 | 1 | NEWENERGY | V4-067
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.79 | 0.98 | FiftyFifty | 0.36859 | 0.0715 |  | 0 | 0.7635 | 1 | CAPACITY | V4-067
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0 | 1.2 | FiftyFifty | 0.36854 | 0.4422 |  | 0 | 0.7635 | 1 | NEWENERGY | AB2-122
924701 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.56 | 0.7 | FiftyFifty | 0.36854 | 0.0505 |  | 0 | 0.7635 | 1 | CAPACITY | AB2-122
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0 | 1.43 | FiftyFifty | 0.34923 | 0.4994 |  | 0 | 0.7635 | 1 | NEWENERGY | AB1-001
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.7 | 0.87 | FiftyFifty | 0.34923 | 0.0597 |  | 0 | 0.7635 | 1 | CAPACITY | AB1-001
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0 | 6 | FiftyFifty | 0.33535 | 2.0121 |  | 0 | 0.7635 | 1 | NEWENERGY | W2-030
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 2.93 | 3.65 | FiftyFifty | 0.33535 | 0.2408 |  | 0 | 0.7635 | 1 | CAPACITY | W2-030
227801 | ONTC&DCT | 13.8 | 234 | 56 | 38.6 | 38.6 | 0 | 38.6 | FiftyFifty | 0.33446 | 12.91 |  | 0.08446 | 0.699 | 1 | NEW
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 | 5.5 | FiftyFifty | 0.33446 | 1.8395 |  | 0.10478 | 0.6257 | 1 | ENERGY
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 | 7.8 | FiftyFifty | 0.33443 | 2.6085 |  | 0.12623 | 0.5468 | 1 | ENERGY
228014 | PVILLEG | 0.48 | 234 | 65 | 1.7 | 3 | 1.04 | 3 | FiftyFifty | 0.3341 | 0.6535 |  | 0 | 0.5468 | 1 | CAPACITY
900001 | BLE E | 138 | 234 | 74 | 0 | 310.6 | 0 | 310.6 | FiftyFifty | 0.27955 | 86.8296 |  | 0 | 0.5468 | 1 | NEWENERGY | OSW_BLE
228110 | BLE C | 138 | 234 | 74 | 0 | 121.4 | 121.4 | 121.4 | FiftyFifty | 0.27955 |  |  | 0 | 0.5468 | 1 | CAPACITY | OSW_BLE
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.61 | 2 | FiftyFifty | 0.23683 | 0.0933 |  | 0 | 0.5468 | 1 | CAPACITY
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 74.48 | 85.5 | FiftyFifty | 0.17388 | 1.9162 |  | 0.08446 | 0.5006 | 1 | CAPACITY
228712 | V2-041E | 13.2 | 234 | 75 | 2.5 | 2.48 | 0 | 2.11 | Adder/OL | 0.16817 | 0.3545 | 0.0035 | 0 |  | 1 | NEWENERGY | V2-041
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0 | 4.84 | Adder/OL | 0.14263 | 0.691 | 0.0081 | 0 |  | 1 | NEWENERGY | W1-130
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 4.8 | 0 | 4.08 | Adder/OL | 0.11133 | 0.4542 | 0.0069 | 0 |  | 1 | NEW
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0 | 5.27 | Adder/OL | 0.11129 | 0.5865 | 0.0089 | 0 |  | 1 | NEWENERGY | V4-054
228721 | V2-035E | 12.9 | 234 | 75 | 1.2 | 1.2 | 0 | 1.02 | Adder/OL | 0.08518 | 0.0869 | 0.0017 | 0 |  | 1 | NEWENERGY | V2-035
228343 | QUINTN#1 | 12.9 | 234 | 64 | 0 | 1.7 | 0 | 1.45 | Adder/OL | 0.07956 | 0.115 | 0.0024 | 0 |  | 1 | CAPACITY
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  | 673 | LTF/CMTX NF | 0.00418 | 2.8123 | -1.132
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  | 105 | LTF/CMTX NF | 0.00396 | 0.4154 | -0.1766
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  | 55.3 | CLTF | 0.00354 | 0.1955 | -0.093
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  | 258.3 | CLTF | 0.00211 | 0.5456 | -0.4345
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.6 |  | 173.6 | CLTF | 0.00212 | 0.3675 | -0.292
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 0.00212 | 0.1178 | -0.0936
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 0.00212 | 0.1156 | -0.0918
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  | 210 | CLTF | 0.0021 | 0.4415 | -0.3532
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 0.00209 | 0.1048 | -0.0842
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 0.00209 | 0.1041 | -0.0836
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  | 35 | CLTF | 0.00208 | 0.0727 | -0.0589
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  | 57.8 | CLTF | 0.00207 | 0.1194 | -0.0971
228203 | P06 | 13.8 | 234 | 57 | 80.6 | 92.7 | 80.75 |  |  | 0.17179 |  |  | 0.08446 |  | 1 | CAPACITY
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 1.22 |  |  | 0.16817 |  |  | 0 |  | 1 | CAPACITY | V2-041
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 73.09 |  |  | 0.15997 |  |  | 0.08446 |  | 1 | CAPACITY
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 2.57 |  |  | 0.14263 |  |  | 0 |  | 1 | CAPACITY | W1-130
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 48.35 |  |  | 0.13505 |  |  | 0.08446 |  | 1 | CAPACITY
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.5 | 18.87 |  |  | 0.12705 |  |  | 0.08446 |  | 1 | CAPACITY
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 49.65 |  |  | 0.12304 |  |  | 0.10478 |  | 1 | CAPACITY
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 3.05 |  |  | 0.11129 |  |  | 0 |  | 1 | CAPACITY | V4-054
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.6 | 39.8 | 34.67 |  |  | 0.1111 |  |  | 0.08446 |  | 1 | CAPACITY
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 32.75 |  |  | 0.1111 |  |  | 0.08446 |  | 1 | CAPACITY
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.61 |  |  | 0.08518 |  |  | 0 |  | 1 | CAPACITY | V2-035
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 192.69 |  |  | 0.06444 |  |  | 0.10478 |  | 1 | CAPACITY
228357 | V2-046E | 12.9 | 234 | 75 | 12.9 | 12.9 | 0 |  |  | 0.0607 |  |  | 0 |  | 1 | NEWENERGY | V2-046
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 6.26 |  |  | 0.0607 |  |  | 0 |  | 1 | CAPACITY | V2-046
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 58.9 | 47.29 |  |  | 0.04099 |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 58.9 | 47.29 |  |  | 0.04099 |  |  | 0.04435 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 175.82 |  |  | 0.03296 |  |  | 0.10478 |  | 1 | CAPACITY
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | 0.02237 |  |  | 0 |  | 1 | ENERGY
228471 | VALERO1 | 13.8 | 234 | 2 | 19.1 | 22 | 19.16 |  |  | 0.02156 |  |  | 0 |  | 1 | CAPACITY
228473 | VALERO3 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.02156 |  |  | 0 |  | 1 | CAPACITY
228472 | VALERO2 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.02156 |  |  | 0 |  | 1 | CAPACITY
228484 | VALERO4 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | 0.02156 |  |  | 0 |  | 1 | CAPACITY
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 55.49 |  |  | 0.01816 |  |  | 0.08446 |  | 1 | CAPACITY
923293 | AB1-138 E | 34.5 | 228 | 75 | 0 | 6 | 0 |  |  | 0.00599 |  |  | 0 |  | 1 | NEWENERGY | AB1-138
206280 | 28LAKEHURS | 34.5 | 228 | 64 | 0 | 13.8 | 11.08 |  |  | 0.00599 |  |  | 0.08446 |  | 1 | CAPACITY
923292 | AB1-138 C | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | 0.00599 |  |  | 0 |  | 1 | CAPACITY | AB1-138
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 271.13 |  |  | 0.00581 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.00581 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | 0.00581 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 60.21 |  |  | 0.00351 |  |  | 0.10478 |  | 1 | CAPACITY
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 998.11 |  |  | 0.00289 |  |  | 0.01494 |  | 1 | CAPACITY
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 992.1 |  |  | 0.00289 |  |  | 0.01494 |  | 1 | CAPACITY
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | 0.00289 |  |  | 0.08446 |  | 1 | ENERGY
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1026.43 |  |  | 0.00276 |  |  | 0.01494 |  | 1 | CAPACITY
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | 0.00136 |  |  | 0.04435 |  | 1 | NEW | AA2-069
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 154.95 |  |  | 0.00136 |  |  | 0.04435 |  | 1 | CAPACITY | Garrison
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 93.29 |  |  | 0.00136 |  |  | 0 |  | 1 | CAPACITY | Garrison
232901 | NORTHST | 69 | 235 | 56 | 5 | 46 | 36.93 |  |  | 0.00136 |  |  | 0.08446 |  | 1 | CAPACITY
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 12.2 |  |  | 0.00136 |  |  | 0.10478 |  | 1 | CAPACITY
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 39.34 |  |  | 0.00132 |  |  | 0.08446 |  | 1 | CAPACITY
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 38.54 |  |  | 0.00132 |  |  | 0.08446 |  | 1 | CAPACITY
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 152.54 |  |  | 0.00123 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00123 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00123 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00123 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC2
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 0 |  |  | 0.0012 |  |  | 0 |  | 1 | NEWENERGY | AB1-056
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 330.7 |  |  | 0.0012 |  |  | 0.10478 |  | 1 | CAPACITY
930201 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 51.71 |  |  | 0.0012 |  |  | 0 |  | 1 | CAPACITY | AB1-056
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | 0.00119 |  |  | 0.10478 |  | 1 | ENERGY
232920 | IR10 | 13.2 | 235 | 55 | 12.6 | 16.1 | 12.93 |  |  | 0.0012 |  |  | 0.08446 |  | 1 | CAPACITY
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0 |  |  | 0.0012 |  |  | 0 |  | 1 | NEWENERGY | AB1-137
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 3.37 |  |  | 0.0012 |  |  | 0 |  | 1 | CAPACITY | AB1-137
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.00119 |  |  | 0 |  | 1 | NEWENERGY | Z2-076
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | 0.00119 |  |  | 0 |  | 1 | NEWENERGY | Z2-077
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.00119 |  |  | 0 |  | 1 | CAPACITY | Z2-077
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | 0.00119 |  |  | 0 |  | 1 | CAPACITY | Z2-076
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.41 |  |  | 0.00119 |  |  | 0 |  | 1 | CAPACITY
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.00117 |  |  | 0.08446 |  | 1 | CAPACITY
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | 0.00117 |  |  | 0.08446 |  | 1 | CAPACITY
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.05 |  |  | 0.00118 |  |  | 0 |  | 1 | CAPACITY
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 0 |  |  | 0.00115 |  |  | 0 |  | 1 | NEWENERGY | AA1-102
917082 | CHERRYDALE E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00116 |  |  | 0 |  | 1 | NEWENERGY | Z2-012
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00116 |  |  | 0 |  | 1 | NEWENERGY | W1-003
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00116 |  |  | 0 |  | 1 | NEWENERGY | W1-005
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00116 |  |  | 0 |  | 1 | NEWENERGY | W1-006
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00116 |  |  | 0 |  | 1 | NEWENERGY | W1-004
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 45.76 |  |  | 0.00115 |  |  | 0 |  | 1 | CAPACITY | AA1-102
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.00116 |  |  | 0.08446 |  | 1 | CAPACITY
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.00116 |  |  | 0.08446 |  | 1 | CAPACITY
232915 | OH NUG4 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.00116 |  |  | 0.08446 |  | 1 | CAPACITY
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | 0.00116 |  |  | 0.08446 |  | 1 | CAPACITY
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 39.03 |  |  | 0.00116 |  |  | 0.08446 |  | 1 | CAPACITY
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 38.94 |  |  | 0.00116 |  |  | 0.08446 |  | 1 | CAPACITY
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 38.68 |  |  | 0.00116 |  |  | 0.08446 |  | 1 | CAPACITY
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0 |  |  | 0.00115 |  |  | 0 |  | 1 | NEWENERGY | X1-032
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 26.05 |  |  | 0.00116 |  |  | 0.08446 |  | 1 | CAPACITY
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.00116 |  |  | 0 |  | 1 | CAPACITY | W1-005
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.00116 |  |  | 0 |  | 1 | CAPACITY | W1-006
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.00116 |  |  | 0 |  | 1 | CAPACITY | W1-004
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | 0.00116 |  |  | 0 |  | 1 | CAPACITY | W1-003
232905 | BAYVIEW1 | 24.9 | 235 | 65 | 0 | 12.5 | 10.04 |  |  | 0.00116 |  |  | 0.12623 |  | 1 | CAPACITY
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 8.03 |  |  | 0.00115 |  |  | 0 |  | 1 | CAPACITY
917081 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.00116 |  |  | 0 |  | 1 | CAPACITY | Z2-012
293670 | O-025 C | 25 | 235 | 64 | 0 | 6 | 4.82 |  |  | 0.00115 |  |  | 0 |  | 1 | CAPACITY
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0 |  |  | 0.00114 |  |  | 0 |  | 1 | NEWENERGY | Y3-058
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 5.7 | 4.58 |  |  | 0.00114 |  |  | 0 |  | 1 | CAPACITY | Y3-058
232919 | VN10 | 13.2 | 235 | 55 | 12.4 | 14.3 | 12.46 |  |  | 0.00111 |  |  | 0 |  | 1 | CAPACITY
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 122.84 |  |  | 0.00111 |  |  | 0.10478 |  | 1 | CAPACITY
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0 |  |  | 0.00111 |  |  | 0 |  | 1 | NEWENERGY | Y1-080
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 1.03 |  |  | 0.00111 |  |  | 0 |  | 1 | CAPACITY | Y1-080
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00108 |  |  | 0 |  | 1 | NEWENERGY | X3-008
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | 0.00108 |  |  | 0 |  | 1 | CAPACITY | X3-008
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 55.4 |  |  | 0.00099 |  |  | 0.12623 |  | 1 | CAPACITY
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0 |  |  | 0.00094 |  |  | 0 |  | 1 | NEWENERGY | Y1-079
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.00094 |  |  | 0 |  | 1 | CAPACITY | Y1-079
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 57.24 |  |  | 0.0009 |  |  | 0.10478 |  | 1 | CAPACITY
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 45.76 |  |  | 0.0009 |  |  | 0.08446 |  | 1 | CAPACITY
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 44.16 |  |  | 0.0009 |  |  | 0.04435 |  | 1 | CAPACITY | DELAWARE CITY
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0 |  |  | 0.00091 |  |  | 0 |  | 1 | NEWENERGY | X3-066
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 14.29 |  |  | 0.0009 |  |  | 0.08446 |  | 1 | CAPACITY
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 2.28 | 1.83 |  |  | 0.00091 |  |  | 0 |  | 1 | CAPACITY | X3-066
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 19.11 |  |  | 0.00089 |  |  | 0.12623 |  | 1 | CAPACITY
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.00087 |  |  | 0 |  | 1 | NEWENERGY | AB1-141
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | 0.00087 |  |  | 0 |  | 1 | NEWENERGY | AB1-142
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.00087 |  |  | 0 |  | 1 | CAPACITY | AB1-141
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | 0.00087 |  |  | 0 |  | 1 | CAPACITY | AB1-142
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 0 |  |  | 0.00066 |  |  | 0 |  | 1 | NEWENERGY | AB2-179
233931 | AB2-179 C | 0.38 | 235 | 75 | 0 | 38 | 30.51 |  |  | 0.00066 |  |  | 0 |  | 1 | CAPACITY | AB2-179
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.09 |  |  | 0.00048 |  |  | 0 |  | 1 | CAPACITY
925112 | AB2-168 E | 34.5 | 235 | 75 | 0 | 5.2 | 0 |  |  | 0.00032 |  |  | 0 |  | 1 | NEWENERGY | AB2-168
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 13.81 |  |  | 0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
925111 | AB2-168 C | 34.5 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | 0.00032 |  |  | 0 |  | 1 | CAPACITY | AB2-168
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 18.47 |  |  | 0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 18.39 |  |  | 0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 139.7 |  |  | 0.00021 |  |  | 0.10478 |  | 1 | CAPACITY
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00021 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.00021 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | 0.0002 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 69.05 |  |  | 0.0002 |  |  | 0.10478 |  | 1 | CAPACITY
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 11.4 |  |  | 0.0002 |  |  | 0.08446 |  | 1 | CAPACITY
923463 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.00014 |  |  | 0 |  | 1 | NEWENERGY | AB1-163
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.00018 |  |  | 0 |  | 1 | NEWENERGY | W1-120
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.00018 |  |  | 0 |  | 1 | NEWENERGY | W1-119
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.00018 |  |  | 0 |  | 1 | CAPACITY | W1-120
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.00018 |  |  | 0 |  | 1 | CAPACITY | W1-119
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 361.29 |  |  | -0.00022 |  |  | 0.10478 |  | 1 | CAPACITY
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 148.77 |  |  | -0.00022 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC1
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0 |  |  | -0.00029 |  |  | 0 |  | 1 | NEWENERGY | Z2-102
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 3.97 |  |  | -0.00029 |  |  | 0 |  | 1 | CAPACITY | Z2-102
213893 | PHLISST1 | 20 | 230 | 58 | 184 | 267 | 214.36 |  |  | -0.00057 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00057 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00057 |  |  | 0.04435 |  | 1 | CAPACITY | PHILLIPS ISLAND
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00057 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 369.31 |  |  | -0.00086 |  |  | 0.04435 |  | 1 | CAPACITY | Y1-065
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | -0.00086 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | -0.00086 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200054 | ROCKSP 3 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | -0.00086 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 3
200055 | ROCKSP 4 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | -0.00086 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 4
200052 | ROCKSP 1 | 18 | 225 | 57 | 145.7 | 167.5 | 145.91 |  |  | -0.00086 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 1
200053 | ROCKSP 2 | 18 | 225 | 57 | 144.9 | 166.5 | 145.04 |  |  | -0.00086 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 2
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1034.24 |  |  | -0.00141 |  |  | 0.01494 |  | 1 | CAPACITY
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 306.69 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | -0.00142 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA2
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 154.95 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | DELTA
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | DELTA
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | -0.00142 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | DELTA
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1049.33 |  |  | -0.00144 |  |  | 0.01494 |  | 1 | CAPACITY
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | -0.00152 |  |  | 0.07484 |  | 1 | CAPACITY
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | -0.00152 |  |  | 0.07484 |  | 1 | CAPACITY
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 77.07 |  |  | -0.00151 |  |  | 0.07484 |  | 1 | CAPACITY
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | -0.00151 |  |  | 0.07484 |  | 1 | CAPACITY
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | -0.00151 |  |  | 0.07484 |  | 1 | CAPACITY
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 38.54 |  |  | -0.00151 |  |  | 0.07484 |  | 1 | CAPACITY
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | -0.00156 |  |  | 0.0316 |  | 1 | CAPACITY
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | -0.00156 |  |  | 0.0316 |  | 1 | CAPACITY
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | -0.00156 |  |  | 0.0316 |  | 1 | CAPACITY
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | -0.00156 |  |  | 0.0316 |  | 1 | CAPACITY
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 31.31 |  |  | -0.00158 |  |  | 0.08446 |  | 1 | CAPACITY
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00161 |  |  | 0.08446 |  | 1 | CAPACITY
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00161 |  |  | 0.08446 |  | 1 | CAPACITY
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00171 |  |  | 0.10478 |  | 1 | CAPACITY
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.0017 |  |  | 0.08446 |  | 1 | CAPACITY
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00172 |  |  | 0.10478 |  | 1 | CAPACITY
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 27.3 |  |  | -0.00171 |  |  | 0.08446 |  | 1 | CAPACITY
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 238 | 191.08 |  |  | -0.00174 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00174 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00174 |  |  | 0.04435 |  | 1 | CAPACITY | LIBERTY EDDY
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | -0.00181 |  |  | 0 |  | 1 | ENERGY
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 256.27 |  |  | -0.00184 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | -0.00184 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | -0.00184 |  |  | 0.04435 |  | 1 | CAPACITY | HUNTERSTOWN
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 134.08 |  |  | -0.00184 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 140.6 | 112.88 |  |  | -0.00187 |  |  | 0.08446 |  | 1 | CAPACITY
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 91.2 |  |  | -0.00187 |  |  | 0.08446 |  | 1 | CAPACITY
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 83.5 |  |  | -0.00187 |  |  | 0.08446 |  | 1 | CAPACITY
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 41.75 |  |  | -0.00187 |  |  | 0.08446 |  | 1 | CAPACITY
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0 |  |  | -0.00186 |  |  | 0 |  | 1 | NEWENERGY | AA2-072
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | -0.00187 |  |  | 0 |  | 1 | ENERGY
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.21 |  |  | -0.00187 |  |  | 0 |  | 1 | CAPACITY
220904 | CRANE G2 | 20 | 232 | 12 | 60 | 195 | 0 |  |  | -0.00187 |  |  | 0.10478 |  | 1 | NEW
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 246 |  |  | -0.00188 |  |  | 0.10478 |  | 1 | CAPACITY
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 102.85 |  |  | -0.00188 |  |  | 0.10478 |  | 1 | CAPACITY
220905 | CRANE GT | 4.16 | 232 | 55 | 0 | 14 | 0 |  |  | -0.00187 |  |  | 0.08446 |  | 1 | NEW
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 45.76 |  |  | -0.00188 |  |  | 0.10478 |  | 1 | CAPACITY
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | -0.00188 |  |  | 0.08446 |  | 1 | ENERGY
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.5 | 24.49 |  |  | -0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 30 | 24.08 |  |  | -0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 10.68 |  |  | -0.00188 |  |  | 0.08446 |  | 1 | CAPACITY
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 516 |  |  | -0.00188 |  |  | 0.10478 |  | 1 | CAPACITY
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 512.95 |  |  | -0.00188 |  |  | 0.10478 |  | 1 | CAPACITY
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 318.73 |  |  | -0.00188 |  |  | 0.10478 |  | 1 | CAPACITY
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.49 |  |  | -0.0019 |  |  | 0 |  | 1 | CAPACITY
226895 | WOAKV2-037 E | 69 | 233 | 65 | 0 | 4.5 | 0 |  |  | -0.0019 |  |  | 0 |  | 1 | ENERGY
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 695.27 |  |  | -0.00191 |  |  | 0.01494 |  | 1 | CAPACITY
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 675.85 |  |  | -0.00191 |  |  | 0.01494 |  | 1 | CAPACITY
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 477.7 |  |  | -0.00192 |  |  | 0.10478 |  | 1 | CAPACITY
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 469.91 |  |  | -0.00192 |  |  | 0.10478 |  | 1 | CAPACITY
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
227024 | SMECOCT | 13.8 | 238 | 57 | 30 | 80.2 | 64.39 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | ENERGY
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 19.59 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 14.45 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0 |  |  | -0.00192 |  |  | 0 |  | 1 | NEWENERGY | AB2-157
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.69 |  |  | -0.00192 |  |  | 0 |  | 1 | CAPACITY
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.76 |  |  | -0.00192 |  |  | 0 |  | 1 | CAPACITY
925011 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00192 |  |  | 0 |  | 1 | CAPACITY | AB2-157
910861 | X3-087 C | 230 | 233 | 58 | 0 | 744 | 597.33 |  |  | -0.00193 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 497.29 |  |  | -0.00192 |  |  | 0.10478 |  | 1 | CAPACITY
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 492.39 |  |  | -0.00192 |  |  | 0.10478 |  | 1 | CAPACITY
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 272.01 |  |  | -0.00192 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | -0.00192 |  |  | 0.04435 |  | 1 | CAPACITY | WALDORF
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | -0.00192 |  |  | 0 |  | 1 | CAPACITY | WALDORF
917371 | Z2-060 | 230 | 233 | 58 | 0 | 116 | 93.13 |  |  | -0.00193 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 0 |  |  | -0.00192 |  |  | 0 |  | 1 | NEWENERGY | AC2-101
920642 | AA2-170 E | 230 | 233 | 58 | 0 | 19.1 | 0 |  |  | -0.00193 |  |  | 0.04435 |  | 1 | NEW | AA2-170
920641 | AA2-170 C | 230 | 233 | 58 | 0 | 92 | 73.86 |  |  | -0.00193 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-170
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 0 |  |  | -0.00192 |  |  | 0 |  | 1 | NEWENERGY | AC2-120
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 64.23 |  |  | -0.00193 |  |  | 0 |  | 1 | CAPACITY | PANDA
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | -0.00193 |  |  | 0.04435 |  | 1 | CAPACITY | PANDA
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | -0.00193 |  |  | 0 |  | 1 | CAPACITY | PANDA
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | -0.00192 |  |  | 0.08446 |  | 1 | CAPACITY
226915 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 9.92 |  |  | -0.00192 |  |  | 0 |  | 1 | CAPACITY | AC2-101
226912 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 8.39 |  |  | -0.00192 |  |  | 0 |  | 1 | CAPACITY | AC2-120
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 330 | 264.94 |  |  | -0.00193 |  |  | 0 |  | 1 | CAPACITY | X4-035
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | -0.00193 |  |  | 0 |  | 1 | CAPACITY | X4-035
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | -0.00193 |  |  | 0.04435 |  | 1 | CAPACITY | X4-035
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | -0.00193 |  |  | 0.10478 |  | 1 | ENERGY
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | -0.00195 |  |  | 0.08446 |  | 1 | CAPACITY
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | -0.00195 |  |  | 0.08446 |  | 1 | CAPACITY
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 41.75 |  |  | -0.00195 |  |  | 0.10478 |  | 1 | CAPACITY
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 14.45 |  |  | -0.00195 |  |  | 0.08446 |  | 1 | CAPACITY
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 0 |  |  | -0.00196 |  |  | 0 |  | 1 | NEWENERGY | AB2-129
924771 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 0 |  |  | -0.00196 |  |  | 0 |  | 1 | NEW | AB2-129
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 245.67 |  |  | -0.00197 |  |  | 0 |  | 1 | CAPACITY | X4-039
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 201.52 |  |  | -0.00198 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.00197 |  |  | 0.04435 |  | 1 | CAPACITY | X4-039
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.00197 |  |  | 0 |  | 1 | CAPACITY | X4-039
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00198 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00198 |  |  | 0.04435 |  | 1 | CAPACITY | POSSUM POINT
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00198 |  |  | 0.10478 |  | 1 | CAPACITY
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00198 |  |  | 0.10478 |  | 1 | CAPACITY
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 28.74 |  |  | -0.00198 |  |  | 0.10478 |  | 1 | CAPACITY
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 28.66 |  |  | -0.00198 |  |  | 0.10478 |  | 1 | CAPACITY
314088 | 6VANDORN | 230 | 345 | 2 | 7 | 21 | 16.86 |  |  | -0.00198 |  |  | 0 |  | 1 | CAPACITY
313821 | 6PACIFIC | 230 | 345 | 75 | 0 | 0.09 | 0 |  |  | -0.00197 |  |  | 0 |  | 1 | NEWENERGY
235002 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0 |  |  | -0.00199 |  |  | 0 |  | 1 | NEW | AC1-039
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0 |  |  | -0.00199 |  |  | 0 |  | 1 | NEWENERGY | AC1-039
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00198 |  |  | 0 |  | 1 | NEWENERGY | AC2-072
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0 |  |  | -0.00199 |  |  | 0 |  | 1 | NEWENERGY | AA1-109
932521 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00198 |  |  | 0 |  | 1 | CAPACITY | AC2-072
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 3.61 |  |  | -0.00199 |  |  | 0 |  | 1 | CAPACITY | AA1-109
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 0.68 | 0 |  |  | -0.00199 |  |  | 0 |  | 1 | NEWENERGY
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 2
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 1
315033 | 1BIRCHWDA | 18 | 345 | 13 | 85 | 238 | 191.08 |  |  | -0.002 |  |  | 0.10478 |  | 1 | CAPACITY
926737 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.002 |  |  | 0 |  | 1 | CAPACITY | AC1-158 1
926738 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.002 |  |  | 0 |  | 1 | CAPACITY | AC1-158 2
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.002 |  |  | 0.08446 |  | 1 | CAPACITY
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.002 |  |  | 0.08446 |  | 1 | CAPACITY
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00199 |  |  | 0.08446 |  | 1 | CAPACITY
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00199 |  |  | 0.08446 |  | 1 | CAPACITY
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 128.94 |  |  | -0.002 |  |  | 0.08446 |  | 1 | CAPACITY
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 128.86 |  |  | -0.00199 |  |  | 0.08446 |  | 1 | CAPACITY
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 128.54 |  |  | -0.002 |  |  | 0.08446 |  | 1 | CAPACITY
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 128.3 |  |  | -0.002 |  |  | 0.08446 |  | 1 | CAPACITY
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 152.3 | 122.28 |  |  | -0.00199 |  |  | 0.10478 |  | 1 | CAPACITY
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00199 |  |  | 0.10478 |  | 1 | CAPACITY
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00199 |  |  | 0.10478 |  | 1 | CAPACITY
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 120.19 |  |  | -0.00199 |  |  | 0.10478 |  | 1 | CAPACITY
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 0 |  |  | -0.00199 |  |  | 0 |  | 1 | NEWENERGY | AB2-029
923213 | AB1-125 E OP | 34.5 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.00199 |  |  | 0 |  | 1 | NEWENERGY | W1-116
923202 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AC2-136
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AB1-096
923212 | AB1-125 C OP | 34.5 | 201 | 75 | 0 | 5.7 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
314078 | 3REMNGTN | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00199 |  |  | 0 |  | 1 | CAPACITY | AB2-029
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 6.98 |  |  | -0.002 |  |  | 0 |  | 1 | CAPACITY
933251 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 4.41 |  |  | -0.002 |  |  | 0 |  | 1 | CAPACITY | AC2-136
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 4.27 |  |  | -0.00199 |  |  | 0 |  | 1 | CAPACITY | W1-116
930521 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 2.49 |  |  | -0.002 |  |  | 0 |  | 1 | CAPACITY | AB1-096
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 1.61 |  |  | -0.00199 |  |  | 0 |  | 1 | CAPACITY
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 761.83 |  |  | -0.002 |  |  | 0.01494 |  | 1 | CAPACITY
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 761.51 |  |  | -0.002 |  |  | 0.01494 |  | 1 | CAPACITY
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 136.49 |  |  | -0.00201 |  |  | 0.08446 |  | 1 | CAPACITY
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.00201 |  |  | 0.08446 |  | 1 | CAPACITY
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.00201 |  |  | 0.08446 |  | 1 | CAPACITY
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 126.85 |  |  | -0.00201 |  |  | 0.08446 |  | 1 | CAPACITY
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY | AB2-158
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00201 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 5
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00201 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 6
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
316149 | AD1-046 E | 230 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AD1-044
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00201 |  |  | 0.08446 |  | 1 | CAPACITY
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00201 |  |  | 0.08446 |  | 1 | CAPACITY
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.00201 |  |  | 0.08446 |  | 1 | CAPACITY
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 61.9 |  |  | -0.00201 |  |  | 0.08446 |  | 1 | CAPACITY
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | W4-102
925021 | AB2-158 C | 230 | 345 | 75 | 0 | 61 | 48.97 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | AB2-158
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AB2-097
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00201 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 2
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.00201 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 1
237799 | 01AA2-159 C | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
920562 | AA2-159 E | 34.5 | 201 | 75 | 0 | 7.3 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
923192 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY | AC1-118
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AE1-124
316148 | AD1-046 C | 230 | 345 | 75 | 0 | 30.7 | 24.65 |  |  | -0.002 |  |  | 0 |  | 1 | CAPACITY | AD1-044
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY | AC2-138
923872 | AB2-027 E | 34.5 | 201 | 75 | 0 | 5.5 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEWENERGY | AB2-027
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 19.99 |  |  | -0.00201 |  |  | 0.10478 |  | 1 | CAPACITY
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | South Anna 2
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | South Anna 1
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 19.27 |  |  | -0.00201 |  |  | 0.10478 |  | 1 | CAPACITY
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY | AA1-092
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY | AA1-095
235006 | AB2-027 C | 34.5 | 201 | 75 | 0 | 3.3 | 0 |  |  | -0.002 |  |  | 0 |  | 1 | NEW | AB2-027
938961 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.002 |  |  | 0 |  | 1 | CAPACITY | AE1-124
314766 | 6LOUISA | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY
314190 | 6WESTMOR | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | AC1-118
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 6.42 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | AA1-092
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.002 |  |  | 0 |  | 1 | CAPACITY | W4-102
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 6.3 | 5.06 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | AC2-138
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 2.33 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | AA1-095
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 2.09 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.002 |  |  | 0 |  | 1 | CAPACITY
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.88 |  |  | -0.002 |  |  | 0 |  | 1 | CAPACITY
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEW | AC1-107
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEW | AC1-107
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.00202 |  |  | 0.04435 |  | 1 | NEW | AC1-107
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 788.9 | 633.38 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 422.86 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
926785 | AC1-164 E | 0.44 | 345 | 75 | 0 | 99.2 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AC1-164
316114 | AB2-068 ST | 22 | 345 | 58 | 0 | 492 | 395.01 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AB2-068
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AB2-134
316113 | AB2-068 CT2 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316112 | AB2-068 CT1 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.00202 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-068
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00202 |  |  | 0.04435 |  | 1 | CAPACITY | WARREN COUNTY CC
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AB2-160
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AB2-190
926784 | AC1-164 C | 0.44 | 345 | 75 | 0 | 220.8 | 177.27 |  |  | -0.00202 |  |  | 0 |  | 1 | NEW | AC1-164
315085 | 1SPRUNCC | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | NEW
315086 | 1SPRUNCD | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | NEW
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | ENERGY
314189 | 6PAPERMILL | 230 | 345 | 1 | 12 | 37 | 0 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | ENERGY
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AC1-065
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 104.93 |  |  | -0.00202 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 7
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 103.25 |  |  | -0.00202 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 8
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 101.16 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 89.92 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AB2-190
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 69.05 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 68.97 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 68.72 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 68.64 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.00202 |  |  | 0.04435 |  | 1 | CAPACITY | HOPEWELL HCF
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 57.65 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AB2-134
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 53.15 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 48.17 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
925863 | AC1-065 C | 0.39 | 345 | 75 | 0 | 41.8 | 33.56 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AC1-065
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AC2-137
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AD2-030
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AE1-074
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AB2-024
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY | AC1-112
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY | AB1-027
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AD1-063
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 24.41 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AB2-160
316158 | AD2-164 | 230 | 345 | 57 | 0 | 26.7 | 21.44 |  |  | -0.00202 |  |  | 0.08446 |  | 1 | CAPACITY
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 16.06 |  |  | -0.00202 |  |  | 0.12623 |  | 1 | CAPACITY
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY | AC2-070
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.3 | 13.09 |  |  | -0.00202 |  |  | 0.12623 |  | 1 | CAPACITY
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 12.04 |  |  | -0.00202 |  |  | 0.12623 |  | 1 | CAPACITY
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 11.96 |  |  | -0.00202 |  |  | 0.12623 |  | 1 | CAPACITY
938551 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AE1-074
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AD2-030
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 11.4 | 9.15 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AC2-137
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 8.83 |  |  | -0.00201 |  |  | 0.12623 |  | 1 | CAPACITY
314172 | 6DUNNSVL | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY
314375 | 6CORRCTN | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AB2-024
314187 | 3WAN 176 | 115 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 8.03 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY
314241 | 6OLDCHRC | 230 | 345 | 75 | 0 | 1.82 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | AB1-027
932501 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 7.39 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY | AC2-070
934391 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AD1-063
314176 | 6HARMONY | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 4.98 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 3.21 |  |  | -0.00201 |  |  | 0 |  | 1 | CAPACITY
314734 | 6CASHSCORNER | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY
314177 | 3HAYES89 | 115 | 345 | 75 | 0 | 0.31 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
314294 | 6ENON | 230 | 345 | 75 | 0 | 0.23 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
313812 | 6ROCKLANDING | 230 | 345 | 75 | 0 | 0.11 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
313828 | 3WHITEMARSH | 115 | 345 | 75 | 0 | 0.05 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
314222 | 6HANOVER | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY
314213 | 3CARVER | 115 | 345 | 75 | 0 | 0 | 0 |  |  | -0.00201 |  |  | 0 |  | 1 | NEWENERGY
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | Z1-036
901082 | W1-029 E | 230 | 345 | 74 | 0 | 261 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | W1-029
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 678.09 |  |  | -0.00202 |  |  | 0.01494 |  | 1 | CAPACITY
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 677.21 |  |  | -0.00202 |  |  | 0.01494 |  | 1 | CAPACITY
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 480.11 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 452.01 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00203 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-086
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00203 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEW | AB2-015
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB2-015
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AA1-139
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | -0.00203 |  |  | 0.10478 |  | 1 | ENERGY
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AB2-161
314525 | 6KINGFORK | 230 | 345 | 75 | 0 | 24.3 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AA2-178
314550 | 6HICKORY | 230 | 345 | 75 | 0 | 22.93 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 88.96 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 87.83 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 86.31 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 69.77 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 69.69 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 63.18 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AA1-139
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | Y1-086
314466 | 6FENTRES | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
314632 | 6AYDLETOLD | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
313717 | 6SLIGO L2192 | 230 | 345 | 75 | 0 | 12.34 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
314331 | 6POE | 230 | 345 | 75 | 0 | 12.27 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AA2-178
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | Z1-068
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00203 |  |  | 0.10478 |  | 1 | CAPACITY
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AD1-060
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AE1-162
935212 | AD1-156 E | 230 | 345 | 75 | 0 | 7.92 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AD1-156
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | W1-029
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | Z1-036
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AC1-147
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AB2-022
316145 | AE1-027 E | 230 | 345 | 75 | 0 | 6.9 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AE1-027
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AC2-196
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AC1-027
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AB2-026
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | Z2-030
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AC2-174
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB2-025
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | Z2-027
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AE1-075
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 23.76 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AD1-144
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AD2-215
316147 | AE1-028 E | 230 | 345 | 75 | 0 | 4.4 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY | AE1-028
314541 | 3WATKINS | 115 | 345 | 1 | 0 | 4 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | ENERGY
314333 | 6POWHATN | 230 | 345 | 75 | 0 | 3.97 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AB2-026
933571 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEW | AC2-174
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AB2-161
314651 | 6WINFALL | 230 | 345 | 75 | 0 | 3.35 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY
314645 | 6SLIGO L269 | 230 | 345 | 75 | 0 | 3.22 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 12.2 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 12.04 |  |  | -0.00202 |  |  | 0.12623 |  | 1 | CAPACITY
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 11.96 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
316144 | AE1-027 C | 230 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AE1-027
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00202 |  |  | 0.08446 |  | 1 | CAPACITY
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 10.44 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AB2-022
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 10.36 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
926661 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 10.12 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AC1-147
316258 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AE1-162
938561 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AE1-075
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 9.55 |  |  | -0.00202 |  |  | 0.10478 |  | 1 | CAPACITY
935211 | AD1-156 C | 230 | 345 | 75 | 0 | 11.82 | 9.49 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AD1-156
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 9.05 |  |  | -0.00202 |  |  | 0.12623 |  | 1 | CAPACITY
314533 | 6SMITFLD | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
314435 | 6SAPONY | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AB2-025
933731 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 8.03 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AC2-196
316150 | AD2-215 C | 230 | 345 | 76 | 0 | 9.8 | 7.87 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AD2-215
935111 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 7.79 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AD1-144
314491 | 3PENDLTN | 115 | 345 | 75 | 0 | 1.89 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AC1-027
314637 | 6EDENTON | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AA2-059
314566 | 3CRESWEL | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY
316146 | AE1-028 C | 230 | 345 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AE1-028
942852 | AE2-304 E | 230 | 345 | 75 | 0 | 1.4 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AE2-304
934362 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 4.58 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | AD1-060
314648 | 6SUNBURY | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 3.93 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | Z2-030
942851 | AE2-304 C | 230 | 345 | 75 | 0 | 3.3 | 2.65 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AE2-304
314638 | 6ELIZ CT | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | Y1-086
314662 | 6S HERTFORD | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 1.61 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY
314639 | 6TANGLEW | 230 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | Z2-027
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.2 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY | Z1-068
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.56 |  |  | -0.00202 |  |  | 0 |  | 1 | CAPACITY
314453 | 6CHRHLND | 230 | 345 | 75 | 0 | 0.08 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
314640 | 6KITTY HAWK | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
314487 | 3MCLAUGH | 115 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00202 |  |  | 0 |  | 1 | NEWENERGY
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.5 | 354.46 |  |  | -0.00204 |  |  | 0.10478 |  | 1 | CAPACITY
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 350.93 |  |  | -0.00204 |  |  | 0.10478 |  | 1 | CAPACITY
923262 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 322.35 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AA2-088
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 198.31 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
923991 | AB2-040 C O1 | 115 | 345 | 75 | 0 | 44 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEW | AB2-040
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB2-174
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00203 |  |  | 0.04435 |  | 1 | CAPACITY | BEAR GARDEN
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
923992 | AB2-040 E O1 | 115 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB2-040
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00203 |  |  | 0.04435 |  | 1 | CAPACITY | FLUVANNA
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
925122 | AB2-169 E | 115 | 345 | 75 | 0 | 35 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AB2-169
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AA1-065
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AA1-063A
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AA2-053
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.00203 |  |  | 0.07484 |  | 1 | CAPACITY
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.00203 |  |  | 0.07484 |  | 1 | CAPACITY
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AD1-085
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 2
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 76.6 | 61.5 |  |  | -0.00204 |  |  | 0.04435 |  | 1 | CAPACITY | ROSEMARY
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB1-128
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB1-127
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 44 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AA2-053
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 53.6 | 43.03 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AA1-065
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 40.87 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AA1-063A
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 40.38 |  |  | -0.00204 |  |  | 0.07484 |  | 1 | CAPACITY
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 40.14 |  |  | -0.00203 |  |  | 0.19858 |  | 1 | CAPACITY
314713 | 3PAMPLIN | 115 | 345 | 75 | 0 | 9.73 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314807 | 3MT JACK | 115 | 345 | 75 | 0 | 9.7 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 38.54 |  |  | -0.00204 |  |  | 0.07484 |  | 1 | CAPACITY
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 47.5 | 38.13 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AC1-036
316143 | AD1-160 E | 115 | 345 | 75 | 0 | 9.1 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AD1-160
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 33.72 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AB2-174
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 32.44 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AB1-173
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AC1-116
925121 | AB2-169 C | 115 | 345 | 75 | 0 | 39 | 31.31 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AB2-169
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 30.51 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AA2-088
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 35.9 | 28.82 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AC2-071
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AB2-100 1
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AB2-100 2
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB2-045
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB1-173
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AD1-157
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AE1-099
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AE1-098
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AC2-074
314578 | 3HORNRTN | 115 | 345 | 75 | 0 | 5.15 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314589 | 3MURPHYS | 115 | 345 | 75 | 0 | 4.66 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | V4-068
313853 | 3PONTONDP | 115 | 345 | 2 | 0 | 4 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | ENERGY
314579 | 6HORNRTN | 230 | 345 | 75 | 0 | 3.91 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 16 | 12.85 |  |  | -0.00204 |  |  | 0.12623 |  | 1 | CAPACITY
932511 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AC2-071
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEW
314266 | 6NORTHAMPTON | 230 | 345 | 75 | 0 | 2.47 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 9.88 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AD1-085
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 8.83 |  |  | -0.00204 |  |  | 0.12623 |  | 1 | CAPACITY
314603 | 3SCOT NK | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314617 | 3TUNIS | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY
314593 | 3PARMELE | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314677 | 6BUCKING | 230 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AB2-045
932541 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AC2-074
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AE1-098
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AE1-099
935221 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AD1-157
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | V4-068
925611 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 6.9 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AC1-036
314568 | 3EARLEYS | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | AB2-099
235041 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AB1-128
235040 | 01AB1-127 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AB1-127
316142 | AD1-160 C | 115 | 345 | 75 | 0 | 6.6 | 5.3 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AD1-160
314559 | 3CAROLNA | 115 | 345 | 75 | 0 | 1.21 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314620 | 6CASHIE | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY
314551 | 3AHOSKIE | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY
314626 | 3WOODLND | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY
314596 | 3POPLR C | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314582 | 3KELFORD | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | Z2-043
926451 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 3.77 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AC1-116
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | AB2-099
314594 | 6PLYMOTH | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY
314604 | 3SEABORD | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY
314762 | 3JAMES R | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 1.04 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY
314629 | 3MARTNCO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314798 | 3MERCK5 | 115 | 345 | 75 | 0 | 0.16 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.64 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY
313826 | 6HYDRAULIC | 230 | 345 | 75 | 0 | 0.04 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 0 |  |  | -0.00205 |  |  | 0 |  | 1 | NEWENERGY | T157
315616 | AA1-038 C | 230 | 345 | 74 | 0 | 76.6 | 0 |  |  | -0.00205 |  |  | 0 |  | 1 | NEW | AA1-038
918232 | AA1-038 E | 230 | 345 | 74 | 0 | 66.7 | 0 |  |  | -0.00205 |  |  | 0 |  | 1 | NEWENERGY | AA1-038
314860 | 4E MILL | 138 | 345 | 2 | 0 | 50 | 0 |  |  | -0.00205 |  |  | 0.10478 |  | 1 | ENERGY
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | Z2-088
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AB2-059
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AB2-043
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AB2-060
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AB1-081
919702 | AA2-057 E OP | 115 | 345 | 75 | 0 | 21.1 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AA2-057
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AC1-054
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 0 |  |  | -0.00205 |  |  | 0 |  | 1 | NEWENERGY | AC1-105
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 52.99 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AB2-059
922922 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AB1-081
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 43.67 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AB2-060
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 53 | 42.55 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | Z2-088
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 36.61 |  |  | -0.00205 |  |  | 0.10478 |  | 1 | CAPACITY
313719 | 3CHESTNUT | 115 | 345 | 75 | 0 | 44.7 | 35.89 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AA2-057
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 35.73 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AC1-054
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00204 |  |  | 0.08446 |  | 1 | CAPACITY
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00204 |  |  | 0.08446 |  | 1 | CAPACITY
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00204 |  |  | 0.07484 |  | 1 | CAPACITY
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00204 |  |  | 0.07484 |  | 1 | CAPACITY
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00204 |  |  | 0.07484 |  | 1 | CAPACITY
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00204 |  |  | 0.07484 |  | 1 | CAPACITY
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00204 |  |  | 0.07484 |  | 1 | CAPACITY
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00204 |  |  | 0.07484 |  | 1 | CAPACITY
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AB2-078
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AB2-077
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AB2-079
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 27.7 |  |  | -0.00205 |  |  | 0 |  | 1 | CAPACITY | AC1-105
314608 | 3TARBORO | 115 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314574 | 6EVERETS | 230 | 345 | 75 | 0 | 5.89 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 20.23 |  |  | -0.00205 |  |  | 0.10478 |  | 1 | CAPACITY
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 20.15 |  |  | -0.00205 |  |  | 0.10478 |  | 1 | CAPACITY
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | AA1-067
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 16.46 |  |  | -0.00205 |  |  | 0 |  | 1 | CAPACITY | T157
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 15.17 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | AB2-043
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY | Z2-044
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 12.04 |  |  | -0.00204 |  |  | 0.07484 |  | 1 | CAPACITY
314623 | 3WITAKRS | 115 | 345 | 75 | 0 | 2.51 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | CAPACITY | Z2-044
924321 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00204 |  |  | 0 |  | 1 | NEW | AB2-079
924311 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00204 |  |  | 0 |  | 1 | NEW | AB2-078
924301 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00204 |  |  | 0 |  | 1 | NEW | AB2-077
314554 | 3BTLEBRO | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00205 |  |  | 0 |  | 1 | CAPACITY
314549 | 3TOT1 | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314557 | 3BETHELC | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314607 | 3TAR RVR | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314205 | 3HEARTS | 115 | 345 | 75 | 0 | 0.41 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314545 | 3TOT5 | 115 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
314560 | 3CNETO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00204 |  |  | 0 |  | 1 | NEWENERGY
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 0 |  |  | -0.00205 |  |  | 0 |  | 1 | NEWENERGY | K11
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 443.98 |  |  | -0.00205 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM2
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 440.13 |  |  | -0.00205 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 419.81 |  |  | -0.00205 |  |  | 0.10478 |  | 1 | CAPACITY
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 404.48 |  |  | -0.00205 |  |  | 0.0316 |  | 1 | CAPACITY
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 403.68 |  |  | -0.00205 |  |  | 0.0316 |  | 1 | CAPACITY
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 403.27 |  |  | -0.00205 |  |  | 0.0316 |  | 1 | CAPACITY
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 403.2 |  |  | -0.00205 |  |  | 0.0316 |  | 1 | CAPACITY
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00205 |  |  | 0.0316 |  | 1 | CAPACITY
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00205 |  |  | 0.0316 |  | 1 | CAPACITY
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 0 |  |  | -0.00206 |  |  | 0 |  | 1 | NEWENERGY | AC1-075
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 30.75 |  |  | -0.00206 |  |  | 0 |  | 1 | CAPACITY | AC1-075
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 30.67 |  |  | -0.00205 |  |  | 0 |  | 1 | CAPACITY | K11
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 0 |  |  | -0.00206 |  |  | 0 |  | 1 | NEWENERGY | AC1-080
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00206 |  |  | 0 |  | 1 | NEWENERGY | Y2-081
926023 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 10.28 |  |  | -0.00206 |  |  | 0 |  | 1 | CAPACITY | AC1-080
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 9.55 |  |  | -0.00205 |  |  | 0.08446 |  | 1 | CAPACITY
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.00206 |  |  | 0 |  | 1 | CAPACITY | Y2-081
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 68.3 |  |  |  | -0.0021
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 106.94 |  |  | -0.00206 |  |  | 0.07484 |  | 1 | CAPACITY
208904 | HOLT 696 | 13.2 | 229 | 60 | 23 | 58.4 | 46.89 |  |  | -0.00206 |  |  | 0.07484 |  | 1 | CAPACITY
244012 | 05PINNACLE | 4 | 205 | 1 | 0 | 11 | 0 |  |  | -0.00207 |  |  | 0.10478 |  | 1 | ENERGY
208903 | HOLT 695 | 13.2 | 229 | 60 | 26 | 53.2 | 42.71 |  |  | -0.00206 |  |  | 0.07484 |  | 1 | CAPACITY
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 42.07 |  |  | -0.00207 |  |  | 0.10478 |  | 1 | CAPACITY
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 23.68 |  |  | -0.00206 |  |  | 0.12623 |  | 1 | CAPACITY
919535 | V4-027 E | 0 | 229 | 75 | 0 | 3.1 | 0 |  |  | -0.00206 |  |  | 0 |  | 1 | NEWENERGY | V4-027
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 3.93 |  |  | -0.00206 |  |  | 0 |  | 1 | CAPACITY | V4-027
208474 | KINZ 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00206 |  |  | 0 |  | 1 | CAPACITY
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 1044 |  |  |  | -0.0021
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 154.95 |  |  | -0.00207 |  |  | 0.0316 |  | 1 | CAPACITY
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 152.54 |  |  | -0.00207 |  |  | 0.0316 |  | 1 | CAPACITY
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00207 |  |  | 0 |  | 1 | NEWENERGY | AC1-145
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 97.14 |  |  | -0.00207 |  |  | 0.0316 |  | 1 | CAPACITY
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 59.41 |  |  | -0.00207 |  |  | 0.0316 |  | 1 | CAPACITY
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 57 |  |  | -0.00207 |  |  | 0.0316 |  | 1 | CAPACITY
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.9 | 40.06 |  |  | -0.00207 |  |  | 0.07484 |  | 1 | CAPACITY
926645 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.00207 |  |  | 0 |  | 1 | CAPACITY | AC1-145
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 3.21 |  |  | -0.00208 |  |  | 0 |  | 1 | CAPACITY
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEWENERGY | U2-073 A
235520 | 01WVACO_S38 | 13.8 | 201 | 2 | 0 | 60 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEW
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEWENERGY | U2-073 B
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 144.51 |  |  | -0.00208 |  |  | 0.10478 |  | 1 | CAPACITY
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00208 |  |  | 0 |  | 1 | NEWENERGY | AC1-117
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEWENERGY | AD1-018
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | -0.00208 |  |  | 0.05 |  | 1 | MTX | AA1-100
926461 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00208 |  |  | 0 |  | 1 | NEW | AC1-117
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEW | AD1-018
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00209 |  |  | 0.07484 |  | 1 | CAPACITY
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00209 |  |  | 0.07484 |  | 1 | CAPACITY
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 25.9 | 20.79 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | U2-073 A
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | U2-073 B
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | N47
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 6.42 |  |  | -0.00208 |  |  | 0 |  | 1 | CAPACITY
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEWENERGY | Y1-006
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEWENERGY | S14
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEWENERGY | U2-030
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEWENERGY | AC1-048
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEW | AC1-048
205910 | AC2-053 E | 0.39 | 227 | 74 | 0 | 12.4 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEWENERGY | AC2-053
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.0021 |  |  | 0.08446 |  | 1 | CAPACITY
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.0021 |  |  | 0.08446 |  | 1 | CAPACITY
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.0021 |  |  | 0.08446 |  | 1 | CAPACITY
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.0021 |  |  | 0.08446 |  | 1 | CAPACITY
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.0021 |  |  | 0.08446 |  | 1 | CAPACITY
913034 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEW | Y1-006
242677 | 05INDDRV | 138 | 205 | 64 | 0 | 45 | 36.13 |  |  | -0.0021 |  |  | 0.12623 |  | 1 | CAPACITY
205909 | AC2-053 C | 0.39 | 227 | 74 | 0 | 7.6 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEW | AC2-053
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | -0.00209 |  |  | 0.07484 |  | 1 | ENERGY
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | MTX | AD2-205
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 14.1 | 11.32 |  |  | -0.00209 |  |  | 0.07484 |  | 1 | CAPACITY
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 11.24 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | S14
923771 | AB2-011 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.0021 |  |  | 0 |  | 1 | NEW | AB2-011
923761 | AB2-010 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.0021 |  |  | 0 |  | 1 | NEW | AB2-010
923762 | AB2-010 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.0021 |  |  | 0 |  | 1 | NEWENERGY | AB2-010
923772 | AB2-011 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.0021 |  |  | 0 |  | 1 | NEWENERGY | AB2-011
270148 | AE1-018 E | 138 | 205 | 75 | 0 | 2.2 | 0 |  |  | -0.00209 |  |  | 0 |  | 1 | NEWENERGY | AE1-018
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.7 | 7.79 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 6.26 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | U2-030
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 3.29 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY
270147 | AE1-018 C | 138 | 205 | 75 | 0 | 2.8 | 2.25 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | AE1-018
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 896 |  |  |  | -0.0021
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  |  |  | -0.0021
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  |  |  | -0.0021
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 489.98 |  |  | -0.0021 |  |  | 0.10478 |  | 1 | CAPACITY
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | NEWENERGY | K28
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 180.64 |  |  | -0.00211 |  |  | 0.10478 |  | 1 | CAPACITY
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 38 |  |  |  | -0.0021
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 127.4 | 102.28 |  |  | -0.0021 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 101.08 |  |  | -0.0021 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | NEWENERGY | K28
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 93.13 |  |  | -0.00211 |  |  | 0.10478 |  | 1 | CAPACITY
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 91.93 |  |  | -0.00211 |  |  | 0.07484 |  | 1 | CAPACITY
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 106.7 | 85.67 |  |  | -0.0021 |  |  | 0 |  | 1 | CAPACITY
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 84.78 |  |  | -0.0021 |  |  | 0 |  | 1 | CAPACITY
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 64.23 |  |  | -0.00211 |  |  | 0.07484 |  | 1 | CAPACITY
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 61.42 |  |  | -0.00211 |  |  | 0.07484 |  | 1 | CAPACITY
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 56.2 |  |  | -0.00211 |  |  | 0.07484 |  | 1 | CAPACITY
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.4 | 13.97 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY | K28
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00211 |  |  | 0.07484 |  | 1 | CAPACITY
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY
342070 | 2PINE GROVE | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 1.3 | 1.04 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY
342442 | 2W GLASGOW | 69 | 320 | 2 | 0 | 1 | 0.8 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY
237085 | AD2-192 GEN | 23 | 201 | 57 | 0 | 600 | 0 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | NEW
293798 | W4-005 E | 0.69 | 222 | 74 | 0 | 305.37 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | W4-005
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1396 | 1120.79 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | GVG2
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1371 | 1100.72 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | GVG1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1088.67 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | RKG1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1356 | 1088.67 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | MTG1
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1067.8 |  |  | -0.00211 |  |  | 0.10478 |  | 1 | CAPACITY | AMG3
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1043.71 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | RKG2
274656 | BYRON ;1U | 25 | 222 | 45 | 700 | 1168.5 | 938.14 |  |  | -0.00212 |  |  | 0.01494 |  | 1 | CAPACITY
274657 | BYRON ;2U | 25 | 222 | 45 | 700 | 1141.5 | 916.46 |  |  | -0.00212 |  |  | 0.01494 |  | 1 | CAPACITY
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 200 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | Q57
918472 | AA1-062 E | 138 | 201 | 74 | 0 | 195 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | NEWENERGY | AA1-062
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | X2-022
274663 | QUAD CITI;2U | 18 | 222 | 48 | 150 | 911.7 | 731.97 |  |  | -0.00212 |  |  | 0.01494 |  | 1 | CAPACITY
274662 | QUAD CITI;1U | 18 | 222 | 48 | 150 | 911.1 | 731.48 |  |  | -0.00212 |  |  | 0.01494 |  | 1 | CAPACITY
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | Z2-087
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  |  |  | -0.0021
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | S28
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | S27
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 642.29 |  |  | -0.00211 |  |  | 0.10478 |  | 1 | CAPACITY
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 642.29 |  |  | -0.00211 |  |  | 0.10478 |  | 1 | CAPACITY
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 570.03 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
235587 | 01HARRN3 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
235586 | 01HARRN2 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
235585 | 01HARRN1 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 124 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | ENERGY | L05_CE22
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 443.18 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 437.96 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 409.46 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | P36 2
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | P36 1
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AC1-089
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | O29 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | P26
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | NEWENERGY | P59
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | NEWENERGY | M24
293516 | O-009 E1 | 0.69 | 222 | 74 | 0 | 82.04 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | O09 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | P11 2
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | P11 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | P46
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | W2-048
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 62.8 |  |  |  | -0.0021
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 244.87 |  |  | -0.00211 |  |  | 0.10478 |  | 1 | CAPACITY
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | O35
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 240.86 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | O29 2
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | NQ71
293518 | O-009 E3 | 0.57 | 222 | 74 | 0 | 45.89 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | O09 3
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 45.5 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | Z1-073
916211 | Z1-072 E | 0.6 | 222 | 74 | 0 | 44.8 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | Z1-072
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | O29 3
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | NEWENERGY | AB1-150
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | NEWENERGY | U2-061
293517 | O-009 E2 | 0.6 | 222 | 74 | 0 | 41.67 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | O09 2
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00211 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 1
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00211 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 2
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 144.51 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
247225 | 05FTHLG2 | 18 | 205 | 57 | 120 | 173.8 | 139.54 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
247224 | 05FTHLG1 | 18 | 205 | 57 | 120 | 173.7 | 139.46 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
247231 | 05RIVRG2 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
247232 | 05RIVRG3 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
247230 | 05RIVRG1 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 136.16 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | NELSON
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 135.12 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | NELSON
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 134.32 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 134.16 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | -0.00211 |  |  | 0.05 |  | 1 | MTX | M24 BAT
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | CORDOVA
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 31.5 |  |  |  | -0.0021
919221 | AA1-146 | 345 | 222 | 58 | 0 | 157 | 126.05 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
292981 | N-007 E | 138 | 201 | 74 | 0 | 30.4 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | NEWENERGY | N07
235801 | 01WM_AA1_062 | 138 | 201 | 74 | 0 | 29 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | NEW | AA1-062
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | CLIF4
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | CLIF1
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | CLIF3
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF2
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | CLIF5
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | CLIF6
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 99.47 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | NELSON
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 98.59 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | NELSON
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | NQ72
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 109.5 | 87.91 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
920072 | AA2-103 E | 138 | 201 | 76 | -20 | 20 | 0 |  |  | -0.00211 |  |  | 0.05 |  | 1 | MTX | AA2-103
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00212 |  |  | 0.05 |  | 1 | MTX | AA2-123
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 133.1 | 153 | 133.28 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 129.7 | 149.1 | 129.88 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 77.88 |  |  | -0.00211 |  |  | 0.07484 |  | 1 | CAPACITY
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 128.6 | 147.8 | 128.75 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 67.52 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 60.94 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 60.78 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 60.7 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 60.53 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF6
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF3
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF1
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | CLIF2
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF4
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF5
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 72.9 | 58.53 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 72.6 | 58.29 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 52.91 |  |  | -0.00212 |  |  | 0.07484 |  | 1 | CAPACITY
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 51.78 |  |  | -0.00211 |  |  | 0.07484 |  | 1 | CAPACITY
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 51.38 |  |  | -0.00211 |  |  | 0.07484 |  | 1 | CAPACITY
926103 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 45.76 |  |  | -0.00212 |  |  | 0.05 |  | 1 | NEW | AC1-089
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 55 | 44.16 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | -0.0021
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00211 |  |  | 0.08446 |  | 1 | CAPACITY
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 36.93 |  |  | -0.00212 |  |  | 0.07484 |  | 1 | CAPACITY
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 36.61 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | W4-005
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Q57
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 28.74 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | S28
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00212 |  |  | 0.07484 |  | 1 | CAPACITY
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00212 |  |  | 0.07484 |  | 1 | CAPACITY
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00212 |  |  | 0.07484 |  | 1 | CAPACITY
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 27.94 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | S27
925972 | AC1-073 E | 138 | 201 | 74 | 0 | 5.9 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | NEWENERGY | AC1-073
925971 | AC1-073 C | 138 | 201 | 74 | 0 | 5.8 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | NEW | AC1-073
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 21.68 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | L05_CE22
274889 | BRIGHTSTK;1U | 0.7 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Z2-087
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 20.07 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | O29 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 17.58 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | P26
293513 | O-009 C1 | 0.69 | 222 | 74 | 0 | 20.5 | 16.46 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | O09 1
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | P11 2
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | P11 1
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 15.58 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | P46
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | P36 2
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | P36 1
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY | M24
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 11.88 |  |  | -0.00211 |  |  | 0.07484 |  | 1 | CAPACITY
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00211 |  |  | 0.07484 |  | 1 | CAPACITY
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Z1-073
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 9.64 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | O29 2
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 9.39 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY | P59
293515 | O-009 C3 | 0.57 | 222 | 74 | 0 | 11.5 | 9.23 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | O09 3
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 8.91 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | O29 3
293514 | O-009 C2 | 0.6 | 222 | 74 | 0 | 10.4 | 8.35 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | O09 2
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 10.3 | 8.27 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | O35
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | -0.00211 |  |  | 0 |  | 1 | MTX | AB1-055
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 10 | 8.03 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Z1-072
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.6 | 7.71 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY | K19
235000 | N-007 C | 138 | 201 | 74 | 0 | 7.6 | 6.1 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY | N07
295108 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 5.7 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | NQ71
931011 | AB1-150 C | 138 | 201 | 74 | 0 | 6.7 | 5.38 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY | AB1-150
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 5.22 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY | U2-061
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
342550 | 4BAVARIAN LF | 138 | 320 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
341584 | 2GRIFFIN | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
295110 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 2.57 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | NQ72
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.55 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY
341329 | 2COLESBURG | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00211 |  |  | 0 |  | 1 | CAPACITY
342031 | 2PACTOLUS | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
341200 | 2BROMLEYEK | 69 | 320 | 2 | 0 | 2 | 1.61 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1402 |  |  |  | -0.0021
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | U2-072
247919 | U2-041 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | U2-041
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 949.78 |  |  | -0.00212 |  |  | 0.01494 |  | 1 | CAPACITY
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 926.5 |  |  | -0.00212 |  |  | 0.01494 |  | 1 | CAPACITY
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1148 | 921.68 |  |  | -0.00212 |  |  | 0.01494 |  | 1 | CAPACITY
274661 | LASCO STA;2U | 25 | 222 | 49 | 150 | 1135.9 | 911.97 |  |  | -0.00212 |  |  | 0.01494 |  | 1 | CAPACITY
274660 | LASCO STA;1U | 25 | 222 | 49 | 150 | 1131.2 | 908.19 |  |  | -0.00212 |  |  | 0.01494 |  | 1 | CAPACITY
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 814.5 |  |  | -0.00212 |  |  | 0.01494 |  | 1 | CAPACITY
274658 | DRESDEN ;2U | 18 | 222 | 48 | 150 | 902.5 | 724.58 |  |  | -0.00212 |  |  | 0.01494 |  | 1 | CAPACITY
274659 | DRESDEN ;3U | 18 | 222 | 48 | 150 | 895.5 | 718.96 |  |  | -0.00212 |  |  | 0.01494 |  | 1 | CAPACITY
930042 | AB1-006 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AB1-006
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | U3-002 2
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | V3-007
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | U2-090
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | O50
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 159.7 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | S06
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | Q01 3
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | O22 2
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | P10
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 589.3 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | ZIMM
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | S37
293799 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | S36
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AA1-018
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | Q01 4
253314 | AC1-085 A_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 A
253317 | AC1-085 B_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 B
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 120.8 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | R49
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | O51 1
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | O51 2
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | N15
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | T131
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 470.47 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | ZIMM
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AC2-176
927091 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-204
927093 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AC1-204
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 415.88 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 415.88 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
274687 | WILL CNTY;4U | 20 | 222 | 15 | 0 | 510 | 409.46 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | WILL4
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | S71
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 94.4 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | R60 3
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | R60 1
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | R60 2
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | V1-011
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | Q01 21
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 81.6 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | O22 1
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | T126 2
247943 | T-127 E | 0.74 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | T127 5
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | T127 4
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | T126 3
247903 | 05FR-22G E | 0.69 | 205 | 75 | 0 | 78.8 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | Q01 22
247900 | 05FR-11G E | 0.6 | 205 | 75 | 0 | 78.3 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | Q01 11
930062 | AB1-014 E | 138 | 212 | 75 | 0 | 77.5 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AB1-014
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 522.66 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | Q01 12
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-116
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AA2-116
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 284.53 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK8
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 268.96 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | AC1-173
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 267.35 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AA2-116
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 263.34 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK7
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-169
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 294 | 236.04 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-079
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 225.6 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 201.52 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | X2-052
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 193.49 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | X2-052
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | X2-052
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AB1-169
247529 | 05COVRT2 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00213 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 2
247530 | 05COVRT3 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00213 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 3
247528 | 05COVRT1 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00213 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 1
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 219 | 175.82 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Z1-079
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 162.9 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247506 | U2-041 C | 345 | 205 | 74 | 0 | 39 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | U2-041
274708 | KENDALL ;3C | 18 | 222 | 58 | 140 | 184.3 | 147.97 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 3
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 146.36 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 2
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 146.36 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 138 | 182.3 | 146.36 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 4
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00213 |  |  | 0.08446 |  | 1 | CAPACITY
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00213 |  |  | 0.08446 |  | 1 | CAPACITY
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 1
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 2
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 132.47 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 131.75 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 130.06 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AC2-067
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00213 |  |  | 0.08446 |  | 1 | CAPACITY
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00213 |  |  | 0.08446 |  | 1 | CAPACITY
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 120.19 |  |  | -0.00213 |  |  | 0.08446 |  | 1 | CAPACITY
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | ENERGY
247533 | 05COVRT6 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | Covert 3
247531 | 05COVRT4 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | Covert 1
247532 | 05COVRT5 | 16.5 | 205 | 58 | 90 | 131.2 | 105.33 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | Covert 2
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 99.72 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | KYG1
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | KYG4
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | KYG3
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | KYG5
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | KYG2
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 97.87 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Kendall 1
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 97.87 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Kendall 2
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 97.87 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Kendall 4
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 97.87 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Kendall 3
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 96.42 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 115.4 | 92.65 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | EQUISTAR MORRIS
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 75.6 | 104 | 83.5 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 72.7 | 101.6 | 81.57 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00212 |  |  | 0.05 |  | 1 | MTX | Z1-108
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00212 |  |  | 0.05 |  | 1 | MTX | Z1-107
276592 | O-012 C | 138 | 222 | 64 | 0 | 20 | 0 |  |  | -0.00212 |  |  | 0.12623 |  | 1 | ENERGY
902531 | W2-040 C | 69 | 209 | 75 | 0 | 20 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEW | W2-040
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 80.93 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 71.2 | 100.6 | 80.77 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 80.69 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 80.21 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
243415 | 05WWVSTA | 69 | 205 | 61 | 60 | 96 | 77.08 |  |  | -0.00212 |  |  | 0.07484 |  | 1 | CAPACITY
927184 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -0.00213 |  |  | 0.05 |  | 1 | MTX | AC1-212
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AC1-166
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AC1-165
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00213 |  |  | 0.08446 |  | 1 | CAPACITY
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00213 |  |  | 0.08446 |  | 1 | CAPACITY
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00213 |  |  | 0.08446 |  | 1 | CAPACITY
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 65.51 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 81.5 | 65.43 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 65.03 |  |  | -0.00213 |  |  | 0.08446 |  | 1 | CAPACITY
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.8 | 64.87 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AC1-068
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | AC1-069
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 64.31 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 64.23 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 64.23 |  |  | -0.00213 |  |  | 0.08446 |  | 1 | CAPACITY
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 63.43 |  |  | -0.00213 |  |  | 0.08446 |  | 1 | CAPACITY
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 62.14 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
250166 | HLCRST AB114 | 138 | 212 | 75 | 0 | 76 | 61.02 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AB1-014
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AC1-085 B
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AC1-085 A
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 58.77 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 58.45 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | KYG1
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | KYG4
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00212 |  |  | 0.10478 |  | 1 | CAPACITY | KYG2
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | KYG3
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | KYG5
251955 | 08MADSN4 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
251958 | 08MADSN7 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
251953 | 08MADSN2 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
251956 | 08MADSN5 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
251952 | 08MADSN1 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
251959 | 08MADSN8 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
251957 | 08MADSN6 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
251954 | 08MADSN3 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 56.84 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 55.4 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
902532 | W2-040 E | 69 | 209 | 75 | 0 | 12.4 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | W2-040
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | V3-028
251828 | CLNTESP1 | 34.5 | 212 | 76 | 0 | 12 | 0 |  |  | -0.00212 |  |  | 0.05 |  | 1 | MTX | Z1-080
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 48.09 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 47.93 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 46.65 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 46.41 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 43.03 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00212 |  |  | 0.05 |  | 1 | MTX | Z1-106
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00212 |  |  | 0.05 |  | 1 | MTX | Z1-106
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 40.54 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | MIDDLETOWN COKE
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 37.49 |  |  | -0.00212 |  |  | 0.07484 |  | 1 | CAPACITY
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | O50
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 31.31 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | U2-072
247549 | V3-028 C | 345 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | V3-028
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 28.18 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | O22 2
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | S36
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | S37
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AC1-068
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AC1-069
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AC1-166
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AC1-165
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 42.68 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 42.6 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 42.51 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
932312 | AC2-045 E | 69 | 205 | 75 | 0 | 6.2 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | AC2-045
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -0.00212 |  |  | 0.05 |  | 1 | MTX | Z1-065
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 24.08 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247521 | T131 | 0.69 | 205 | 74 | 22.4 | 30 | 24.08 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | T131
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 23.36 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Q01 4
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | X3-005
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 20.3 | 27.6 | 22.16 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 22 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | N15
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 21.28 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AC2-067
930041 | AB1-006 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AB1-006
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | U2-090
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | V3-007
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 20.79 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | S06
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 20.63 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Q01 11
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 19.27 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | S71
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 18.39 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | R49
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | O51 2
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | O51 1
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00213 |  |  | 0.07484 |  | 1 | CAPACITY
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00213 |  |  | 0.07484 |  | 1 | CAPACITY
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | MTX
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 16.22 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | T127 5
274891 | OTTER CRK;1U | 0.69 | 222 | 74 | 0 | 19.5 | 15.66 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AA1-018
932311 | AC2-045 C | 69 | 205 | 75 | 0 | 3.8 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEW | AC2-045
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 14.77 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | O22 1
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 22.91 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
933594 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 13.57 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | AC2-176
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 13.25 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | R60 3
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | R60 1
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | R60 2
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 12.28 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | T126 3
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | T126 2
276173 | Z2-081 | 138 | 222 | 2 | 0 | 13.3 | 10.68 |  |  | -0.00212 |  |  | 0.12623 |  | 1 | CAPACITY
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 10.6 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | U3-002 1
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Q01 22
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Q01 21
247607 | V1-011 C | 34.5 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | V1-011
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 10.36 |  |  | -0.00212 |  |  | 0.08446 |  | 1 | CAPACITY
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 10.28 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | U3-002 2
208769 | SISO | 12.5 | 229 | 2 | 0 | 2.48 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | ENERGY
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Q01 12
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Q01 3
904211 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 9.71 |  |  | -0.00212 |  |  | 0.07484 |  | 1 | CAPACITY
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00212 |  |  | 0.12623 |  | 1 | CAPACITY
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00213 |  |  | 0.12623 |  | 1 | CAPACITY
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 9.47 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | T127 4
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | Z2-113
294740 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | ENERGY
904201 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 8.51 |  |  | -0.00212 |  |  | 0.07484 |  | 1 | CAPACITY
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 8.19 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | P10
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | MTX | Y3-100
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | MTX | Y3-099
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 8.03 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
926865 | AC1-173 C | 0.65 | 205 | 75 | 0 | 9.9 | 7.95 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | AC1-173
903052 | W2-094 E | 115 | 227 | 75 | 0 | 1.9 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | W2-094
AC1-212 | BATTERY_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | -0.0021
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | V4-073
247969 | Z2-116 E | 138 | 205 | 76 | 0 | 1.3 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | Z2-116
247968 | Z2-115 E | 12 | 205 | 74 | 0 | 1.25 | 0 |  |  | -0.00212 |  |  | 0 |  | 1 | NEWENERGY | Z2-115
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 4.82 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
276159 | W4-082 | 138 | 222 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
205911 | 27W2-094 | 115 | 227 | 75 | 0 | 1.1 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | W2-094
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 3.13 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 2.73 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | X3-005
208876 | WLAN | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
247604 | X1-042 | 12 | 205 | 64 | 0 | 3 | 2.41 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.8 | 2.25 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 2.09 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 1.85 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | Z2-113
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.76 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
927183 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.53 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | AC1-212
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.5 | 1.2 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Z2-116
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 1 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | Z2-115
904721 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | V4-073
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 618.28 |  |  | -0.00213 |  |  | 0.10478 |  | 1 | CAPACITY
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 533.66 |  |  | -0.00213 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-173
893022 | V2-006 E | 138 | 205 | 74 | 0 | 130.5 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | V2-006
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | AB2-067
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00213 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-044
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00213 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-067
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 292.88 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 318.8 | 255.95 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | RONCO
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 238.45 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 225.4 | 180.96 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | U1-059
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00213 |  |  | 0.04435 |  | 1 | CAPACITY | WASHINGTON
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | RONCO
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00213 |  |  | 0.04435 |  | 1 | CAPACITY | RONCO
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.00213 |  |  | 0.04435 |  | 1 | CAPACITY | DRESDEN
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00213 |  |  | 0.04435 |  | 1 | CAPACITY | WATERFORD
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.00214 |  |  | 0.08446 |  | 1 | CAPACITY
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.00214 |  |  | 0.08446 |  | 1 | CAPACITY
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.66 | 96.07 |  |  | -0.00214 |  |  | 0.08446 |  | 1 | CAPACITY
893021 | V2-006 C | 138 | 205 | 74 | 0 | 19.5 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | V2-006
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | W1-056
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | U1-059
930262 | AB1-065 E | 34.5 | 201 | 75 | 0 | 6.8 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00214 |  |  | 0.07484 |  | 1 | CAPACITY
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00214 |  |  | 0.07484 |  | 1 | CAPACITY
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 17.66 |  |  | -0.00214 |  |  | 0.08446 |  | 1 | CAPACITY
235013 | 01AB1-065 C | 34.5 | 201 | 75 | 0 | 4.1 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 10.19 |  |  | -0.00214 |  |  | 0.10478 |  | 1 | CAPACITY
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 8.83 |  |  | -0.00214 |  |  | 0.10478 |  | 1 | CAPACITY
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY
245413 | 05S FULTHA | 69 | 205 | 65 | 0 | 0.85 | 0 |  |  | -0.00213 |  |  | 0 |  | 1 | ENERGY
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.93 |  |  | -0.00213 |  |  | 0 |  | 1 | CAPACITY | W1-056
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | -0.00215 |  |  | 0 |  | 1 | NEW | AB1-069
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00215 |  |  | 0 |  | 1 | NEW | AB1-069
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00215 |  |  | 0.04435 |  | 1 | NEW | AB1-069
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00214 |  |  | 0 |  | 1 | NEWENERGY | V4-010
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 634.42 |  |  | -0.00214 |  |  | 0.10478 |  | 1 | CAPACITY
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 780.51 |  |  | -0.00215 |  |  | 0.01494 |  | 1 | CAPACITY
924440 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 389.39 |  |  | -0.00215 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-093
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00214 |  |  | 0 |  | 1 | NEWENERGY | U4-028
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00214 |  |  | 0 |  | 1 | NEWENERGY | U4-029
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 364.2 | 292.4 |  |  | -0.00215 |  |  | 0 |  | 1 | CAPACITY | FREMONT
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 261.89 |  |  | -0.00214 |  |  | 0 |  | 1 | CAPACITY | OREGON
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 248.73 |  |  | -0.00214 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00214 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00214 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-107
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00214 |  |  | 0.04435 |  | 1 | CAPACITY | OREGON
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00214 |  |  | 0 |  | 1 | CAPACITY | OREGON
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 170 | 136.49 |  |  | -0.00215 |  |  | 0.04435 |  | 1 | CAPACITY | FREMONT
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 166.4 | 133.6 |  |  | -0.00215 |  |  | 0 |  | 1 | CAPACITY | FREMONT
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00214 |  |  | 0.10478 |  | 1 | CAPACITY
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00214 |  |  | 0.08446 |  | 1 | CAPACITY
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00214 |  |  | 0.08446 |  | 1 | CAPACITY
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00214 |  |  | 0.10478 |  | 1 | CAPACITY
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 109.19 |  |  | -0.00214 |  |  | 0.10478 |  | 1 | CAPACITY
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 0 |  |  | -0.00214 |  |  | 0 |  | 1 | NEW | V4-010
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 0 |  |  | -0.00214 |  |  | 0 |  | 1 | NEWENERGY
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 60 | 48.17 |  |  | -0.00215 |  |  | 0.08446 |  | 1 | CAPACITY
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00214 |  |  | 0.08446 |  | 1 | CAPACITY
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00214 |  |  | 0.08446 |  | 1 | CAPACITY
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 19.5 | 15.66 |  |  | -0.00214 |  |  | 0.08446 |  | 1 | CAPACITY
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 15.25 |  |  | -0.00214 |  |  | 0.07484 |  | 1 | CAPACITY
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 10.68 |  |  | -0.00214 |  |  | 0.10478 |  | 1 | CAPACITY
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00214 |  |  | 0 |  | 1 | NEW | U4-028
247552 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00214 |  |  | 0 |  | 1 | NEW | U4-029
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 4.41 |  |  | -0.00215 |  |  | 0 |  | 1 | CAPACITY | N32
936011 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 16.06 |  |  | -0.00215 |  |  | 0.10478 |  | 1 | CAPACITY
209030 | FRFA O01 | 12.5 | 229 | 2 | 0 | 3.2 | 0 |  |  | -0.00215 |  |  | 0 |  | 1 | NEW
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 8.03 |  |  | -0.00215 |  |  | 0 |  | 1 | CAPACITY
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 7.95 |  |  | -0.00215 |  |  | 0 |  | 1 | CAPACITY
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 1.85 |  |  | -0.00216 |  |  | 0 |  | 1 | CAPACITY
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 0.4 | 0.32 |  |  | -0.00215 |  |  | 0 |  | 1 | CAPACITY | V3-051
237082 | AA2-121 | 345 | 201 | 58 | 0 | 830 | 666.37 |  |  | -0.00217 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-121
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 503.47 |  |  | -0.00217 |  |  | 0.04435 |  | 1 | CAPACITY | AVON LAKE
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 498.09 |  |  | -0.00216 |  |  | 0.10478 |  | 1 | CAPACITY
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00216 |  |  | 0.10478 |  | 1 | CAPACITY
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00216 |  |  | 0.10478 |  | 1 | CAPACITY
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 272 | 218.38 |  |  | -0.00216 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00216 |  |  | 0.04435 |  | 1 | CAPACITY | Y2-050
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00216 |  |  | 0 |  | 1 | CAPACITY | Y2-050
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 62.22 |  |  | -0.00216 |  |  | 0.08446 |  | 1 | CAPACITY
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00216 |  |  | 0.08446 |  | 1 | CAPACITY
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.00216 |  |  | 0.08446 |  | 1 | CAPACITY
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 60.86 |  |  | -0.00216 |  |  | 0.08446 |  | 1 | CAPACITY
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 60.29 |  |  | -0.00216 |  |  | 0.08446 |  | 1 | CAPACITY
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 41.03 |  |  | -0.00216 |  |  | 0.12623 |  | 1 | CAPACITY
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 39.82 |  |  | -0.00216 |  |  | 0.12623 |  | 1 | CAPACITY
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0 |  |  | -0.00217 |  |  | 0 |  | 1 | NEWENERGY | W1-045
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 11.24 |  |  | -0.00216 |  |  | 0.12623 |  | 1 | CAPACITY
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.13 | 4.12 |  |  | -0.00217 |  |  | 0 |  | 1 | CAPACITY | W1-045
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 3.21 |  |  | -0.00217 |  |  | 0 |  | 1 | CAPACITY
253900 | 15BVRVL1 | 22 | 215 | 44 | 843.9 | 970 | 844.97 |  |  | -0.00217 |  |  | 0.01494 |  | 1 | CAPACITY
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00217 |  |  | 0.10478 |  | 1 | CAPACITY
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.00217 |  |  | 0.10478 |  | 1 | CAPACITY
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 783.39 |  |  | -0.00217 |  |  | 0.01494 |  | 1 | CAPACITY
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 455.62 |  |  | -0.00217 |  |  | 0.10478 |  | 1 | CAPACITY
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 329.17 |  |  | -0.00218 |  |  | 0 |  | 1 | CAPACITY | AA1-044
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.00217 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.00217 |  |  | 0 |  | 1 | CAPACITY | AA1-123
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 300.6 | 241.34 |  |  | -0.00218 |  |  | 0 |  | 1 | CAPACITY | Z2-028
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00218 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-044
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00218 |  |  | 0 |  | 1 | CAPACITY | AA1-044
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 233.87 |  |  | -0.00217 |  |  | 0.10478 |  | 1 | CAPACITY
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00218 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-028
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.00218 |  |  | 0 |  | 1 | CAPACITY | Z2-028
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.00217 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-123
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.00217 |  |  | 0 |  | 1 | CAPACITY | AA1-123
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 81.57 |  |  | -0.00217 |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND
253970 | 15BI2 | 13.8 | 215 | 58 | 60 | 96.2 | 77.24 |  |  | -0.00217 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | -0.00218 |  |  | 0.10478 |  | 1 | ENERGY
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.00217 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.00217 |  |  | 0 |  | 1 | CAPACITY | Y3-103
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.7 | 39.1 |  |  | -0.00217 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0 |  |  | -0.00217 |  |  | 0 |  | 1 | NEWENERGY | AC2-168
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00217 |  |  | 0.04435 |  | 1 | CAPACITY | Y3-103
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00217 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.00217 |  |  | 0 |  | 1 | CAPACITY | Y3-103
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 24.6 | 19.75 |  |  | -0.00218 |  |  | 0.12623 |  | 1 | CAPACITY
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 21 | 16.86 |  |  | -0.00217 |  |  | 0.12623 |  | 1 | CAPACITY
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 14.53 |  |  | -0.00217 |  |  | 0.08446 |  | 1 | CAPACITY
933531 | AC2-168 C | 138 | 215 | 75 | 0 | 7.55 | 6.06 |  |  | -0.00217 |  |  | 0 |  | 1 | CAPACITY | AC2-168
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.5 |  |  | -0.00217 |  |  | 0 |  | 1 | CAPACITY
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 3.21 |  |  | -0.00218 |  |  | 0 |  | 1 | CAPACITY
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 261.73 |  |  | -0.00219 |  |  | 0 |  | 1 | CAPACITY | T-174
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00219 |  |  | 0.04435 |  | 1 | CAPACITY | T-174
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.00219 |  |  | 0 |  | 1 | CAPACITY | T-174
239024 | 02NWCAG5 | 16.5 | 202 | 58 | 23 | 141 | 113.2 |  |  | -0.00219 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
239022 | 02NWCAG3 | 14.4 | 202 | 58 | 20 | 92.3 | 74.11 |  |  | -0.00219 |  |  | 0.04435 |  | 1 | CAPACITY | NEW CASTLE
239023 | 02NWCAG4 | 14.4 | 202 | 58 | 20 | 92 | 73.86 |  |  | -0.00219 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 0 |  |  | -0.00218 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 16.46 |  |  | -0.00218 |  |  | 0.12623 |  | 1 | CAPACITY
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 19.6 | 15.74 |  |  | -0.00219 |  |  | 0.08446 |  | 1 | CAPACITY
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 0 |  |  | -0.00218 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 2.01 |  |  | -0.00219 |  |  | 0 |  | 1 | CAPACITY
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 1.37 |  |  | -0.00219 |  |  | 0 |  | 1 | CAPACITY | K20
920571 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 411.86 |  |  | -0.0022 |  |  | 0.04435 |  | 1 | NEW | AA2-161
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 39.5 | 31.71 |  |  | -0.0022 |  |  | 0.08446 |  | 1 | CAPACITY
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1086.27 |  |  | -0.0022 |  |  | 0.01494 |  | 1 | CAPACITY
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 28.1 |  |  | -0.00221 |  |  | 0.10478 |  | 1 | CAPACITY
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.82 |  |  | -0.0022 |  |  | 0 |  | 1 | CAPACITY
913142 | Y1-033 E OP1 | 115 | 226 | 74 | 0 | 34.02 | 0 |  |  | -0.00222 |  |  | 0 |  | 1 | NEWENERGY | Y1-033
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 38.7 | 31.07 |  |  | -0.00222 |  |  | 0.08446 |  | 1 | CAPACITY
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 4.01 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | Y1-033
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 3.05 |  |  | -0.00221 |  |  | 0 |  | 1 | CAPACITY
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 353.26 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00222 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-076
204638 | 27CAT TRAC | 13.2 | 227 | 58 | 0 | 32.3 | 25.93 |  |  | -0.00223 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
204555 | 27QUEEN ST | 115 | 227 | 74 | 0 | 5 | 0 |  |  | -0.00222 |  |  | 0 |  | 1 | NEWENERGY
204706 | 27CAT TRC2 | 13.2 | 227 | 58 | 0 | 13.9 | 11.16 |  |  | -0.00223 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 140 | 182.2 | 146.28 |  |  | -0.00224 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 118.7 | 175.2 | 140.66 |  |  | -0.00224 |  |  | 0.04435 |  | 1 | CAPACITY | AE SPRINGDALE
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 118.7 | 172.2 | 138.25 |  |  | -0.00224 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.00224 |  |  | 0.08446 |  | 1 | CAPACITY
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.00224 |  |  | 0.08446 |  | 1 | CAPACITY
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 24.08 |  |  | -0.00223 |  |  | 0.10478 |  | 1 | CAPACITY
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 5.54 |  |  | -0.00225 |  |  | 0 |  | 1 | CAPACITY
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00226 |  |  | 0 |  | 1 | NEWENERGY | K23
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 0 |  |  | -0.00226 |  |  | 0 |  | 1 | NEWENERGY | L13
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 0 |  |  | -0.00226 |  |  | 0 |  | 1 | NEWENERGY | O48
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | -0.00226 |  |  | 0.05 |  | 1 | MTX
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | -0.00226 |  |  | 0.05 |  | 1 | MTX
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 0 |  |  | -0.00226 |  |  | 0 |  | 1 | NEWENERGY | R40
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 5.06 |  |  | -0.00226 |  |  | 0 |  | 1 | CAPACITY | O48
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 4.74 |  |  | -0.00226 |  |  | 0 |  | 1 | CAPACITY | L13
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 5.1 | 4.09 |  |  | -0.00226 |  |  | 0 |  | 1 | CAPACITY | K23
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 682.91 |  |  | -0.00226 |  |  | 0.10478 |  | 1 | CAPACITY | Cone1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 682.43 |  |  | -0.00226 |  |  | 0.10478 |  | 1 | CAPACITY | Cone2
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 400 | 321.14 |  |  | -0.00227 |  |  | 0.04435 |  | 1 | CAPACITY | AD2-114
235621 | 01SBEND3 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00227 |  |  | 0.08446 |  | 1 | CAPACITY
235620 | 01SBEND2 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00227 |  |  | 0.08446 |  | 1 | CAPACITY
235619 | 01SBEND1 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00227 |  |  | 0.08446 |  | 1 | CAPACITY
235622 | 01SBEND4 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00227 |  |  | 0.08446 |  | 1 | CAPACITY
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 6.1 |  |  | -0.00227 |  |  | 0 |  | 1 | CAPACITY
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 853.3 | 685.08 |  |  | -0.00227 |  |  | 0.10478 |  | 1 | CAPACITY | Keys1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 853.1 | 684.92 |  |  | -0.00227 |  |  | 0.10478 |  | 1 | CAPACITY | Keys2
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 16.55 |  |  | -0.00227 |  |  | 0.07484 |  | 1 | CAPACITY
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 5.46 |  |  | -0.00229 |  |  | 0 |  | 1 | CAPACITY
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00228 |  |  | 0 |  | 1 | CAPACITY
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.45 |  |  | -0.00229 |  |  | 0 |  | 1 | CAPACITY
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.72 |  |  | -0.00229 |  |  | 0 |  | 1 | CAPACITY | K22
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 42 | 0 |  |  | -0.0023 |  |  | 0 |  | 1 | NEWENERGY | P60
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 68.24 |  |  | -0.0023 |  |  | 0.10478 |  | 1 | CAPACITY
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 42.95 |  |  | -0.0023 |  |  | 0.08446 |  | 1 | CAPACITY
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 42.95 |  |  | -0.0023 |  |  | 0.08446 |  | 1 | CAPACITY
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.0023 |  |  | 0.08446 |  | 1 | CAPACITY
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.0023 |  |  | 0.08446 |  | 1 | CAPACITY
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.0023 |  |  | 0.08446 |  | 1 | CAPACITY
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.0023 |  |  | 0.12623 |  | 1 | CAPACITY
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 6.82 |  |  | -0.0023 |  |  | 0 |  | 1 | CAPACITY | P60
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.02 |  |  | -0.0023 |  |  | 0 |  | 1 | CAPACITY
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 23.2 | 0 |  |  | -0.00231 |  |  | 0 |  | 1 | NEWENERGY | K13
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 24.24 |  |  | -0.00231 |  |  | 0.07484 |  | 1 | CAPACITY
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 10.44 |  |  | -0.00231 |  |  | 0.12623 |  | 1 | CAPACITY
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 2.57 |  |  | -0.00231 |  |  | 0 |  | 1 | CAPACITY | K13
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.0023 |  |  | 0 |  | 1 | CAPACITY
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 422.06 |  |  | -0.00231 |  |  | 0.10478 |  | 1 | CAPACITY
903644 | W3-099 E OP1 | 230 | 226 | 74 | 0 | 87 | 0 |  |  | -0.00231 |  |  | 0 |  | 1 | NEWENERGY | W3-099
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 60 | 0 |  |  | -0.00232 |  |  | 0 |  | 1 | NEWENERGY | R32
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 52 | 0 |  |  | -0.00232 |  |  | 0 |  | 1 | NEWENERGY | O18
200805 | 26COLVER13 | 13.2 | 226 | 12 | 77 | 110 | 88.31 |  |  | -0.00232 |  |  | 0.10478 |  | 1 | CAPACITY
201144 | W3-099 C OP1 | 230 | 226 | 74 | 0 | 13 | 0 |  |  | -0.00231 |  |  | 0 |  | 1 | NEW | W3-099
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 10.19 |  |  | -0.00232 |  |  | 0 |  | 1 | CAPACITY | R32
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00231 |  |  | 0.12623 |  | 1 | CAPACITY
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00232 |  |  | 0 |  | 1 | CAPACITY | O18
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 497.77 |  |  | -0.00232 |  |  | 0.10478 |  | 1 | CAPACITY
200809 | 26SITHE | 138 | 226 | 15 | 0 | 36 | 28.9 |  |  | -0.00232 |  |  | 0.10478 |  | 1 | CAPACITY
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 48 | 0 |  |  | -0.00234 |  |  | 0 |  | 1 | NEWENERGY | Q53
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 0 |  |  | -0.00233 |  |  | 0 |  | 1 | NEWENERGY | V3-030
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 5.14 |  |  | -0.00234 |  |  | 0 |  | 1 | CAPACITY | Q53
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 4.25 |  |  | -0.00233 |  |  | 0 |  | 1 | CAPACITY | V3-030
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 521.86 |  |  | -0.00234 |  |  | 0.10478 |  | 1 | CAPACITY
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 492.95 |  |  | -0.00234 |  |  | 0.10478 |  | 1 | CAPACITY
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 0 |  |  | -0.00235 |  |  | 0 |  | 1 | NEWENERGY | N39
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00235 |  |  | 0 |  | 1 | NEWENERGY | O38
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -0.00234 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00235 |  |  | 0 |  | 1 | CAPACITY | N39
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.4 | 7.55 |  |  | -0.00235 |  |  | 0 |  | 1 | CAPACITY | O38
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 601.34 |  |  | -0.00235 |  |  | 0.10478 |  | 1 | CAPACITY
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 293.93 |  |  | -0.00235 |  |  | 0.10478 |  | 1 | CAPACITY | Bris2
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 248.4 |  |  | -0.00235 |  |  | 0.10478 |  | 1 | CAPACITY | Bris1
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 33.72 |  |  | -0.00236 |  |  | 0.04435 |  | 1 | CAPACITY | EAGLE POINT
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 24.08 |  |  | -0.00236 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 57 | 45.76 |  |  | -0.00237 |  |  | 0.08446 |  | 1 | CAPACITY
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -0.00238 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 187.87 |  |  | -0.00239 |  |  | 0.0316 |  | 1 | CAPACITY
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 177.43 |  |  | -0.00239 |  |  | 0.0316 |  | 1 | CAPACITY
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 40 | 0 |  |  | -0.00238 |  |  | 0 |  | 1 | NEWENERGY | Q36
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 26.13 |  |  | -0.00239 |  |  | 0.07484 |  | 1 | CAPACITY
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | -0.00238 |  |  | 0 |  | 1 | ENERGY
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 6.66 |  |  | -0.00238 |  |  | 0 |  | 1 | CAPACITY | Q36
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 16.86 |  |  | -0.00239 |  |  | 0.07484 |  | 1 | CAPACITY
208947 | WSHO CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.0024 |  |  | 0.08446 |  | 1 | CAPACITY
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 33.96 |  |  | -0.00242 |  |  | 0.10478 |  | 1 | CAPACITY
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4.82 |  |  | -0.00242 |  |  | 0 |  | 1 | CAPACITY
208348 | EELI | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00243 |  |  | 0 |  | 1 | CAPACITY
200722 | 26SHAWVL 2 | 18 | 226 | 12 | 62 | 124.7 | 100.12 |  |  | -0.00243 |  |  | 0.10478 |  | 1 | CAPACITY
200715 | 26SHAWVL 1 | 18 | 226 | 12 | 62 | 122 | 97.95 |  |  | -0.00243 |  |  | 0.10478 |  | 1 | CAPACITY
208942 | HARR CT | 12.5 | 229 | 55 | 0 | 42 | 33.72 |  |  | -0.00244 |  |  | 0.08446 |  | 1 | CAPACITY
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 9.64 |  |  | -0.00244 |  |  | 0.12623 |  | 1 | CAPACITY
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 8.19 |  |  | -0.00244 |  |  | 0.10478 |  | 1 | CAPACITY
210022 | LING 2 | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00244 |  |  | 0 |  | 1 | CAPACITY
200665 | 26SHAWVL 3 | 22 | 226 | 12 | 120 | 174.2 | 139.86 |  |  | -0.00245 |  |  | 0.10478 |  | 1 | CAPACITY
200666 | 26SHAWVL 4 | 22 | 226 | 12 | 120 | 171 | 137.29 |  |  | -0.00245 |  |  | 0.10478 |  | 1 | CAPACITY
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 24.08 |  |  | -0.00245 |  |  | 0.10478 |  | 1 | CAPACITY
236828 | 01GRAYMONT | 46 | 201 | 2 | 0 | 4 | 0 |  |  | -0.00245 |  |  | 0 |  | 1 | ENERGY
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | -0.00245 |  |  | 0 |  | 1 | MTX | AC1-025
210319 | WCAR 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00245 |  |  | 0 |  | 1 | CAPACITY
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | -0.00248 |  |  | 0.12623 |  | 1 | ENERGY
208885 | WNHO | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00248 |  |  | 0 |  | 1 | CAPACITY
208697 | PRIN B34 | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00248 |  |  | 0 |  | 1 | CAPACITY
922932 | AB1-082 OP | 46 | 201 | 55 | 0 | 19.9 | 0 |  |  | -0.00249 |  |  | 0.08446 |  | 1 | NEW
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 0 |  |  | -0.00255 |  |  | 0 |  | 1 | NEWENERGY | Z1-069
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00255 |  |  | 0 |  | 1 | CAPACITY | Z1-069
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | -0.00254 |  |  | 0 |  | 1 | ENERGY
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.61 |  |  | -0.00254 |  |  | 0 |  | 1 | CAPACITY
204662 | 27AES GEN1 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00255 |  |  | 0.04435 |  | 1 | CAPACITY | IRONWOOD
204664 | 27AES GEN3 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00255 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204663 | 27AES GEN2 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.00255 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | -0.0026 |  |  | 0 |  | 1 | ENERGY
208580 | MGTN 2 | 12.5 | 229 | 2 | 0 | 4.8 | 3.85 |  |  | -0.0026 |  |  | 0 |  | 1 | CAPACITY
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 19 | 15.25 |  |  | -0.00267 |  |  | 0.08446 |  | 1 | CAPACITY
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 130.87 |  |  | -0.00268 |  |  | 0.04435 |  | 1 | CAPACITY | GRAYS FERRY
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 0 |  |  | -0.00269 |  |  | 0 |  | 1 | NEWENERGY | P47
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00269 |  |  | 0 |  | 1 | NEWENERGY | K02
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.8 | 12.69 |  |  | -0.00269 |  |  | 0 |  | 1 | CAPACITY | P47
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.00271 |  |  | 0.08446 |  | 1 | CAPACITY
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.00271 |  |  | 0.08446 |  | 1 | CAPACITY
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 61.6 | 88.4 | 70.97 |  |  | -0.00271 |  |  | 0.04435 |  | 1 | CAPACITY | LAKEWOOD
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 61.2 | 88.3 | 70.89 |  |  | -0.00271 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 76.92 |  |  | -0.00271 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 17.18 |  |  | -0.00272 |  |  | 0.12623 |  | 1 | CAPACITY
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 16.86 |  |  | -0.00272 |  |  | 0.12623 |  | 1 | CAPACITY
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 16.86 |  |  | -0.00272 |  |  | 0.12623 |  | 1 | CAPACITY
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.00275 |  |  | 0.08446 |  | 1 | CAPACITY
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 389.39 |  |  | -0.00279 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-115
920341 | AA2-132 | 34.5 | 226 | 55 | 0 | 19.9 | 0 |  |  | -0.00278 |  |  | 0.08446 |  | 1 | NEW
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 30.1 | 24.17 |  |  | -0.00279 |  |  | 0.08446 |  | 1 | CAPACITY
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.0028 |  |  | 0 |  | 1 | NEWENERGY | Y2-051
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 4.82 |  |  | -0.0028 |  |  | 0 |  | 1 | CAPACITY
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.0028 |  |  | 0 |  | 1 | CAPACITY | Y2-051
919201 | AA1-144 OP | 230 | 226 | 58 | 0 | 163 | 130.87 |  |  | -0.00282 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-144
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 6 | 4.82 |  |  | -0.00282 |  |  | 0 |  | 1 | CAPACITY
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00282 |  |  | 0 |  | 1 | CAPACITY | X1-109
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00282 |  |  | 0.04435 |  | 1 | CAPACITY | X1-109
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.04 |  |  | -0.00283 |  |  | 0 |  | 1 | CAPACITY
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.00285 |  |  | 0.08446 |  | 1 | CAPACITY
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.00285 |  |  | 0.08446 |  | 1 | CAPACITY
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 64.23 |  |  | -0.00287 |  |  | 0.10478 |  | 1 | CAPACITY
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 152.86 |  |  | -0.00289 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 152.86 |  |  | -0.00289 |  |  | 0.04435 |  | 1 | CAPACITY | ONTELAUNEE
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 139.94 |  |  | -0.00289 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
203932 | AA2-133 GEN | 13.8 | 226 | 55 | 0 | 19.89 | 0 |  |  | -0.00289 |  |  | 0.08446 |  | 1 | NEW
919662 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 |  |  | -0.00294 |  |  | 0.05 |  | 1 | MTX | AA2-048
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.00294 |  |  | 0 |  | 1 | NEWENERGY | W3-079
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.00294 |  |  | 0 |  | 1 | CAPACITY | W3-079
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 317.93 |  |  | -0.00295 |  |  | 0 |  | 1 | CAPACITY | Hummel
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 194.29 |  |  | -0.00295 |  |  | 0 |  | 1 | CAPACITY | Hummel
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.00295 |  |  | 0 |  | 1 | CAPACITY | Hummel
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.00295 |  |  | 0.04435 |  | 1 | CAPACITY | Hummel
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 0 |  |  | -0.00296 |  |  | 0 |  | 1 | NEWENERGY | P28
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | -0.00296 |  |  | 0.10478 |  | 1 | NEW
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 47.37 |  |  | -0.00296 |  |  | 0.10478 |  | 1 | CAPACITY
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00296 |  |  | 0 |  | 1 | CAPACITY | P28
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 17.18 |  |  | -0.00296 |  |  | 0.12623 |  | 1 | CAPACITY
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 900.89 |  |  | -0.00301 |  |  | 0.01494 |  | 1 | CAPACITY
209018 | SUNBIPCT | 12.5 | 229 | 55 | 0 | 36 | 28.9 |  |  | -0.00305 |  |  | 0.08446 |  | 1 | CAPACITY
212345 | PENS | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00305 |  |  | 0 |  | 1 | CAPACITY
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 18.3 | 14.69 |  |  | -0.00308 |  |  | 0.12623 |  | 1 | CAPACITY
212435 | SMIL | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00308 |  |  | 0 |  | 1 | CAPACITY
208948 | WILL CT | 12.5 | 229 | 55 | 0 | 27.4 | 22 |  |  | -0.0031 |  |  | 0.08446 |  | 1 | CAPACITY
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 11.24 |  |  | -0.00309 |  |  | 0.08446 |  | 1 | CAPACITY
212005 | ALWD | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.0031 |  |  | 0 |  | 1 | CAPACITY
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00311 |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00311 |  |  | 0.04435 |  | 1 | CAPACITY | MOXIE PATRIOT
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 22.48 |  |  | -0.00311 |  |  | 0.10478 |  | 1 | CAPACITY
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 608.97 |  |  | -0.00312 |  |  | 0.10478 |  | 1 | CAPACITY
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 608.49 |  |  | -0.00312 |  |  | 0.10478 |  | 1 | CAPACITY
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 34.28 |  |  | -0.00313 |  |  | 0.10478 |  | 1 | CAPACITY
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 26.09 |  |  | -0.00313 |  |  | 0.10478 |  | 1 | CAPACITY
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 6.42 |  |  | -0.00313 |  |  | 0 |  | 1 | CAPACITY
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 4.9 |  |  | -0.00313 |  |  | 0 |  | 1 | CAPACITY
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 69.05 |  |  | -0.00317 |  |  | 0.10478 |  | 1 | CAPACITY
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 65.83 |  |  | -0.00317 |  |  | 0.10478 |  | 1 | CAPACITY
208941 | FISH CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00317 |  |  | 0.08446 |  | 1 | CAPACITY
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.4 | 9.15 |  |  | -0.00317 |  |  | 0 |  | 1 | CAPACITY | Q27
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.81 |  |  | -0.00317 |  |  | 0 |  | 1 | CAPACITY | N14
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 898.96 |  |  | -0.0032 |  |  | 0.01494 |  | 1 | CAPACITY
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1090.36 |  |  | -0.0032 |  |  | 0.01494 |  | 1 | CAPACITY
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00321 |  |  | 0 |  | 1 | CAPACITY | Z2-046
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00321 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-046
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1091.76 |  |  | -0.00322 |  |  | 0.01494 |  | 1 | CAPACITY
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 35.57 |  |  | -0.00325 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 23.44 |  |  | -0.00325 |  |  | 0.04435 |  | 1 | CAPACITY | HUNLOCK
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 39.1 |  |  | -0.00325 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 38.86 |  |  | -0.00325 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00326 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00326 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00326 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00326 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00326 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200044 | BETH CT1 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00326 |  |  | 0.04435 |  | 1 | CAPACITY | BETH1234
200048 | BETH CT5 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00326 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
211375 | BEAC | 69 | 229 | 2 | 0 | 20 | 0 |  |  | -0.00326 |  |  | 0.10478 |  | 1 | ENERGY
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.00326 |  |  | 0.05 |  | 1 | MTX | AB1-182
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 47.77 |  |  | -0.00326 |  |  | 0.08446 |  | 1 | CAPACITY
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 47.21 |  |  | -0.00326 |  |  | 0.08446 |  | 1 | CAPACITY
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.00327 |  |  | 0.08446 |  | 1 | CAPACITY
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 23.76 |  |  | -0.00326 |  |  | 0.08446 |  | 1 | CAPACITY
208944 | JENK CT | 12.5 | 229 | 55 | 0 | 28 | 22.48 |  |  | -0.00326 |  |  | 0.08446 |  | 1 | CAPACITY
208943 | HARW CT | 12.5 | 229 | 55 | 0 | 27.2 | 21.84 |  |  | -0.00326 |  |  | 0.08446 |  | 1 | CAPACITY
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.65 |  |  | -0.00326 |  |  | 0 |  | 1 | CAPACITY | L18
211591 | HARW | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00326 |  |  | 0 |  | 1 | CAPACITY
211374 | AVOC | 12.5 | 229 | 2 | 0 | 17.4 | 13.97 |  |  | -0.00328 |  |  | 0 |  | 1 | CAPACITY
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00331 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G3
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00331 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G2
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.00331 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G1
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 0 |  |  | -0.00331 |  |  | 0 |  | 1 | NEWENERGY | AC1-071
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | -0.00331 |  |  | 0.05 |  | 1 | MTX | Z2-107
209009 | PEIP 2 | 13.8 | 229 | 56 | 0 | 43.7 | 35.08 |  |  | -0.00331 |  |  | 0.08446 |  | 1 | CAPACITY
209010 | PEIP 1 | 13.8 | 229 | 29 | 0 | 26.7 | 21.43 |  |  | -0.00331 |  |  | 0.10478 |  | 1 | CAPACITY
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 7.23 |  |  | -0.00331 |  |  | 0 |  | 1 | CAPACITY | K21
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 7.02 |  |  | -0.00331 |  |  | 0 |  | 1 | NEW | AC1-071
209003 | KSTN IPP | 13.8 | 229 | 65 | 0 | 4.9 | 3.93 |  |  | -0.00331 |  |  | 0 |  | 1 | CAPACITY
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 0 |  |  | -0.00335 |  |  | 0 |  | 1 | NEWENERGY | AA2-017
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 0 |  |  | -0.00335 |  |  | 0 |  | 1 | NEW | AA2-017
208940 | ALLE CT | 12.5 | 229 | 55 | 0 | 56 | 44.96 |  |  | -0.00335 |  |  | 0.08446 |  | 1 | CAPACITY
209007 | NOEN IPP | 13.8 | 229 | 12 | 80 | 111.4 | 89.44 |  |  | -0.00336 |  |  | 0.10478 |  | 1 | CAPACITY
900005 | 28LARRABEE E | 230 | 228 | 74 | 0 | 840 | 0 |  |  | -0.00337 |  |  | 0 |  | 1 | NEWENERGY | OSW_LARRAB
211065 | PSPA IPP | 13.8 | 229 | 75 | 0 | 18.4 | 6.74 |  |  | -0.00338 |  |  | 0 |  | 1 | NEWENERGY | U4-014
206294 | 28LARRABEE C | 230 | 228 | 74 | 0 | 360 | 360 |  |  | -0.00337 |  |  | 0 |  | 1 | CAPACITY | OSW_LARRAB
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00338 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.00343 |  |  | 0 |  | 1 | NEWENERGY | X4-031
208946 | MACR CT | 12.5 | 229 | 55 | 0 | 72 | 57.81 |  |  | -0.00345 |  |  | 0.08446 |  | 1 | CAPACITY
208920 | WLPK | 12.5 | 229 | 60 | 0 | 40.9 | 32.84 |  |  | -0.00345 |  |  | 0.07484 |  | 1 | CAPACITY
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.33 |  |  | -0.00347 |  |  | 0 |  | 1 | CAPACITY
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 152 | 122.03 |  |  | -0.00348 |  |  | 0.08446 |  | 1 | CAPACITY
206341 | 28GIL 8 | 13.8 | 228 | 58 | 69.9 | 90 | 72.26 |  |  | -0.00348 |  |  | 0.04435 |  | 1 | CAPACITY | GILBERT
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 87 | 100 | 87.11 |  |  | -0.00348 |  |  | 0 |  | 1 | CAPACITY | GILBERT
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 85.3 | 98 | 85.37 |  |  | -0.00348 |  |  | 0 |  | 1 | CAPACITY | GILBERT
213798 | MERCK 3 | 13.8 | 230 | 2 | 13 | 35 | 28.1 |  |  | -0.00348 |  |  | 0 |  | 1 | CAPACITY
213797 | MERCK 2 | 13.8 | 230 | 2 | 4 | 25 | 20.07 |  |  | -0.00348 |  |  | 0 |  | 1 | CAPACITY
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 3.29 |  |  | -0.00348 |  |  | 0 |  | 1 | CAPACITY
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00348 |  |  | 0.10478 |  | 1 | CAPACITY
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00348 |  |  | 0.10478 |  | 1 | CAPACITY
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 192.53 |  |  | -0.00348 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 160.57 |  |  | -0.00348 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 160.57 |  |  | -0.00348 |  |  | 0.04435 |  | 1 | CAPACITY | LOWER MT BETHEL
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0 |  |  | -0.0035 |  |  | 0 |  | 1 | NEWENERGY | X1-037
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 3.37 |  |  | -0.0035 |  |  | 0 |  | 1 | CAPACITY | X1-037
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 120 |  |  |  | -0.0035
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00354 |  |  | 0 |  | 1 | NEWENERGY | W4-073
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00353 |  |  | 0 |  | 1 | NEWENERGY | W1-127
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.00354 |  |  | 0 |  | 1 | CAPACITY
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0 |  |  | -0.00353 |  |  | 0 |  | 1 | NEWENERGY | U2-059
925462 | AC1-018 E | 34.5 | 228 | 75 | 0 | 0.9 | 0 |  |  | -0.00353 |  |  | 0 |  | 1 | NEWENERGY | AC1-018
925461 | AC1-018 C | 34.5 | 228 | 75 | 0 | 0.5 | 0 |  |  | -0.00353 |  |  | 0 |  | 1 | NEW | AC1-018
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00353 |  |  | 0 |  | 1 | CAPACITY | W1-127
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00353 |  |  | 0 |  | 1 | CAPACITY | U2-059
207402 | 28AA2-082 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.00354 |  |  | 0.05 |  | 1 | MTX | AA2-082
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0 |  |  | -0.00355 |  |  | 0 |  | 1 | NEWENERGY | AD2-070
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 20 | 16.06 |  |  | -0.00355 |  |  | 0.08446 |  | 1 | CAPACITY
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 4 | 3.21 |  |  | -0.00355 |  |  | 0 |  | 1 | CAPACITY
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00355 |  |  | 0 |  | 1 | CAPACITY | AD2-070
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00355 |  |  | 0 |  | 1 | NEWENERGY | W4-097
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00355 |  |  | 0 |  | 1 | CAPACITY | W4-097
204651 | 27PORT CT | 13.8 | 227 | 56 | 4 | 35 | 28.1 |  |  | -0.00358 |  |  | 0.08446 |  | 1 | CAPACITY
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 134 | 107.58 |  |  | -0.0036 |  |  | 0.08446 |  | 1 | CAPACITY
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.00359 |  |  | 0 |  | 1 | NEWENERGY | W3-077
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 5.7 | 4.58 |  |  | -0.00359 |  |  | 0 |  | 1 | CAPACITY | W3-077
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.00359 |  |  | 0 |  | 1 | CAPACITY | W2-091
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.0036 |  |  | 0 |  | 1 | NEWENERGY | W1-124
921743 | AA2-049 E | 34.5 | 228 | 76 | -3 | 3 | 0 |  |  | -0.0036 |  |  | 0 |  | 1 | MTX | AA2-049
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.0036 |  |  | 0 |  | 1 | CAPACITY | W1-124
920732 | AA2-184 E | 34.5 | 228 | 75 | 0 | 20 | 0 |  |  | -0.00361 |  |  | 0 |  | 1 | NEWENERGY | AA2-184
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00365 |  |  | 0.0316 |  | 1 | CAPACITY
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00365 |  |  | 0.0316 |  | 1 | CAPACITY
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00365 |  |  | 0.0316 |  | 1 | CAPACITY
206747 | 28DSM_X3-029 | 34.5 | 228 | 29 | 0 | 11.15 | 0 |  |  | -0.00365 |  |  | 0.10478 |  | 1 | ENERGY
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | -0.00365 |  |  | 0.08446 |  | 1 | ENERGY
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00365 |  |  | 0 |  | 1 | NEWENERGY | Y2-018
206201 | 28JERSVGEN | 34.5 | 228 | 2 | 0 | 2 | 1.61 |  |  | -0.00365 |  |  | 0 |  | 1 | CAPACITY
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 0 |  |  | -0.00368 |  |  | 0 |  | 1 | NEWENERGY | W3-044
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00368 |  |  | 0 |  | 1 | CAPACITY | W3-044
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00369 |  |  | 0 |  | 1 | NEWENERGY | W4-046
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 1.93 |  |  | -0.00369 |  |  | 0 |  | 1 | CAPACITY | W4-046
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0 |  |  | -0.00374 |  |  | 0 |  | 1 | NEWENERGY | W1-112
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00374 |  |  | 0 |  | 1 | CAPACITY | W1-112
933322 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | -0.00374 |  |  | 0 |  | 1 | MTX | AC2-144
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.00375 |  |  | 0 |  | 1 | NEWENERGY | V4-001
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.61 |  |  | -0.00375 |  |  | 0 |  | 1 | CAPACITY | V4-001
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00382 |  |  | 0 |  | 1 | NEWENERGY | W4-064
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00382 |  |  | 0 |  | 1 | CAPACITY | W4-064
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | -0.00384 |  |  | 0.05 |  | 1 | MTX | AA2-061
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00383 |  |  | 0 |  | 1 | NEWENERGY | X1-012
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | -0.00384 |  |  | 0.05 |  | 1 | MTX | AA2-060
206742 | 28SUX_V3-011 | 34.5 | 228 | 64 | 0 | 2 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | CAPACITY
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 2.97 |  |  | -0.00383 |  |  | 0 |  | 1 | CAPACITY | X1-012
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY | W3-106
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0 |  |  | -0.00384 |  |  | 0 |  | 1 | NEWENERGY | W3-110
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 2.99 |  |  | -0.00385 |  |  | 0 |  | 1 | CAPACITY | Y1-020
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 2.29 |  |  | -0.00384 |  |  | 0 |  | 1 | CAPACITY | W3-110
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0 |  |  | -0.00385 |  |  | 0 |  | 1 | NEWENERGY | AC2-175
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0 |  |  | -0.00385 |  |  | 0 |  | 1 | NEWENERGY | AE1-081
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.77 |  |  | -0.00385 |  |  | 0 |  | 1 | CAPACITY | AE1-081
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00386 |  |  | 0 |  | 1 | NEWENERGY | W4-060
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.00386 |  |  | 0 |  | 1 | CAPACITY | W4-060
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.00388 |  |  | 0 |  | 1 | NEWENERGY | W2-016
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.00388 |  |  | 0 |  | 1 | CAPACITY | W2-016
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 66.1 | 98 | 78.68 |  |  | -0.00391 |  |  | 0.08446 |  | 1 | CAPACITY
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 87.02 |  |  | -0.00391 |  |  | 0.08446 |  | 1 | CAPACITY
206327 | 28S RIV G1 | 13.8 | 228 | 57 | 86.9 | 99.9 | 87.02 |  |  | -0.00391 |  |  | 0.08446 |  | 1 | CAPACITY
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 43.63 |  |  | -0.00391 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 46.17 |  |  | -0.00391 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 199.11 |  |  | -0.00393 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.00392 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 141.3 |  |  | -0.00392 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.00393 |  |  | 0.04435 |  | 1 | CAPACITY | RED OAK
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.00394 |  |  | 0.08446 |  | 1 | CAPACITY
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.00394 |  |  | 0.08446 |  | 1 | CAPACITY
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  |  |  | -0.004
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 245.67 |  |  | -0.00396 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.00396 |  |  | 0.04435 |  | 1 | CAPACITY | RARITAN RIVER
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.00396 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
207435 | AD1-113 CT2 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.00396 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207441 | AD1-113 ST | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.00396 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207434 | AD1-113 CT1 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.00396 |  |  | 0.04435 |  | 1 | NEW | RARITAN RIVER
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 97.1 | 111.6 | 97.21 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 90.9 | 104.5 | 91.03 |  |  | -0.00396 |  |  | 0.08446 |  | 1 | CAPACITY
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00395 |  |  | 0 |  | 1 | NEWENERGY | X1-095
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00395 |  |  | 0 |  | 1 | CAPACITY | X1-095
933332 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | -0.00396 |  |  | 0 |  | 1 | MTX | AC2-145
901032 | W1-024E OP1 | 34.5 | 228 | 0 | 0 | 0 | 0 |  |  | -0.00403 |  |  | 0 |  | 1 | NEW
937512 | AD2-210 E | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | -0.00403 |  |  | 0 |  | 1 | MTX | AD2-210
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0 |  |  | -0.00403 |  |  | 0 |  | 1 | NEWENERGY | W2-080
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00403 |  |  | 0 |  | 1 | CAPACITY | W1-024
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00403 |  |  | 0 |  | 1 | CAPACITY | W2-080
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00404 |  |  | 0 |  | 1 | NEWENERGY | W2-082
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00404 |  |  | 0 |  | 1 | CAPACITY | W2-082
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00406 |  |  | 0 |  | 1 | NEWENERGY | W1-032
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00406 |  |  | 0 |  | 1 | CAPACITY | W1-032
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0 |  |  | -0.0041 |  |  | 0 |  | 1 | NEWENERGY | AC1-207
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0 |  |  | -0.0041 |  |  | 0 |  | 1 | NEWENERGY | X2-075
207420 | AC1-207 C | 34.5 | 228 | 75 | 0 | 4.9 | 3.93 |  |  | -0.0041 |  |  | 0 |  | 1 | CAPACITY | AC1-207
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 1.83 |  |  | -0.0041 |  |  | 0 |  | 1 | CAPACITY | X2-075
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00412 |  |  | 0 |  | 1 | NEWENERGY | W3-029
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0 |  |  | -0.00412 |  |  | 0 |  | 1 | NEWENERGY | W3-003
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0 |  |  | -0.00412 |  |  | 0 |  | 1 | NEW | AE1-156
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0 |  |  | -0.00412 |  |  | 0 |  | 1 | NEWENERGY | AE1-156
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.00412 |  |  | 0 |  | 1 | NEWENERGY | W1-132
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00412 |  |  | 0 |  | 1 | NEWENERGY | W2-061
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00412 |  |  | 0 |  | 1 | NEWENERGY | V4-070
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00412 |  |  | 0 |  | 1 | NEWENERGY | V4-069
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.00412 |  |  | 0 |  | 1 | CAPACITY | W3-029
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00412 |  |  | 0 |  | 1 | CAPACITY | V4-069
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00412 |  |  | 0 |  | 1 | CAPACITY | V4-070
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00412 |  |  | 0 |  | 1 | CAPACITY | W2-061
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0 |  |  | -0.00414 |  |  | 0 |  | 1 | NEWENERGY | V3-070
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0 |  |  | -0.00413 |  |  | 0 |  | 1 | NEWENERGY | AB1-021
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.00414 |  |  | 0 |  | 1 | CAPACITY | V3-070
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00413 |  |  | 0 |  | 1 | CAPACITY | AB1-021
207419 | AB2-139 E | 34.5 | 228 | 76 | 0 | 0.21 | 0 |  |  | -0.00415 |  |  | 0 |  | 1 | ENERGY | AB2-139
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0 |  |  | -0.00416 |  |  | 0 |  | 1 | NEWENERGY | W2-050
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00417 |  |  | 0 |  | 1 | NEWENERGY | V2-025
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 207.94 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 202.48 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.00418 |  |  | 0.04435 |  | 1 | CAPACITY | DELANCY STREET
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 143.63 |  |  | -0.00418 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN2
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 143.63 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 76.11 |  |  | -0.00417 |  |  | 0.08446 |  | 1 | CAPACITY
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.00417 |  |  | 0.08446 |  | 1 | CAPACITY
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.00417 |  |  | 0.08446 |  | 1 | CAPACITY
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.00417 |  |  | 0.08446 |  | 1 | CAPACITY
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.00417 |  |  | 0.08446 |  | 1 | CAPACITY
218092 | PRIMEENG_G | 26.4 | 231 | 29 | 10 | 70.3 | 56.44 |  |  | -0.00418 |  |  | 0.10478 |  | 1 | CAPACITY
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 70.56 |  |  | -0.00418 |  |  | 0.08446 |  | 1 | CAPACITY
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.00418 |  |  | 0.04435 |  | 1 | CAPACITY | NEWARK BAY
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 27.46 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217831 | PB_NUTCLIF | 26 | 231 | 2 | 0 | 10.7 | 8.59 |  |  | -0.00417 |  |  | 0 |  | 1 | CAPACITY
217850 | MONTCLAIR_U | 26 | 231 | 2 | 0 | 10.6 | 8.51 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0 |  |  | -0.00418 |  |  | 0 |  | 1 | NEWENERGY | W4-059
934302 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.00418 |  |  | 0 |  | 1 | NEWENERGY | AD1-054
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.74 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0 |  |  | -0.00418 |  |  | 0 |  | 1 | NEWENERGY | X1-072
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0 |  |  | -0.00418 |  |  | 0 |  | 1 | NEWENERGY | W2-036
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.85 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0 |  |  | -0.00418 |  |  | 0 |  | 1 | NEWENERGY | V3-065
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0 |  |  | -0.00417 |  |  | 0 |  | 1 | NEWENERGY | V3-066
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY | X1-072
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY | W2-036
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.18 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY | W4-059
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.17 |  |  | -0.00418 |  |  | 0 |  | 1 | CAPACITY | V3-065
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.00417 |  |  | 0 |  | 1 | CAPACITY | V3-066
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 169.24 |  |  | -0.0042 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.0042 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.0042 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.0042 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 |  |  | -0.0042 |  |  | 0 |  | 1 | CAPACITY | BERGEN1
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.00422 |  |  | 0.10478 |  | 1 | CAPACITY
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | -0.00422 |  |  | 0.10478 |  | 1 | CAPACITY
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0 |  |  | -0.00421 |  |  | 0 |  | 1 | NEWENERGY | X2-087
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.00421 |  |  | 0 |  | 1 | CAPACITY | X2-087
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0 |  |  | -0.00423 |  |  | 0 |  | 1 | NEWENERGY | W2-078
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.00423 |  |  | 0 |  | 1 | NEWENERGY | W1-113
217825 | UMD_NJ | 26 | 231 | 2 | 0 | 10.5 | 8.43 |  |  | -0.00422 |  |  | 0 |  | 1 | CAPACITY
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00423 |  |  | 0 |  | 1 | CAPACITY | W2-078
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 2.25 |  |  | -0.00423 |  |  | 0 |  | 1 | CAPACITY | W1-113
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0 |  |  | -0.00422 |  |  | 0 |  | 1 | NEWENERGY | V3-067
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0 |  |  | -0.00422 |  |  | 0 |  | 1 | NEWENERGY | V3-068
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.23 |  |  | -0.00422 |  |  | 0 |  | 1 | CAPACITY | V3-067
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.00422 |  |  | 0 |  | 1 | CAPACITY | V3-068
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0 |  |  | -0.00425 |  |  | 0 |  | 1 | NEWENERGY | W1-101
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.43 |  |  | -0.00425 |  |  | 0 |  | 1 | CAPACITY | W1-101
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 5.3 |  |  | -0.00427 |  |  | 0 |  | 1 | CAPACITY
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 309 | 248.08 |  |  | -0.0043 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 180 | 144.51 |  |  | -0.0043 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -0.0043 |  |  | 0.08446 |  | 1 | CAPACITY
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | -0.0043 |  |  | 0.08446 |  | 1 | CAPACITY
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 30.03 |  |  | -0.0043 |  |  | 0.10478 |  | 1 | CAPACITY
214030 | WAYNEJCT | 13.8 | 230 | 2 | 0 | 8.8 | 7.07 |  |  | -0.0043 |  |  | 0 |  | 1 | CAPACITY
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  |  |  | -0.0043
218344 | TOSCO_G6 | 18 | 231 | 2 | 90 | 180 | 144.51 |  |  | -0.00434 |  |  | 0.04435 |  | 1 | CAPACITY | TOSCO
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 309 | 248.08 |  |  | -0.00435 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.00435 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC2
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.00435 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | -0.00435 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | -0.00435 |  |  | 0.08446 |  | 1 | CAPACITY
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | -0.00435 |  |  | 0.08446 |  | 1 | CAPACITY
900004 | SMITHBRG E | 500 | 228 | 74 | 0 | 820.4 | 0 |  |  | -0.00446 |  |  | 0 |  | 1 | NEWENERGY | OSW_SMITHB
219001 | SEWAREN7GT | 25 | 231 | 58 | 101.5 | 324.6 | 260.61 |  |  | -0.00446 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-089
219002 | SEWAREN7ST | 18 | 231 | 58 | 96.3 | 216.4 | 173.74 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY | Z2-089
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | -0.00446 |  |  | 0.04435 |  | 1 | ENERGY | Z2-089
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | -0.00446 |  |  | 0 |  | 1 | ENERGY | Z2-089
200017 | SMITHBRG C | 500 | 228 | 74 | 0 | 327.6 | 327.6 |  |  | -0.00446 |  |  | 0 |  | 1 | CAPACITY | OSW_SMITHB
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 538.72 |  |  | -0.00449 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-116
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | AB1-139
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | AE1-041
930901 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 2.01 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | AB1-139
938281 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | AE1-041
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0 |  |  | -0.00449 |  |  | 0 |  | 1 | NEWENERGY | W2-052
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | -0.00449 |  |  | 0 |  | 1 | CAPACITY | W2-052
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00451 |  |  | 0 |  | 1 | NEWENERGY | X4-015
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0 |  |  | -0.00452 |  |  | 0 |  | 1 | NEWENERGY | X2-089
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00451 |  |  | 0 |  | 1 | CAPACITY | X4-015
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.61 |  |  | -0.00452 |  |  | 0 |  | 1 | CAPACITY | X2-089
900003 | DEANS E | 500 | 231 | 74 | 0 | 1779.4 | 0 |  |  | -0.00455 |  |  | 0 |  | 1 | NEWENERGY | OSW_DEANS
200006 | DEANS C | 500 | 231 | 74 | 0 | 762.6 | 762.6 |  |  | -0.00455 |  |  | 0 |  | 1 | CAPACITY | OSW_DEANS
218455 | CINNBAY_CGEN | 26.4 | 231 | 75 | 0 | 9 | 0 |  |  | -0.00472 |  |  | 0 |  | 1 | NEWENERGY
924132 | NEWROADSO E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.00472 |  |  | 0 |  | 1 | NEWENERGY | AB2-057
217198 | EDGEBORO_1E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.00472 |  |  | 0 |  | 1 | NEWENERGY | V3-058
217199 | EDGEBORO_2E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | -0.00472 |  |  | 0 |  | 1 | NEWENERGY | V3-059
924131 | NEWROADSO C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00472 |  |  | 0 |  | 1 | CAPACITY | AB2-057
218781 | BRIS_MYERS | 26 | 231 | 2 | 0 | 3 | 2.41 |  |  | -0.00472 |  |  | 0 |  | 1 | CAPACITY
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.00485 |  |  | 0 |  | 1 | NEWENERGY | W4-025
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00485 |  |  | 0 |  | 1 | NEWENERGY | W1-129
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.00485 |  |  | 0 |  | 1 | CAPACITY | W4-025
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00485 |  |  | 0 |  | 1 | CAPACITY | W1-129
219650 | TRENT_COLLEG | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.00489 |  |  | 0 |  | 1 | CAPACITY
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0 |  |  | -0.00489 |  |  | 0 |  | 1 | NEWENERGY | W4-058
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.22 |  |  | -0.00489 |  |  | 0 |  | 1 | CAPACITY | W4-058
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0 |  |  | -0.00491 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0 |  |  | -0.00491 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
932032 | AC2-009 E | 13.2 | 231 | 75 | -0.5 | 0.49 | 0 |  |  | -0.00491 |  |  | 0 |  | 1 | NEWENERGY | AC2-009
932031 | AC2-009 C | 13.2 | 231 | 75 | -0.1 | 0.1 | 0 |  |  | -0.00491 |  |  | 0 |  | 1 | NEW | AC2-009
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00491 |  |  | 0 |  | 1 | CAPACITY | AA2-058
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.00506 |  |  | 0 |  | 1 | NEWENERGY | V3-024
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0 |  |  | -0.00506 |  |  | 0 |  | 1 | NEWENERGY | V2-009 2
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0 |  |  | -0.00507 |  |  | 0 |  | 1 | NEWENERGY | W3-124
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0 |  |  | -0.00507 |  |  | 0 |  | 1 | NEWENERGY | V2-009 1
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0 |  |  | -0.00506 |  |  | 0 |  | 1 | NEWENERGY | X2-088
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00506 |  |  | 0 |  | 1 | CAPACITY | V3-024
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 1.52 |  |  | -0.00506 |  |  | 0 |  | 1 | CAPACITY | V2-009 2
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.87 |  |  | -0.00507 |  |  | 0 |  | 1 | CAPACITY | W3-124
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00507 |  |  | 0 |  | 1 | CAPACITY | V2-009 1
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.72 |  |  | -0.00506 |  |  | 0 |  | 1 | CAPACITY | X2-088
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.00521 |  |  | 0.08446 |  | 1 | CAPACITY
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.00521 |  |  | 0.08446 |  | 1 | CAPACITY
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0 |  |  | -0.0052 |  |  | 0 |  | 1 | NEWENERGY | V2-009 3
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0 |  |  | -0.0052 |  |  | 0 |  | 1 | NEWENERGY | V2-009 4
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 1.92 |  |  | -0.0052 |  |  | 0 |  | 1 | CAPACITY | V2-009 3
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 1.15 |  |  | -0.0052 |  |  | 0 |  | 1 | CAPACITY | V2-009 4
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 64.31 |  |  | -0.00529 |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 52.35 |  |  | -0.00529 |  |  | 0.04435 |  | 1 | CAPACITY | CAMDEN COGEN TECH
925391 | AC1-010 C | 26.4 | 231 | 75 | 0 | 6 | 0 |  |  | -0.00529 |  |  | 0 |  | 1 | NEW | AC1-010
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 19.27 |  |  | -0.00529 |  |  | 0.10478 |  | 1 | CAPACITY
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -0.00529 |  |  | 0 |  | 1 | NEWENERGY | AC1-010
219765 | PARADISE E | 26.4 | 231 | 75 | 0 | 3.2 | 0 |  |  | -0.00529 |  |  | 0 |  | 1 | NEWENERGY | U4-036
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.3 | 9.07 |  |  | -0.00529 |  |  | 0.10478 |  | 1 | CAPACITY
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | -0.00529 |  |  | 0 |  | 1 | MTX | X2-013
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00529 |  |  | 0 |  | 1 | CAPACITY | U4-036
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00532 |  |  | 0 |  | 1 | NEWENERGY | X1-085
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00532 |  |  | 0 |  | 1 | CAPACITY | X1-085
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.0055 |  |  | 0.05 |  | 1 | MTX
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0 |  |  | -0.00552 |  |  | 0 |  | 1 | NEWENERGY | W2-019
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 1.85 |  |  | -0.00552 |  |  | 0 |  | 1 | CAPACITY | W2-019
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 35.24 |  |  | -0.00562 |  |  | 0.10478 |  | 1 | CAPACITY
218780 | PRINCENTON_U | 26 | 231 | 2 | 0 | 31.56 | 25.34 |  |  | -0.00576 |  |  | 0 |  | 1 | CAPACITY
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0 |  |  | -0.00576 |  |  | 0 |  | 1 | NEWENERGY | Z1-096
219622 | TRENT_BIOGAS | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | -0.00576 |  |  | 0 |  | 1 | CAPACITY
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 2.39 |  |  | -0.00576 |  |  | 0 |  | 1 | CAPACITY | Z1-096
219913 | PENNSAU2 E | 26.4 | 231 | 75 | 0 | 8.2 | 0 |  |  | -0.00578 |  |  | 0 |  | 1 | NEWENERGY | AD2-042
219915 | CINNAMSOL E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -0.00578 |  |  | 0 |  | 1 | NEWENERGY | AD2-027
219912 | PENNSAU2 C | 26.4 | 231 | 75 | 0 | 5 | 0 |  |  | -0.00578 |  |  | 0 |  | 1 | NEW | AD2-042
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.63 | 3.72 |  |  | -0.00578 |  |  | 0 |  | 1 | CAPACITY
219914 | CINNAMSOL C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00578 |  |  | 0 |  | 1 | CAPACITY | AD2-027
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.4 |  |  | -0.00578 |  |  | 0 |  | 1 | CAPACITY
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0 |  |  | -0.00644 |  |  | 0 |  | 1 | NEWENERGY | W1-121 Z
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00644 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00644 |  |  | 0 |  | 1 | CAPACITY | W1-121 Z
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.46 |  |  | -0.00644 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.00654 |  |  | 0 |  | 1 | NEWENERGY | AC1-030
925561 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00654 |  |  | 0 |  | 1 | CAPACITY | AC1-030
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0 |  |  | -0.00654 |  |  | 0 |  | 1 | NEWENERGY | X1-071
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.28 |  |  | -0.00654 |  |  | 0 |  | 1 | CAPACITY | X1-071
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.00661 |  |  | 0.08446 |  | 1 | CAPACITY
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00661 |  |  | 0 |  | 1 | CAPACITY | T20
219647 | COOPERSOLA E | 13.2 | 231 | 75 | 0 | 0.4 | 0 |  |  | -0.00687 |  |  | 0 |  | 1 | NEWENERGY | AB1-063
219123 | BCRR_COGEN | 13.8 | 231 | 64 | 0 | 6 | 0 |  |  | -0.00717 |  |  | 0.12623 |  | 1 | CAPACITY
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 260.3 | 208.98 |  |  | -0.00722 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 205.69 |  |  | -0.00722 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | -0.00722 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill B
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | -0.00722 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | -0.00722 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | -0.00722 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill A
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0 |  |  | -0.00737 |  |  | 0 |  | 1 | NEWENERGY | AC1-017
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0 |  |  | -0.00737 |  |  | 0 |  | 1 | NEWENERGY | X1-070
925451 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 1.12 |  |  | -0.00737 |  |  | 0 |  | 1 | CAPACITY | AC1-017
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.96 |  |  | -0.00737 |  |  | 0 |  | 1 | CAPACITY | X1-070
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00753 |  |  | 0.08446 |  | 1 | CAPACITY
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00753 |  |  | 0.08446 |  | 1 | CAPACITY
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00753 |  |  | 0.08446 |  | 1 | CAPACITY
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00753 |  |  | 0.08446 |  | 1 | CAPACITY
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00753 |  |  | 0.08446 |  | 1 | CAPACITY
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00753 |  |  | 0.08446 |  | 1 | CAPACITY
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | -0.00753 |  |  | 0.08446 |  | 1 | CAPACITY
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 38.54 |  |  | -0.00753 |  |  | 0.08446 |  | 1 | CAPACITY
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | -0.00784 |  |  | 0 |  | 1 | MTX | Z1-082
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 0 |  |  | -0.00797 |  |  | 0 |  | 1 | NEWENERGY | W3-080
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.00797 |  |  | 0.08446 |  | 1 | CAPACITY
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.00797 |  |  | 0.08446 |  | 1 | CAPACITY
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.00797 |  |  | 0.08446 |  | 1 | CAPACITY
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | -0.00797 |  |  | 0.08446 |  | 1 | CAPACITY
925442 | AC1-016 E | 26.4 | 231 | 75 | 0 | 5.45 | 0 |  |  | -0.00797 |  |  | 0 |  | 1 | NEWENERGY | AC1-016
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | -0.00797 |  |  | 0 |  | 1 | NEWENERGY | W4-103
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | -0.00797 |  |  | 0 |  | 1 | NEWENERGY | W2-102
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -0.00797 |  |  | 0 |  | 1 | NEWENERGY | Y3-026
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00797 |  |  | 0 |  | 1 | CAPACITY | Y3-026
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 2.97 |  |  | -0.00797 |  |  | 0 |  | 1 | CAPACITY | W3-080
925441 | AC1-016 C | 26.4 | 231 | 75 | 0 | 3.34 | 2.68 |  |  | -0.00797 |  |  | 0 |  | 1 | CAPACITY | AC1-016
219685 | NATIONAL_GYP | 26 | 231 | 2 | 0 | 2.8 | 2.25 |  |  | -0.00797 |  |  | 0 |  | 1 | CAPACITY
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.00797 |  |  | 0 |  | 1 | CAPACITY | W4-103
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -0.00797 |  |  | 0 |  | 1 | CAPACITY | W2-102
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0 |  |  | -0.00866 |  |  | 0 |  | 1 | NEWENERGY | X3-075
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0 |  |  | -0.0092 |  |  | 0 |  | 1 | NEWENERGY | Y3-087
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 1.84 |  |  | -0.0092 |  |  | 0 |  | 1 | CAPACITY | Y3-087
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0 |  |  | -0.01447 |  |  | 0 |  | 1 | NEWENERGY | Y1-075
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.01447 |  |  | 0 |  | 1 | CAPACITY | Y1-075
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0 |  |  | -0.01457 |  |  | 0 |  | 1 | NEWENERGY | V4-005
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.88 |  |  | -0.01457 |  |  | 0 |  | 1 | CAPACITY | V4-005
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0 |  |  | -0.01559 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 S
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | -0.01559 |  |  | 0 |  | 1 | CAPACITY | AB1-025 S
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0 |  |  | -0.01601 |  |  | 0 |  | 1 | NEWENERGY | W2-071
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.85 |  |  | -0.01601 |  |  | 0 |  | 1 | CAPACITY | W2-071
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0 |  |  | -0.01624 |  |  | 0 |  | 1 | NEWENERGY | W2-056
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 3.36 |  |  | -0.01624 |  |  | 0 |  | 1 | CAPACITY | W2-056
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0 |  |  | -0.01625 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 N
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | -0.01625 |  |  | 0 |  | 1 | CAPACITY | AB1-025 N

## Bergen 138 kV Line
****** PJM Generator Deliverability Detailed Report ****** POWER-GEM [TARA Ver 2001.1a PJMGD RC3 64-bit - Tue Aug 17 14:35:55 2021]
FG Index | 12 | Monitored Facility:217163 BERGEN_4 138 217157 BERGEN_R 138 1 / Contingency:PS_P2-3_BERG_1-2[Breaker]
Rating | Final DC %LD | Final AC %LD | DC¦AC | Base FG Flow | 50/50 MW | Adder MW | LTF Impact | Adder Impact | DC Final Flow | AC Final Flow | Shift Factor | Import Cap | Transfer Cap | Adder Cap | Missing Outlier Cap | Outlier Dfax Cutoff | Total Dispatch | 80¦50 Dispatch | Adder Dispatch | External Dispatch
350 | 101.86 | 100.14 | AC | 295.09 | 35.75 | 0.06 | 27.02 | -1.41 | 356.5 | 350.5 | 0.001248 | 0 | 12823.7 | 0 | 12720.4 | 0.05 | 104.06 | 103.32 | 0.74 | 0
Bus# | Bus Name | Volt | Area | Gen Class | PMin | PMax | PGen | PNew | Flag | Dfax | Impact | Adder Impact | EEFORD | Cum Avai | Com Prob | Unit Type | Group ID | Study Bus? | MFO Limited?
217118 | BERGEN 1 ST | 18 | 231 | 58 | 47 | 210.8 | 169.24 | 210.8 | FiftyFifty | 0.34598 | 14.3777 |  | 0.04435 | 0.9556 | 1 | CAPACITY | BERGEN1
217916 | BERGEN_12 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 | 119.8 | FiftyFifty | 0.34598 | 5.3423 |  | 0 | 0.9556 | 1 | CAPACITY | BERGEN1
217915 | BERGEN_11 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 | 119.8 | FiftyFifty | 0.34598 | 5.3423 |  | 0 | 0.9556 | 1 | CAPACITY | BERGEN1
217918 | BERGEN_14 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 | 119.8 | FiftyFifty | 0.34598 | 5.3423 |  | 0 | 0.9556 | 1 | CAPACITY | BERGEN1
217917 | BERGEN_13 | 13.8 | 231 | 58 | 104.2 | 119.8 | 104.36 | 119.8 | FiftyFifty | 0.34598 | 5.3423 |  | 0 | 0.9556 | 1 | CAPACITY | BERGEN1
217082 | WEATEXAS E | 13.2 | 231 | 75 | 0 | 0.87 | 0 | 0.74 | Adder/OL | 0.07609 | 0.0561 | 0.0009 | 0 |  | 1 | NEWENERGY | W1-101
O66 | PJM->LTFIMP_O-066 |  |  | LTF |  | 673 |  | 673 | LTF/CMTX NF | 0.02056 | 13.835 | -0.8402
VTF | LTFEXP_VFT->PJM |  |  | LTF |  | 645 |  | 645 | LTF/CMTX | 0.01683 | 10.8555 | 0.8052
NY | PJM->LTFIMP_NY |  |  | LTF |  | 55.3 |  | 55.3 | CLTF | 0.01293 | 0.715 | -0.069
G-007 | PJM->LTFIMP_G-007 |  |  | LTF |  | 105 |  | 105 | LTF/CMTX NF | 0.00225 | 0.2367 | -0.1311
PRAIRIE | PJM->LTFIMP_PRAIRIE |  |  | LTF |  | 258.3 |  | 258.3 | CLTF | 0.00146 | 0.378 | -0.3225
BlueGrass | PJM->LTFIMP_BlueG |  |  | LTF |  | 173.6 |  | 173.6 | CLTF | 0.00147 | 0.2546 | -0.2167
TRIMBLE | PJM->LTFIMP_TRIMBLE |  |  | LTF |  | 55.7 |  | 55.7 | CLTF | 0.00147 | 0.0816 | -0.0695
Gibson | PJM->LTFIMP_GIBSON |  |  | LTF |  | 54.6 |  | 54.6 | CLTF | 0.00147 | 0.0801 | -0.0682
COTTONWOOD | PJM->LTFIMP_COTTONWOOD |  |  | LTF |  | 210 |  | 210 | CLTF | 0.00146 | 0.306 | -0.2622
CHEOAH | PJM->LTFIMP_CHEOAH |  |  | LTF |  | 50 |  | 50 | CLTF | 0.00145 | 0.0727 | -0.0625
CALDErWOOD | PJM->LTFIMP_CALDERWOOD |  |  | LTF |  | 49.7 |  | 49.7 | CLTF | 0.00145 | 0.0722 | -0.062
CATAWBA | PJM->LTFIMP_CATAWBA |  |  | LTF |  | 35 |  | 35 | CLTF | 0.00144 | 0.0504 | -0.0437
HAMLET | PJM->LTFIMP_HAMLET |  |  | LTF |  | 57.8 |  | 57.8 | CLTF | 0.00144 | 0.0829 | -0.0721
217081 | WEATEXAS C | 13.2 | 231 | 75 | 0 | 0.53 | 0.43 |  |  | 0.07609 |  |  | 0 |  | 1 | CAPACITY | W1-101
218435 | LINDEN_1101 | 18 | 231 | 58 | 90 | 309 | 248.08 |  |  | 0.04971 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
218436 | LINDEN_1001 | 18 | 231 | 58 | 60 | 180 | 144.51 |  |  | 0.04971 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC1
219035 | LINDEN_G8 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | 0.04971 |  |  | 0.08446 |  | 1 | CAPACITY
219036 | LINDEN_G7 | 13.8 | 231 | 57 | 73.2 | 84.1 | 73.26 |  |  | 0.04971 |  |  | 0.08446 |  | 1 | CAPACITY
218516 | UCRR | 26.4 | 231 | 2 | 0 | 37.4 | 30.03 |  |  | 0.04971 |  |  | 0.10478 |  | 1 | CAPACITY
217214 | CENTRL HS E | 13.2 | 231 | 75 | 0 | 0.51 | 0 |  |  | 0.03006 |  |  | 0 |  | 1 | NEWENERGY | V3-067
217210 | CAMDEN ST E | 13.2 | 231 | 75 | 0 | 0.26 | 0 |  |  | 0.03006 |  |  | 0 |  | 1 | NEWENERGY | V3-068
217209 | CENTRL HS C | 13.8 | 231 | 75 | 0 | 0.29 | 0.23 |  |  | 0.03006 |  |  | 0 |  | 1 | CAPACITY | V3-067
217211 | CAMDEN ST C | 13.8 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | 0.03006 |  |  | 0 |  | 1 | CAPACITY | V3-068
217065 | ECRRF_1 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | 0.02418 |  |  | 0.10478 |  | 1 | CAPACITY
217323 | ECRRF_2 | 138 | 231 | 1 | 0 | 30.15 | 24.21 |  |  | 0.02409 |  |  | 0.10478 |  | 1 | CAPACITY
218426 | LINDEN_2ST | 18 | 231 | 58 | 60 | 309 | 248.08 |  |  | 0.02082 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218425 | LINDEN_1201 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | 0.02082 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC1
218424 | LINDEN_G22 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | 0.02082 |  |  | 0 |  | 1 | CAPACITY | LINDEN CC2
218423 | LINDEN_G21 | 18 | 231 | 58 | 90 | 180 | 144.51 |  |  | 0.02082 |  |  | 0.04435 |  | 1 | CAPACITY | LINDEN CC2
218419 | LINDEN_G6 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | 0.02082 |  |  | 0.08446 |  | 1 | CAPACITY
218418 | LINDEN_G5 | 13.8 | 231 | 57 | 74.8 | 86 | 74.92 |  |  | 0.02082 |  |  | 0.08446 |  | 1 | CAPACITY
218344 | TOSCO_G6 | 18 | 231 | 2 | 90 | 180 | 144.51 |  |  | 0.01797 |  |  | 0.04435 |  | 1 | CAPACITY | TOSCO
219001 | SEWAREN7GT | 25 | 231 | 58 | 101.5 | 324.6 | 260.61 |  |  | 0.01005 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-089
219002 | SEWAREN7ST | 18 | 231 | 58 | 96.3 | 216.4 | 173.74 |  |  | 0.01005 |  |  | 0 |  | 1 | CAPACITY | Z2-089
917522 | SEWARENG7E2 | 18 | 231 | 58 | 0 | 13 | 0 |  |  | 0.01005 |  |  | 0 |  | 1 | ENERGY | Z2-089
917521 | SEWARENG7E1 | 25 | 231 | 58 | 0 | 13 | 0 |  |  | 0.01005 |  |  | 0.04435 |  | 1 | ENERGY | Z2-089
219901 | Z1-116 | 22.5 | 231 | 57 | 0 | 671 | 538.72 |  |  | 0.00725 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-116
930902 | AB1-139 E | 26.4 | 231 | 75 | 0 | 4.1 | 0 |  |  | 0.00725 |  |  | 0 |  | 1 | NEWENERGY | AB1-139
938282 | AE1-041 E | 26.4 | 231 | 75 | 0 | 0.9 | 0 |  |  | 0.00725 |  |  | 0 |  | 1 | NEWENERGY | AE1-041
930901 | AB1-139 C | 26.4 | 231 | 75 | 0 | 2.5 | 2.01 |  |  | 0.00725 |  |  | 0 |  | 1 | CAPACITY | AB1-139
938281 | AE1-041 C | 26.4 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | 0.00725 |  |  | 0 |  | 1 | CAPACITY | AE1-041
218429 | ETC SOLAR E | 13.2 | 231 | 75 | 0 | 0.37 | 0 |  |  | 0.00717 |  |  | 0 |  | 1 | NEWENERGY | W2-052
218428 | ETC SOLAR C | 13.2 | 231 | 75 | 0 | 0.2 | 0.16 |  |  | 0.00717 |  |  | 0 |  | 1 | CAPACITY | W2-052
218439 | SUMMTASSOC E | 13 | 231 | 75 | 0 | 1.24 | 0 |  |  | 0.00638 |  |  | 0 |  | 1 | NEWENERGY | X2-089
218440 | SUMMTASSOC C | 13 | 231 | 75 | 0 | 0.76 | 0.61 |  |  | 0.00638 |  |  | 0 |  | 1 | CAPACITY | X2-089
218404 | KENILWRTH C | 26.4 | 231 | 29 | 0 | 6.6 | 5.3 |  |  | 0.00485 |  |  | 0 |  | 1 | CAPACITY
218455 | CINNBAY_CGEN | 26.4 | 231 | 75 | 0 | 9 | 0 |  |  | 0.00348 |  |  | 0 |  | 1 | NEWENERGY
924132 | NEWROADSO E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | 0.00348 |  |  | 0 |  | 1 | NEWENERGY | AB2-057
217199 | EDGEBORO_2E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | 0.00348 |  |  | 0 |  | 1 | NEWENERGY | V3-059
217198 | EDGEBORO_1E | 26.4 | 231 | 75 | 0 | 2 | 0 |  |  | 0.00348 |  |  | 0 |  | 1 | NEWENERGY | V3-058
924131 | NEWROADSO C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | 0.00348 |  |  | 0 |  | 1 | CAPACITY | AB2-057
218781 | BRIS_MYERS | 26 | 231 | 2 | 0 | 3 | 2.41 |  |  | 0.00348 |  |  | 0 |  | 1 | CAPACITY
217196 | RE CRAN E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | 0.00289 |  |  | 0 |  | 1 | NEWENERGY | V3-024
219881 | V2-009 E2 | 13 | 231 | 75 | 0 | 3.08 | 0 |  |  | 0.00289 |  |  | 0 |  | 1 | NEWENERGY | V2-009 2
218437 | BLK ROCK E | 13 | 231 | 75 | 0 | 1.4 | 0 |  |  | 0.00289 |  |  | 0 |  | 1 | NEWENERGY | X2-088
217197 | RE CRAN C | 13 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | 0.00289 |  |  | 0 |  | 1 | CAPACITY | V3-024
219882 | V2-009 C2 | 13 | 231 | 75 | 0 | 1.89 | 1.52 |  |  | 0.00289 |  |  | 0 |  | 1 | CAPACITY | V2-009 2
218438 | BLK ROCK C | 13 | 231 | 75 | 0 | 0.9 | 0.72 |  |  | 0.00289 |  |  | 0 |  | 1 | CAPACITY | X2-088
219613 | MATRIX E | 13.2 | 231 | 75 | 0 | 1.77 | 0 |  |  | 0.00288 |  |  | 0 |  | 1 | NEWENERGY | W3-124
219883 | V2-009 E1 | 13 | 231 | 75 | 0 | 1.54 | 0 |  |  | 0.00288 |  |  | 0 |  | 1 | NEWENERGY | V2-009 1
219612 | MATRIX C | 13.2 | 231 | 75 | 0 | 1.08 | 0.87 |  |  | 0.00288 |  |  | 0 |  | 1 | CAPACITY | W3-124
219884 | V2-009 C1 | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | 0.00288 |  |  | 0 |  | 1 | CAPACITY | V2-009 1
218359 | V2-009 E3 | 13 | 231 | 75 | 0 | 3.89 | 0 |  |  | 0.00258 |  |  | 0 |  | 1 | NEWENERGY | V2-009 3
219878 | V2-009 E4 | 13 | 231 | 75 | 0 | 2.34 | 0 |  |  | 0.00258 |  |  | 0 |  | 1 | NEWENERGY | V2-009 4
219880 | V2-009 C3 | 13 | 231 | 75 | 0 | 2.39 | 1.92 |  |  | 0.00258 |  |  | 0 |  | 1 | CAPACITY | V2-009 3
219879 | V2-009 C4 | 13 | 231 | 75 | 0 | 1.43 | 1.15 |  |  | 0.00258 |  |  | 0 |  | 1 | CAPACITY | V2-009 4
218780 | PRINCENTON_U | 26 | 231 | 2 | 0 | 31.56 | 25.34 |  |  | 0.00168 |  |  | 0 |  | 1 | CAPACITY
219275 | PARKLANDSO E | 26.4 | 231 | 75 | 0 | 4.86 | 0 |  |  | 0.00168 |  |  | 0 |  | 1 | NEWENERGY | Z1-096
219622 | TRENT_BIOGAS | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | 0.00168 |  |  | 0 |  | 1 | CAPACITY
219276 | PARKLANDSO C | 26.4 | 231 | 75 | 0 | 2.98 | 2.39 |  |  | 0.00168 |  |  | 0 |  | 1 | CAPACITY | Z1-096
217188 | WHELABTR_G | 13.8 | 231 | 2 | 0 | 43.9 | 35.24 |  |  | 0.00151 |  |  | 0.10478 |  | 1 | CAPACITY
219117 | HARTZZ_E | 13.2 | 231 | 75 | 0 | 2.48 | 0 |  |  | 0.00128 |  |  | 0 |  | 1 | NEWENERGY | W1-121 Z
219114 | HARTZY_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | 0.00128 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
219116 | HARTZZ_C | 13.2 | 231 | 75 | 0 | 1.52 | 1.22 |  |  | 0.00128 |  |  | 0 |  | 1 | CAPACITY | W1-121 Z
219115 | HARTZY_E | 13.2 | 231 | 75 | 0 | 0.57 | 0.46 |  |  | 0.00128 |  |  | 0 |  | 1 | CAPACITY | W1-121 Y
900003 | DEANS E | 500 | 231 | 74 | 0 | 1779.4 | 0 |  |  | 0.00094 |  |  | 0 |  | 1 | NEWENERGY | OSW_DEANS
200006 | DEANS C | 500 | 231 | 74 | 0 | 762.6 | 762.6 |  |  | 0.00094 |  |  | 0 |  | 1 | CAPACITY | OSW_DEANS
219682 | HOPEWELLV E2 | 13.2 | 231 | 75 | 0 | 0.8 | 0 |  |  | 0.00091 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
219681 | HOPEWELLV E1 | 13.2 | 231 | 75 | 0 | 0.6 | 0 |  |  | 0.00091 |  |  | 0 |  | 1 | NEWENERGY | AA2-058
932032 | AC2-009 E | 13.2 | 231 | 75 | -0.5 | 0.49 | 0 |  |  | 0.00091 |  |  | 0 |  | 1 | NEWENERGY | AC2-009
932031 | AC2-009 C | 13.2 | 231 | 75 | -0.1 | 0.1 | 0 |  |  | 0.00091 |  |  | 0 |  | 1 | NEW | AC2-009
219680 | HOPEWELLV C1 | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | 0.00091 |  |  | 0 |  | 1 | CAPACITY | AA2-058
219123 | BCRR_COGEN | 13.8 | 231 | 64 | 0 | 6 | 0 |  |  | 0.00085 |  |  | 0.12623 |  | 1 | CAPACITY
900004 | SMITHBRG E | 500 | 228 | 74 | 0 | 820.4 | 0 |  |  | 0.00077 |  |  | 0 |  | 1 | NEWENERGY | OSW_SMITHB
200017 | SMITHBRG C | 500 | 228 | 74 | 0 | 327.6 | 327.6 |  |  | 0.00077 |  |  | 0 |  | 1 | CAPACITY | OSW_SMITHB
219650 | TRENT_COLLEG | 26 | 231 | 2 | 0 | 3.75 | 3.01 |  |  | 0.0007 |  |  | 0 |  | 1 | CAPACITY
219621 | RIDERU E | 13.2 | 231 | 75 | 0 | 0.44 | 0 |  |  | 0.0007 |  |  | 0 |  | 1 | NEWENERGY | W4-058
219620 | RIDERU C | 13.2 | 231 | 75 | 0 | 0.27 | 0.22 |  |  | 0.0007 |  |  | 0 |  | 1 | CAPACITY | W4-058
213611 | FALLS1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | 0.0005 |  |  | 0.08446 |  | 1 | CAPACITY
214067 | T20SOLAR | 0.48 | 230 | 75 | 0 | 1.3 | 1.04 |  |  | 0.0005 |  |  | 0 |  | 1 | CAPACITY | T20
219611 | FLORENCE E | 26.4 | 231 | 75 | 0 | 12.4 | 0 |  |  | 0.00038 |  |  | 0 |  | 1 | NEWENERGY | W3-080
219223 | BURLING_CT3 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.00038 |  |  | 0.08446 |  | 1 | CAPACITY
219222 | BURLING_CT2 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.00038 |  |  | 0.08446 |  | 1 | CAPACITY
219224 | BURLING_CT4 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.00038 |  |  | 0.08446 |  | 1 | CAPACITY
219221 | BURLING_CT1 | 13.8 | 231 | 56 | 30 | 42.75 | 34.32 |  |  | 0.00038 |  |  | 0.08446 |  | 1 | CAPACITY
925442 | AC1-016 E | 26.4 | 231 | 75 | 0 | 5.45 | 0 |  |  | 0.00038 |  |  | 0 |  | 1 | NEWENERGY | AC1-016
219608 | WPEMNERT E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | 0.00038 |  |  | 0 |  | 1 | NEWENERGY | W2-102
219305 | NAMERICA E | 26.4 | 231 | 75 | 0 | 4.34 | 0 |  |  | 0.00038 |  |  | 0 |  | 1 | NEWENERGY | W4-103
219349 | LDSOLAR E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | 0.00038 |  |  | 0 |  | 1 | NEWENERGY | Y3-026
219348 | LDSOLAR C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | 0.00038 |  |  | 0 |  | 1 | CAPACITY | Y3-026
219610 | FLORENCE C | 26.4 | 231 | 75 | 0 | 3.7 | 2.97 |  |  | 0.00038 |  |  | 0 |  | 1 | CAPACITY | W3-080
925441 | AC1-016 C | 26.4 | 231 | 75 | 0 | 3.34 | 2.68 |  |  | 0.00038 |  |  | 0 |  | 1 | CAPACITY | AC1-016
219685 | NATIONAL_GYP | 26 | 231 | 2 | 0 | 2.8 | 2.25 |  |  | 0.00038 |  |  | 0 |  | 1 | CAPACITY
219607 | WPEMNERT C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | 0.00038 |  |  | 0 |  | 1 | CAPACITY | W2-102
219304 | NAMERICA C | 26.4 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | 0.00038 |  |  | 0 |  | 1 | CAPACITY | W4-103
213537 | CROYDN21 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
213538 | CROYDN22 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
213536 | CROYDN12 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
213535 | CROYDN11 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
213539 | CROYDN31 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
213541 | CROYDN41 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
213542 | CROYDN42 | 13.8 | 230 | 56 | 10 | 49 | 39.34 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
213540 | CROYDN32 | 13.8 | 230 | 56 | 10 | 48 | 38.54 |  |  | 0.00032 |  |  | 0.08446 |  | 1 | CAPACITY
213621 | FORDBST1 | 18 | 230 | 58 | 55 | 260.3 | 208.98 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213618 | FORDAST1 | 18 | 230 | 58 | 55 | 256.2 | 205.69 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213619 | FORDBCT1 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | 0.0003 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill B
213620 | FORDBCT2 | 18 | 230 | 58 | 105 | 187 | 150.13 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Ford Mill B
213617 | FORDACT2 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | 0.0003 |  |  | 0 |  | 1 | CAPACITY | Ford Mill A
213616 | FORDACT1 | 18 | 230 | 58 | 105 | 183.9 | 147.65 |  |  | 0.0003 |  |  | 0.04435 |  | 1 | CAPACITY | Ford Mill A
925452 | AC1-017 E | 13.2 | 231 | 75 | 0 | 2.31 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | AC1-017
219619 | MILLCREEK E | 13.2 | 231 | 75 | 0 | 2.17 | 0 |  |  | 0.00026 |  |  | 0 |  | 1 | NEWENERGY | X1-070
925451 | AC1-017 C | 13.2 | 231 | 75 | 0 | 1.4 | 1.12 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | AC1-017
219615 | MILLCREEK C | 13.2 | 231 | 75 | 0 | 1.2 | 0.96 |  |  | 0.00026 |  |  | 0 |  | 1 | CAPACITY | X1-070
219689 | LUMSOLAR_S E | 13 | 231 | 75 | 0 | 2.1 | 0 |  |  | 0.00011 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 S
219688 | LUMSOLAR_S C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 0.00011 |  |  | 0 |  | 1 | CAPACITY | AB1-025 S
925562 | AC1-030 E | 13 | 231 | 75 | 0 | 1.5 | 0 |  |  | 9e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-030
219237 | SOUTHERNHQ E | 13.2 | 231 | 75 | 0 | 0.58 | 0 |  |  | 0.0001 |  |  | 0 |  | 1 | NEWENERGY | X1-071
925561 | AC1-030 C | 13 | 231 | 75 | 0 | 0.95 | 0.76 |  |  | 9e-05 |  |  | 0 |  | 1 | CAPACITY | AC1-030
219236 | SOUTHERNHQ C | 13.2 | 231 | 75 | 0 | 0.35 | 0.28 |  |  | 0.0001 |  |  | 0 |  | 1 | CAPACITY | X1-071
218661 | EHAMPSOLAR E | 13.2 | 231 | 75 | 0 | 1.8 | 0 |  |  | 6e-05 |  |  | 0 |  | 1 | NEWENERGY | V4-005
218660 | EHAMPSOLAR C | 13.2 | 231 | 75 | 0 | 1.1 | 0.88 |  |  | 6e-05 |  |  | 0 |  | 1 | CAPACITY | V4-005
219292 | REEVESSO E | 13.2 | 231 | 75 | 0 | 0.62 | 0 |  |  | 6e-05 |  |  | 0 |  | 1 | NEWENERGY | Y1-075
219291 | REEVESSOUT C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | 6e-05 |  |  | 0 |  | 1 | CAPACITY | Y1-075
219273 | CLEANLIGHT E | 13.2 | 231 | 75 | 0 | 1.74 | 0 |  |  | 4e-05 |  |  | 0 |  | 1 | NEWENERGY | W2-071
219272 | CLEANLIGHT C | 13.2 | 231 | 75 | 0 | 1.06 | 0.85 |  |  | 4e-05 |  |  | 0 |  | 1 | CAPACITY | W2-071
219288 | REEVES ST E | 13.2 | 231 | 75 | 0 | 6.82 | 0 |  |  | 3e-05 |  |  | 0 |  | 1 | NEWENERGY | W2-056
219687 | LUMSOLAR_N E | 13.2 | 231 | 75 | 0 | 2.1 | 0 |  |  | 4e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-025 N
219287 | REEVESEAST C | 13.2 | 231 | 75 | 0 | 4.18 | 3.36 |  |  | 3e-05 |  |  | 0 |  | 1 | CAPACITY | W2-056
219686 | LUMSOLAR_N C | 13.2 | 231 | 75 | 0 | 1.3 | 1.04 |  |  | 4e-05 |  |  | 0 |  | 1 | CAPACITY | AB1-025 N
219647 | COOPERSOLA E | 13.2 | 231 | 75 | 0 | 0.4 | 0 |  |  | -3e-05 |  |  | 0 |  | 1 | NEWENERGY | AB1-063
901112 | W1-032 E OP1 | 230 | 228 | 75 | 0 | 1.86 | 0 |  |  | -4e-05 |  |  | 0 |  | 1 | NEWENERGY | W1-032
219726 | BAT.STORG E | 13.2 | 231 | 76 | -1 | 1 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | MTX | Z1-082
206416 | 28MLH_W1-032 | 230 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -4e-05 |  |  | 0 |  | 1 | CAPACITY | W1-032
219913 | PENNSAU2 E | 26.4 | 231 | 75 | 0 | 8.2 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEWENERGY | AD2-042
219915 | CINNAMSOL E | 26.4 | 231 | 75 | 0 | 6.2 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEWENERGY | AD2-027
219912 | PENNSAU2 C | 26.4 | 231 | 75 | 0 | 5 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEW | AD2-042
910862 | OWENSCORIN E | 13.2 | 231 | 75 | 0 | 3 | 0 |  |  | -5e-05 |  |  | 0 |  | 1 | NEWENERGY | X3-075
219624 | KINSLEYBEA E | 13.2 | 231 | 75 | 0 | 2.36 | 0 |  |  | -6e-05 |  |  | 0 |  | 1 | NEWENERGY | Y3-087
219241 | PENNAS_GAS | 4.16 | 231 | 64 | 0 | 4.63 | 3.72 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY
219914 | CINNAMSOL C | 26.4 | 231 | 75 | 0 | 3.8 | 3.05 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY | AD2-027
219623 | KINSLEYBEA C | 13.2 | 231 | 75 | 0 | 2.29 | 1.84 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | Y3-087
219242 | PENNAS_SOLA | 4.16 | 231 | 64 | 0 | 0.5 | 0.4 |  |  | -5e-05 |  |  | 0 |  | 1 | CAPACITY
219126 | CAMDEN_CTG | 13.8 | 231 | 58 | 0 | 80.1 | 64.31 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | CAMDEN COGEN TECH
219124 | CAMDEN_STG | 13.8 | 231 | 58 | 0 | 65.2 | 52.35 |  |  | -6e-05 |  |  | 0.04435 |  | 1 | CAPACITY | CAMDEN COGEN TECH
925391 | AC1-010 C | 26.4 | 231 | 75 | 0 | 6 | 0 |  |  | -6e-05 |  |  | 0 |  | 1 | NEW | AC1-010
219286 | CAMD CO RR | 26.4 | 231 | 2 | 0 | 24 | 19.27 |  |  | -6e-05 |  |  | 0.10478 |  | 1 | CAPACITY
925392 | AC1-010 E | 26.4 | 231 | 75 | 0 | 3.8 | 0 |  |  | -6e-05 |  |  | 0 |  | 1 | NEWENERGY | AC1-010
219765 | PARADISE E | 26.4 | 231 | 75 | 0 | 3.2 | 0 |  |  | -6e-05 |  |  | 0 |  | 1 | NEWENERGY | U4-036
907272 | X1-085 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -7e-05 |  |  | 0 |  | 1 | NEWENERGY | X1-085
219267 | GLOU CO RR | 26.4 | 231 | 2 | 0 | 11.3 | 9.07 |  |  | -6e-05 |  |  | 0.10478 |  | 1 | CAPACITY
219240 | MANTUACREK E | 26.4 | 231 | 76 | -2 | 2 | 0 |  |  | -6e-05 |  |  | 0 |  | 1 | MTX | X2-013
219766 | PARADISE C | 26.4 | 231 | 75 | 0 | 1.9 | 1.53 |  |  | -6e-05 |  |  | 0 |  | 1 | CAPACITY | U4-036
207149 | 28UPF_X1-085 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -7e-05 |  |  | 0 |  | 1 | CAPACITY | X1-085
219230 | EAGLEPT_G1 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219231 | EAGLEPT_G2 | 13.8 | 231 | 58 | 55 | 83 | 66.64 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219229 | EAGLEPT_ST1 | 13.8 | 231 | 58 | 20 | 42 | 33.72 |  |  | -8e-05 |  |  | 0.04435 |  | 1 | CAPACITY | EAGLE POINT
219235 | EAGLEPT_ST2 | 13.8 | 231 | 58 | 0 | 30 | 24.08 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY | EAGLE POINT
219259 | KINSLEYDEP E | 13.2 | 231 | 75 | 0 | 3.1 | 0 |  |  | -8e-05 |  |  | 0 |  | 1 | NEWENERGY | Y2-081
219258 | KINSLEYDEP C | 13.2 | 231 | 75 | 0 | 2.66 | 2.14 |  |  | -8e-05 |  |  | 0 |  | 1 | CAPACITY | Y2-081
207400 | 28PL_AA1-060 | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.0001 |  |  | 0.05 |  | 1 | MTX
230406 | Q90 ST-CC | 22 | 234 | 58 | 80 | 337.7 | 271.13 |  |  | -0.00012 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230404 | Q90 GT1-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | -0.00012 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
230405 | Q90 GT2-CC | 18 | 234 | 58 | 0 | 201.4 | 161.7 |  |  | -0.00012 |  |  | 0.04435 |  | 1 | CAPACITY | Q90
228357 | V2-046E | 12.9 | 234 | 75 | 12.9 | 12.9 | 0 |  |  | -0.00012 |  |  | 0 |  | 1 | NEWENERGY | V2-046
228400 | MICK 1CT | 13.8 | 234 | 57 | 55.4 | 63.7 | 55.49 |  |  | -0.00011 |  |  | 0.08446 |  | 1 | CAPACITY
902092 | W1-130E | 12.9 | 234 | 75 | 0 | 5.7 | 0 |  |  | -0.00011 |  |  | 0 |  | 1 | NEWENERGY | W1-130
228471 | VALERO1 | 13.8 | 234 | 2 | 19.1 | 22 | 19.16 |  |  | -0.00011 |  |  | 0 |  | 1 | CAPACITY
228472 | VALERO2 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | -0.00011 |  |  | 0 |  | 1 | CAPACITY
228473 | VALERO3 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | -0.00011 |  |  | 0 |  | 1 | CAPACITY
228484 | VALERO4 | 13.8 | 234 | 2 | 0 | 10 | 8.03 |  |  | -0.00011 |  |  | 0 |  | 1 | CAPACITY
227881 | GRENWCHG | 2.4 | 234 | 2 | 1.7 | 1.7 | 0 |  |  | -0.00011 |  |  | 0 |  | 1 | ENERGY
228351 | V2-046C | 12.9 | 234 | 75 | 0 | 7.8 | 6.26 |  |  | -0.00012 |  |  | 0 |  | 1 | CAPACITY | V2-046
228721 | V2-035E | 12.9 | 234 | 75 | 1.2 | 1.2 | 0 |  |  | -0.00011 |  |  | 0 |  | 1 | NEWENERGY | V2-035
228728 | W1-130C | 12.9 | 234 | 75 | 0 | 3.2 | 2.57 |  |  | -0.00011 |  |  | 0 |  | 1 | CAPACITY | W1-130
228720 | V2-035C | 12.9 | 234 | 75 | 0 | 0.76 | 0.61 |  |  | -0.00011 |  |  | 0 |  | 1 | CAPACITY | V2-035
228309 | CCLP NUG | 23 | 234 | 13 | 46 | 240 | 192.69 |  |  | -0.00013 |  |  | 0.10478 |  | 1 | CAPACITY
228304 | LOGAN | 22 | 234 | 13 | 50 | 219 | 175.82 |  |  | -0.00012 |  |  | 0.10478 |  | 1 | CAPACITY
228307 | PCLP GT | 13.8 | 234 | 58 | 0 | 58.9 | 47.29 |  |  | -0.00012 |  |  | 0 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228306 | PCLP STM | 13.8 | 234 | 58 | 34.2 | 58.9 | 47.29 |  |  | -0.00012 |  |  | 0.04435 |  | 1 | CAPACITY | PEDRICKTOWN PCLP
228717 | S121 | 13.8 | 234 | 29 | 49.6 | 57 | 49.65 |  |  | -0.00012 |  |  | 0.10478 |  | 1 | CAPACITY
228727 | W2-039G | 13.8 | 234 | 29 | 48.3 | 55.5 | 48.35 |  |  | -0.00013 |  |  | 0.08446 |  | 1 | CAPACITY
228261 | V4-054E | 12.9 | 234 | 75 | 0 | 6.2 | 0 |  |  | -0.00013 |  |  | 0 |  | 1 | NEWENERGY | V4-054
228201 | CARL#2CT | 13.8 | 234 | 56 | 34.6 | 39.8 | 34.67 |  |  | -0.00013 |  |  | 0.08446 |  | 1 | CAPACITY
228200 | CARL#1CT | 13.8 | 234 | 56 | 32.7 | 37.6 | 32.75 |  |  | -0.00013 |  |  | 0.08446 |  | 1 | CAPACITY
228251 | CARLLS#4 | 12.9 | 234 | 64 | 0 | 4.8 | 0 |  |  | -0.00013 |  |  | 0 |  | 1 | NEW
228702 | WEST CT | 13.8 | 234 | 56 | 0 | 23.5 | 18.87 |  |  | -0.00012 |  |  | 0.08446 |  | 1 | CAPACITY
228343 | QUINTN#1 | 12.9 | 234 | 64 | 0 | 1.7 | 0 |  |  | -0.00013 |  |  | 0 |  | 1 | CAPACITY
228260 | V4-054C | 12.9 | 234 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00013 |  |  | 0 |  | 1 | CAPACITY | V4-054
228202 | CUMB CT | 13.8 | 234 | 57 | 74.4 | 85.5 | 74.48 |  |  | -0.00014 |  |  | 0.08446 |  | 1 | CAPACITY
228206 | SHRMN CT | 13.8 | 234 | 57 | 73 | 83.9 | 73.09 |  |  | -0.00013 |  |  | 0.08446 |  | 1 | CAPACITY
228712 | V2-041E | 13.2 | 234 | 75 | 2.5 | 2.48 | 0 |  |  | -0.00014 |  |  | 0 |  | 1 | NEWENERGY | V2-041
228711 | V2-041C | 13.2 | 234 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | V2-041
900000 | CARDIFF E | 230 | 234 | 74 | 0 | 1235 | 0 |  |  | -0.00014 |  |  | 0 |  | 1 | NEWENERGY | OSW_CARDIF
900001 | BLE E | 138 | 234 | 74 | 0 | 310.6 | 0 |  |  | -0.00014 |  |  | 0 |  | 1 | NEWENERGY | OSW_BLE
227801 | ONTC&DCT | 13.8 | 234 | 56 | 38.6 | 38.6 | 0 |  |  | -0.00014 |  |  | 0.08446 |  | 1 | NEW
228203 | P06 | 13.8 | 234 | 57 | 80.6 | 92.7 | 80.75 |  |  | -0.00014 |  |  | 0.08446 |  | 1 | CAPACITY
227842 | MARINGEN | 12.9 | 234 | 29 | 4 | 7.8 | 0 |  |  | -0.00014 |  |  | 0.12623 |  | 1 | ENERGY
902432 | W2-030 E | 12.9 | 234 | 75 | 0 | 6 | 0 |  |  | -0.00014 |  |  | 0 |  | 1 | NEWENERGY | W2-030
228731 | V3-036 | 23 | 234 | 55 | 0 | 5.5 | 0 |  |  | -0.00014 |  |  | 0.10478 |  | 1 | ENERGY
228014 | PVILLEG | 0.48 | 234 | 65 | 1.7 | 3 | 1.04 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY
227928 | V4-067E | 12.9 | 234 | 75 | 1.6 | 1.6 | 0 |  |  | -0.00014 |  |  | 0 |  | 1 | NEWENERGY | V4-067
924702 | AB2-122 E | 12.9 | 234 | 75 | 0 | 1.2 | 0 |  |  | -0.00014 |  |  | 0 |  | 1 | NEWENERGY | AB2-122
228729 | W2-030 C | 12.9 | 234 | 75 | 0 | 3.65 | 2.93 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | W2-030
228732 | V1-021 C | 0.48 | 234 | 64 | 0 | 2 | 1.61 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY
227927 | V4-067C | 12.9 | 234 | 75 | 0 | 0.98 | 0.79 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | V4-067
924701 | AB2-122 C | 12.9 | 234 | 75 | 0 | 0.7 | 0.56 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | AB2-122
228110 | BLE C | 138 | 234 | 74 | 0 | 121.4 | 121.4 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | OSW_BLE
227900 | CARDIFF C | 230 | 234 | 74 | 0 | 275 | 275 |  |  | -0.00014 |  |  | 0 |  | 1 | CAPACITY | OSW_CARDIF
902952 | W2-082 E OP1 | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00016 |  |  | 0 |  | 1 | NEWENERGY | W2-082
905252 | W4-025 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.00016 |  |  | 0 |  | 1 | NEWENERGY | W4-025
902322 | W2-019 E | 34.5 | 228 | 75 | 0 | 3.7 | 0 |  |  | -0.00015 |  |  | 0 |  | 1 | NEWENERGY | W2-019
902082 | W1-129E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00016 |  |  | 0 |  | 1 | NEWENERGY | W1-129
912102 | X4-015 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00016 |  |  | 0 |  | 1 | NEWENERGY | X4-015
207164 | 28NHV_W2-082 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00016 |  |  | 0 |  | 1 | CAPACITY | W2-082
207208 | 28JCB_W4-025 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.00016 |  |  | 0 |  | 1 | CAPACITY | W4-025
207160 | 28EGP_W2-019 | 34.5 | 228 | 75 | 0 | 2.3 | 1.85 |  |  | -0.00015 |  |  | 0 |  | 1 | CAPACITY | W2-019
207207 | 28JCB_W1-129 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00016 |  |  | 0 |  | 1 | CAPACITY | W1-129
207150 | 28HAN_X4-015 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00016 |  |  | 0 |  | 1 | CAPACITY | X4-015
930002 | AB1-001 E | 12.9 | 234 | 75 | 0 | 1.43 | 0 |  |  | -0.00016 |  |  | 0 |  | 1 | NEWENERGY | AB1-001
228754 | AB1-001 C | 12.9 | 234 | 75 | 0 | 0.87 | 0.7 |  |  | -0.00016 |  |  | 0 |  | 1 | CAPACITY | AB1-001
917612 | Z2-102 E | 34.5 | 228 | 75 | 0 | 8.06 | 0 |  |  | -0.00018 |  |  | 0 |  | 1 | NEWENERGY | Z2-102
901982 | W1-119 E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.00018 |  |  | 0 |  | 1 | NEWENERGY | W1-119
901992 | W1-120E | 34.5 | 228 | 75 | 0 | 5.46 | 0 |  |  | -0.00018 |  |  | 0 |  | 1 | NEWENERGY | W1-120
207171 | 28DIX_Z2-102 | 34.5 | 228 | 75 | 0 | 4.94 | 3.97 |  |  | -0.00018 |  |  | 0 |  | 1 | CAPACITY | Z2-102
207158 | 28PEM_W1-120 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.00018 |  |  | 0 |  | 1 | CAPACITY | W1-120
207157 | 28PEM_W1-119 | 34.5 | 228 | 75 | 0 | 3.34 | 2.68 |  |  | -0.00018 |  |  | 0 |  | 1 | CAPACITY | W1-119
213918 | RICHMD91 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.00019 |  |  | 0.08446 |  | 1 | CAPACITY
213919 | RICHMD92 | 13.8 | 230 | 56 | 20 | 49 | 39.34 |  |  | -0.00019 |  |  | 0.08446 |  | 1 | CAPACITY
213400 | COVANTA DELA | 13.8 | 230 | 1 | 20 | 75 | 60.21 |  |  | -0.00026 |  |  | 0.10478 |  | 1 | CAPACITY
901032 | W1-024E OP1 | 34.5 | 228 | 0 | 0 | 0 | 0 |  |  | -0.00026 |  |  | 0 |  | 1 | NEW
207205 | 28MAN_W1-024 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00026 |  |  | 0 |  | 1 | CAPACITY | W1-024
902912 | W2-078 E | 34.5 | 228 | 75 | 0 | 5.6 | 0 |  |  | -0.00026 |  |  | 0 |  | 1 | NEWENERGY | W2-078
901422 | W1-113 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.00026 |  |  | 0 |  | 1 | NEWENERGY | W1-113
207162 | 28APLW2-078 | 34.5 | 228 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00026 |  |  | 0 |  | 1 | CAPACITY | W2-078
207152 | 28NPK_W1-113 | 34.5 | 228 | 75 | 0 | 2.8 | 2.25 |  |  | -0.00026 |  |  | 0 |  | 1 | CAPACITY | W1-113
900002 | 28OYSTER E | 230 | 228 | 74 | 0 | 586.7 | 0 |  |  | -0.00027 |  |  | 0 |  | 1 | NEWENERGY | OSW_OYSCK
200039 | HOPE CG1 | 22 | 231 | 41 | 1025.1 | 1178.3 | 1026.43 |  |  | -0.00028 |  |  | 0.01494 |  | 1 | CAPACITY
200036 | SALEM-G1 | 22 | 231 | 41 | 996.8 | 1145.8 | 998.11 |  |  | -0.00027 |  |  | 0.01494 |  | 1 | CAPACITY
200037 | SALEM-G2 | 22 | 231 | 41 | 990.8 | 1138.9 | 992.1 |  |  | -0.00027 |  |  | 0.01494 |  | 1 | CAPACITY
200062 | SALEM G3 | 22 | 231 | 56 | 0 | 38.4 | 0 |  |  | -0.00027 |  |  | 0.08446 |  | 1 | ENERGY
206360 | 28O CRK C1 | 13.8 | 228 | 65 | 18 | 34 | 27.3 |  |  | -0.00027 |  |  | 0.12623 |  | 1 | CAPACITY
206361 | 28O CRK C2 | 13.8 | 228 | 65 | 27 | 31 | 27 |  |  | -0.00027 |  |  | 0.12623 |  | 1 | CAPACITY
206302 | 28OYSTER C | 230 | 228 | 74 | 0 | 229.3 | 229.3 |  |  | -0.00027 |  |  | 0 |  | 1 | CAPACITY | OSW_OYSCK
217825 | UMD_NJ | 26 | 231 | 2 | 0 | 10.5 | 8.43 |  |  | -0.00028 |  |  | 0 |  | 1 | CAPACITY
923463 | AB1-163 E | 34.5 | 228 | 75 | 0 | 5 | 0 |  |  | -0.00029 |  |  | 0 |  | 1 | NEWENERGY | AB1-163
923293 | AB1-138 E | 34.5 | 228 | 75 | 0 | 6 | 0 |  |  | -0.0003 |  |  | 0 |  | 1 | NEWENERGY | AB1-138
206280 | 28LAKEHURS | 34.5 | 228 | 64 | 0 | 13.8 | 11.08 |  |  | -0.0003 |  |  | 0.08446 |  | 1 | CAPACITY
923292 | AB1-138 C | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.0003 |  |  | 0 |  | 1 | CAPACITY | AB1-138
206367 | 28LKWD CT2 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
206366 | 28LKWD CT1 | 18 | 228 | 57 | 99.3 | 168.1 | 134.96 |  |  | -0.00031 |  |  | 0.08446 |  | 1 | CAPACITY
206306 | 28LKWD G1 | 13.8 | 228 | 58 | 61.6 | 88.4 | 70.97 |  |  | -0.00031 |  |  | 0.04435 |  | 1 | CAPACITY | LAKEWOOD
206308 | 28LKWD G2 | 13.8 | 228 | 58 | 61.2 | 88.3 | 70.89 |  |  | -0.00031 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
206312 | 28LKWD G3 | 13.8 | 228 | 58 | 76.8 | 88.3 | 76.92 |  |  | -0.00031 |  |  | 0 |  | 1 | CAPACITY | LAKEWOOD
207419 | AB2-139 E | 34.5 | 228 | 76 | 0 | 0.21 | 0 |  |  | -0.00031 |  |  | 0 |  | 1 | ENERGY | AB2-139
900005 | 28LARRABEE E | 230 | 228 | 74 | 0 | 840 | 0 |  |  | -0.00032 |  |  | 0 |  | 1 | NEWENERGY | OSW_LARRAB
206294 | 28LARRABEE C | 230 | 228 | 74 | 0 | 360 | 360 |  |  | -0.00032 |  |  | 0 |  | 1 | CAPACITY | OSW_LARRAB
914092 | Y2-051 E | 34.5 | 228 | 75 | 0 | 3.1 | 0 |  |  | -0.00039 |  |  | 0 |  | 1 | NEWENERGY | Y2-051
207145 | 28FRN_Y2-051 | 34.5 | 228 | 75 | 0 | 1.9 | 1.53 |  |  | -0.00039 |  |  | 0 |  | 1 | CAPACITY | Y2-051
919662 | AA2-048 E | 34.5 | 228 | 76 | -7 | 7 | 0 |  |  | -0.00041 |  |  | 0.05 |  | 1 | MTX | AA2-048
213561 | DLWR9-10 | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.0004 |  |  | 0.08446 |  | 1 | CAPACITY
213560 | DLW11-12 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.0004 |  |  | 0.08446 |  | 1 | CAPACITY
903982 | W3-079 E | 34.5 | 228 | 75 | 0 | 4.4 | 0 |  |  | -0.00041 |  |  | 0 |  | 1 | NEWENERGY | W3-079
207148 | 28MDF_W3-079 | 34.5 | 228 | 75 | 0 | 2.6 | 2.09 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY | W3-079
214030 | WAYNEJCT | 13.8 | 230 | 2 | 0 | 8.8 | 7.07 |  |  | -0.00041 |  |  | 0 |  | 1 | CAPACITY
927132 | AC1-207 E | 34.5 | 228 | 75 | 0 | 8.2 | 0 |  |  | -0.00042 |  |  | 0 |  | 1 | NEWENERGY | AC1-207
207420 | AC1-207 C | 34.5 | 228 | 75 | 0 | 4.9 | 3.93 |  |  | -0.00042 |  |  | 0 |  | 1 | CAPACITY | AC1-207
919831 | AA2-069 | 230 | 235 | 58 | 0 | 451 | 0 |  |  | -0.00047 |  |  | 0.04435 |  | 1 | NEW | AA2-069
233920 | W3-032A-CTG1 | 18 | 235 | 58 | 0 | 193 | 154.95 |  |  | -0.00047 |  |  | 0.04435 |  | 1 | CAPACITY | Garrison
233921 | W3-032A-STG1 | 13.8 | 235 | 58 | 0 | 116.2 | 93.29 |  |  | -0.00047 |  |  | 0 |  | 1 | CAPACITY | Garrison
232899 | W1-062 | 138 | 235 | 57 | 0 | 49 | 39.34 |  |  | -0.00048 |  |  | 0.08446 |  | 1 | CAPACITY
232900 | DEMECSMY | 138 | 235 | 57 | 0 | 48 | 38.54 |  |  | -0.00048 |  |  | 0.08446 |  | 1 | CAPACITY
232901 | NORTHST | 69 | 235 | 56 | 5 | 46 | 36.93 |  |  | -0.00047 |  |  | 0.08446 |  | 1 | CAPACITY
232616 | GEN FOOD | 13.2 | 235 | 11 | 0 | 15.2 | 12.2 |  |  | -0.00047 |  |  | 0.10478 |  | 1 | CAPACITY
930202 | AB1-056 E | 230 | 235 | 74 | 0 | 183.4 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AB1-056
918835 | AA1-102 E | 0.55 | 235 | 75 | 0 | 93 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | AA1-102
232904 | IR4 | 26 | 235 | 15 | 80 | 411.9 | 330.7 |  |  | -0.00049 |  |  | 0.10478 |  | 1 | CAPACITY
231914 | HR8 | 18 | 235 | 58 | 50 | 190 | 152.54 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231911 | HR5 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | -0.0005 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC2
231913 | HR7 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
231912 | HR6 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC2
930201 | AB1-056 C | 230 | 235 | 74 | 0 | 64.4 | 51.71 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AB1-056
917082 | CHERRYDALE E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | Z2-012
232411 | W1-006 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | W1-006
232409 | W1-005 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | W1-005
232407 | W1-004 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | W1-004
232405 | W1-003 E | 138 | 235 | 75 | 0 | 12.4 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | W1-003
233923 | AA1-102 C | 0.55 | 235 | 75 | 0 | 57 | 45.76 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | AA1-102
232851 | DUP-SFR1 | 12.5 | 235 | 29 | 0 | 10 | 0 |  |  | -0.00049 |  |  | 0.10478 |  | 1 | ENERGY
232429 | Y3-058 E | 69 | 235 | 75 | 0 | 9.3 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | Y3-058
232911 | NRG_G2 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | -0.00049 |  |  | 0.08446 |  | 1 | CAPACITY
232910 | NRG_G1 | 13.8 | 235 | 56 | 0 | 44 | 35.33 |  |  | -0.00049 |  |  | 0.08446 |  | 1 | CAPACITY
232912 | OH NUG1 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | -0.0005 |  |  | 0.08446 |  | 1 | CAPACITY
232915 | OH NUG4 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | -0.0005 |  |  | 0.08446 |  | 1 | CAPACITY
232914 | OH NUG3 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | -0.0005 |  |  | 0.08446 |  | 1 | CAPACITY
232916 | OH NUG5 | 13.8 | 235 | 53 | 39.2 | 45 | 39.2 |  |  | -0.0005 |  |  | 0.08446 |  | 1 | CAPACITY
232917 | OH NUG6 | 13.8 | 235 | 53 | 39 | 44.8 | 39.03 |  |  | -0.0005 |  |  | 0.08446 |  | 1 | CAPACITY
232918 | OH NUG7 | 13.8 | 235 | 53 | 38.9 | 44.7 | 38.94 |  |  | -0.0005 |  |  | 0.08446 |  | 1 | CAPACITY
232913 | OH NUG2 | 13.8 | 235 | 53 | 38.6 | 44.4 | 38.68 |  |  | -0.0005 |  |  | 0.08446 |  | 1 | CAPACITY
232412 | X1-032 E | 138 | 235 | 75 | 0 | 4 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | X1-032
232921 | TASLEY2G | 13.2 | 235 | 56 | 26 | 29.9 | 26.05 |  |  | -0.0005 |  |  | 0.08446 |  | 1 | CAPACITY
232920 | IR10 | 13.2 | 235 | 55 | 12.6 | 16.1 | 12.93 |  |  | -0.00049 |  |  | 0.08446 |  | 1 | CAPACITY
232406 | W1-004 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | W1-004
232404 | W1-003 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | W1-003
232408 | W1-005 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | W1-005
232410 | W1-006 C | 138 | 235 | 75 | 0 | 13.36 | 10.73 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | W1-006
232905 | BAYVIEW1 | 24.9 | 235 | 65 | 0 | 12.5 | 10.04 |  |  | -0.0005 |  |  | 0.12623 |  | 1 | CAPACITY
232433 | Z2-076 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | Z2-076
232435 | Z2-077 E | 24.9 | 235 | 75 | 0 | 2.01 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | Z2-077
232926 | CRISFLD1 | 12.5 | 235 | 65 | 0 | 10 | 8.03 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY
233912 | AB1-137 E | 0.69 | 235 | 75 | 0 | 1.8 | 0 |  |  | -0.00049 |  |  | 0 |  | 1 | NEWENERGY | AB1-137
917081 | CHERRYDALE C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | Z2-012
293670 | O-025 C | 25 | 235 | 64 | 0 | 6 | 4.82 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY
232428 | Y3-058 C | 69 | 235 | 75 | 0 | 5.7 | 4.58 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | Y3-058
233911 | AB1-137 C | 0.69 | 235 | 75 | 0 | 4.2 | 3.37 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | AB1-137
232434 | Z2-077 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | Z2-077
232432 | Z2-076 C | 24.9 | 235 | 75 | 0 | 3.99 | 3.2 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY | Z2-076
231940 | T-011 | 69 | 235 | 64 | 0 | 3.8 | 3.05 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY
232813 | VAUGHN | 69 | 235 | 64 | 0 | 3 | 2.41 |  |  | -0.00049 |  |  | 0 |  | 1 | CAPACITY
232907 | VN8 | 18 | 235 | 21 | 50 | 153 | 122.84 |  |  | -0.0005 |  |  | 0.10478 |  | 1 | CAPACITY
232418 | X3-008 E | 69 | 235 | 75 | 0 | 12.4 | 0 |  |  | -0.00051 |  |  | 0 |  | 1 | NEWENERGY | X3-008
213957 | STHWK3-4 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.00051 |  |  | 0.08446 |  | 1 | CAPACITY
213958 | STHWK5-6 | 13.8 | 230 | 55 | 10 | 26 | 20.87 |  |  | -0.00051 |  |  | 0.08446 |  | 1 | CAPACITY
232427 | Y1-080 E | 69 | 235 | 75 | 0 | 2.1 | 0 |  |  | -0.0005 |  |  | 0 |  | 1 | NEWENERGY | Y1-080
232919 | VN10 | 13.2 | 235 | 55 | 12.4 | 14.3 | 12.46 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY
232417 | X3-008 C | 69 | 235 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00051 |  |  | 0 |  | 1 | CAPACITY | X3-008
232426 | Y1-080 FULL | 69 | 235 | 75 | 0 | 1.28 | 1.03 |  |  | -0.0005 |  |  | 0 |  | 1 | CAPACITY | Y1-080
231906 | DC3 NUG | 13.8 | 235 | 57 | 0 | 71.3 | 57.24 |  |  | -0.00052 |  |  | 0.10478 |  | 1 | CAPACITY
232902 | EASTMUNI | 69 | 235 | 65 | 0 | 69 | 55.4 |  |  | -0.00052 |  |  | 0.12623 |  | 1 | CAPACITY
231902 | DC CT7 | 13.8 | 235 | 57 | 0 | 57 | 45.76 |  |  | -0.00052 |  |  | 0.08446 |  | 1 | CAPACITY
231915 | DC CT6 | 13.8 | 235 | 57 | 0 | 55 | 44.16 |  |  | -0.00052 |  |  | 0.04435 |  | 1 | CAPACITY | DELAWARE CITY
231131 | BLOOM ENRGY | 138 | 235 | 64 | 0 | 23.8 | 19.11 |  |  | -0.00052 |  |  | 0.12623 |  | 1 | CAPACITY
231907 | DC10 | 13.8 | 235 | 55 | 5 | 17.8 | 14.29 |  |  | -0.00052 |  |  | 0.08446 |  | 1 | CAPACITY
213893 | PHLISST1 | 20 | 230 | 58 | 184 | 267 | 214.36 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213890 | PHLISCT3 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213888 | PHLISCT1 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00053 |  |  | 0.04435 |  | 1 | CAPACITY | PHILLIPS ISLAND
213889 | PHLISCT2 | 18 | 230 | 58 | 100 | 182 | 146.12 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | PHILLIPS ISLAND
213632 | GFCP | 13.8 | 230 | 58 | 27 | 163 | 130.87 |  |  | -0.00053 |  |  | 0.04435 |  | 1 | CAPACITY | GRAYS FERRY
233919 | AB1-142 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY | AB1-142
233916 | AB1-141 E | 0.55 | 235 | 75 | 0 | 6.3 | 0 |  |  | -0.00053 |  |  | 0 |  | 1 | NEWENERGY | AB1-141
232425 | Y1-079 E | 24.9 | 235 | 75 | 0 | 6.2 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | Y1-079
213942 | SCHUYLKILL | 13.8 | 230 | 55 | 10 | 30 | 24.08 |  |  | -0.00052 |  |  | 0.08446 |  | 1 | CAPACITY
232423 | X3-066 E | 12.5 | 235 | 75 | 0 | 3.72 | 0 |  |  | -0.00052 |  |  | 0 |  | 1 | NEWENERGY | X3-066
233915 | AB1-141 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | AB1-141
233918 | AB1-142 C | 0.55 | 235 | 75 | 0 | 13.5 | 10.84 |  |  | -0.00053 |  |  | 0 |  | 1 | CAPACITY | AB1-142
232424 | Y1-079 C | 24.9 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | Y1-079
232422 | X3-066 C | 12.5 | 235 | 75 | 0 | 2.28 | 1.83 |  |  | -0.00052 |  |  | 0 |  | 1 | CAPACITY | X3-066
231900 | EM5 | 23 | 235 | 24 | 100 | 450 | 361.29 |  |  | -0.00053 |  |  | 0.10478 |  | 1 | CAPACITY
213587 | EDDYSTN3 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00054 |  |  | 0.10478 |  | 1 | CAPACITY
213589 | EDDYSTN4 | 24 | 230 | 23 | 38 | 380 | 305.09 |  |  | -0.00054 |  |  | 0.10478 |  | 1 | CAPACITY
213740 | LIBE_ST1 | 18 | 230 | 58 | 120 | 238 | 191.08 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
231505 | HR4 | 18 | 235 | 58 | 50 | 185.3 | 148.77 |  |  | -0.00053 |  |  | 0.04435 |  | 1 | CAPACITY | Hay Road CC1
213739 | LIBE_CT2 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | LIBERTY EDDY
213738 | LIBE_CT1 | 18 | 230 | 58 | 65 | 178.5 | 143.31 |  |  | -0.00054 |  |  | 0.04435 |  | 1 | CAPACITY | LIBERTY EDDY
231901 | EM4 | 19 | 235 | 12 | 50 | 174 | 139.7 |  |  | -0.00054 |  |  | 0.10478 |  | 1 | CAPACITY
231908 | HR1 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231910 | HR3 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231909 | HR2 | 13.8 | 235 | 58 | 80 | 125 | 100.36 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY | Hay Road CC1
231916 | EM3 | 13.2 | 235 | 11 | 30 | 86 | 69.05 |  |  | -0.00054 |  |  | 0.10478 |  | 1 | CAPACITY
213590 | EDY30-40 | 13.8 | 230 | 55 | 10 | 34 | 27.3 |  |  | -0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
231919 | CHRIST1 | 12 | 235 | 56 | 0 | 23 | 18.47 |  |  | -0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
231920 | CHRIST2 | 12 | 235 | 56 | 0 | 22.9 | 18.39 |  |  | -0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
216404 | AE2-010_CTG2 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
216403 | AE2-010_CTG1 | 13.2 | 230 | 55 | 0 | 14.5 | 11.64 |  |  | -0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
231917 | EM10 | 13.1 | 235 | 55 | 5 | 14.2 | 11.4 |  |  | -0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
925254 | AB2-179 E | 0.38 | 235 | 75 | 0 | 12.4 | 0 |  |  | -0.00055 |  |  | 0 |  | 1 | NEWENERGY | AB2-179
213497 | CHSTR7-9 | 13.8 | 230 | 55 | 15 | 39 | 31.31 |  |  | -0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
233931 | AB2-179 C | 0.38 | 235 | 75 | 0 | 38 | 30.51 |  |  | -0.00055 |  |  | 0 |  | 1 | CAPACITY | AB2-179
231918 | WEST 1 | 12 | 235 | 55 | 5 | 17.2 | 13.81 |  |  | -0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
213575 | EDDYST10 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
213577 | EDDYST20 | 13.8 | 230 | 55 | 5 | 13 | 10.44 |  |  | -0.00054 |  |  | 0.08446 |  | 1 | CAPACITY
232416 | X2-083 | 34.5 | 235 | 64 | 0 | 2.6 | 2.09 |  |  | -0.00054 |  |  | 0 |  | 1 | CAPACITY
925112 | AB2-168 E | 34.5 | 235 | 75 | 0 | 5.2 | 0 |  |  | -0.00058 |  |  | 0 |  | 1 | NEWENERGY | AB2-168
925111 | AB2-168 C | 34.5 | 235 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00058 |  |  | 0 |  | 1 | CAPACITY | AB2-168
206201 | 28JERSVGEN | 34.5 | 228 | 2 | 0 | 2 | 1.61 |  |  | -0.00058 |  |  | 0 |  | 1 | CAPACITY
907082 | X1-037 E | 34.5 | 228 | 75 | 0 | 10.54 | 0 |  |  | -0.00059 |  |  | 0 |  | 1 | NEWENERGY | X1-037
207144 | 28HOW_X1-037 | 34.5 | 228 | 75 | 0 | 4.2 | 3.37 |  |  | -0.00059 |  |  | 0 |  | 1 | CAPACITY | X1-037
207143 | 28BYD_X4-031 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.0007 |  |  | 0 |  | 1 | NEWENERGY | X4-031
213806 | COVANTA PLYM | 13.8 | 230 | 2 | 4.7 | 28 | 22.48 |  |  | -0.00071 |  |  | 0.10478 |  | 1 | CAPACITY
213554 | DALEVLLE | 35 | 230 | 64 | 0 | 4 | 0 |  |  | -0.00079 |  |  | 0 |  | 1 | ENERGY
213508 | CON10-11 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | -0.00081 |  |  | 0.07484 |  | 1 | CAPACITY
213518 | CONOW8-9 | 13.8 | 230 | 61 | 65 | 130 | 104.37 |  |  | -0.00081 |  |  | 0.07484 |  | 1 | CAPACITY
213515 | CONOW3-4 | 13.8 | 230 | 61 | 44 | 96 | 77.07 |  |  | -0.00081 |  |  | 0.07484 |  | 1 | CAPACITY
213516 | CONOW5-6 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | -0.00081 |  |  | 0.07484 |  | 1 | CAPACITY
213514 | CONOW1-2 | 13.8 | 230 | 61 | 34 | 84 | 67.44 |  |  | -0.00081 |  |  | 0.07484 |  | 1 | CAPACITY
213517 | CONOW7 | 13.8 | 230 | 61 | 22 | 48 | 38.54 |  |  | -0.00081 |  |  | 0.07484 |  | 1 | CAPACITY
213798 | MERCK 3 | 13.8 | 230 | 2 | 13 | 35 | 28.1 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY
213797 | MERCK 2 | 13.8 | 230 | 2 | 4 | 25 | 20.07 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY
214194 | N WALES4 | 35 | 230 | 65 | 0 | 4.1 | 3.29 |  |  | -0.00082 |  |  | 0 |  | 1 | CAPACITY
213815 | MOSER1-3 | 13.8 | 230 | 55 | 15 | 51 | 40.94 |  |  | -0.00082 |  |  | 0.08446 |  | 1 | CAPACITY
902032 | W1-124E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00086 |  |  | 0 |  | 1 | NEWENERGY | W1-124
921743 | AA2-049 E | 34.5 | 228 | 76 | -3 | 3 | 0 |  |  | -0.00086 |  |  | 0 |  | 1 | MTX | AA2-049
207206 | 28TIN_W1-124 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.00086 |  |  | 0 |  | 1 | CAPACITY | W1-124
920732 | AA2-184 E | 34.5 | 228 | 75 | 0 | 20 | 0 |  |  | -0.00088 |  |  | 0 |  | 1 | NEWENERGY | AA2-184
213742 | LIMERCK1 | 22 | 230 | 41 | 55 | 1119.7 | 898.96 |  |  | -0.00091 |  |  | 0.01494 |  | 1 | CAPACITY
200203 | Y1-065-STG | 23.5 | 225 | 58 | 0 | 460 | 369.31 |  |  | -0.00097 |  |  | 0.04435 |  | 1 | CAPACITY | Y1-065
200204 | Y1-065-CTG1 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200205 | Y1-065-CTG2 | 21 | 225 | 58 | 100 | 266 | 213.56 |  |  | -0.00097 |  |  | 0 |  | 1 | CAPACITY | Y1-065
200055 | ROCKSP 4 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 4
200054 | ROCKSP 3 | 18 | 225 | 57 | 147 | 169 | 147.22 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 3
200052 | ROCKSP 1 | 18 | 225 | 57 | 145.7 | 167.5 | 145.91 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 1
200053 | ROCKSP 2 | 18 | 225 | 57 | 144.9 | 166.5 | 145.04 |  |  | -0.00097 |  |  | 0.08446 |  | 1 | CAPACITY | Rock Springs 2
213793 | MDYRN3-4 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | -0.00101 |  |  | 0.0316 |  | 1 | CAPACITY
213795 | MDYRN7-8 | 13.8 | 230 | 62 | 0 | 268 | 215.17 |  |  | -0.00101 |  |  | 0.0316 |  | 1 | CAPACITY
213792 | MDYRN1-2 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | -0.00101 |  |  | 0.0316 |  | 1 | CAPACITY
213794 | MDYRN5-6 | 13.8 | 230 | 62 | 0 | 267 | 214.36 |  |  | -0.00101 |  |  | 0.0316 |  | 1 | CAPACITY
200042 | LIMERCK2 | 22 | 230 | 41 | 55 | 1122.1 | 900.89 |  |  | -0.00103 |  |  | 0.01494 |  | 1 | CAPACITY
200035 | PCHBTM 3 | 22 | 230 | 41 | 150 | 1307 | 1049.33 |  |  | -0.00109 |  |  | 0.01494 |  | 1 | CAPACITY
200034 | PCHBTM 2 | 22 | 230 | 41 | 150 | 1288.2 | 1034.24 |  |  | -0.00109 |  |  | 0.01494 |  | 1 | CAPACITY
200202 | DELTA2 ST | 19.5 | 230 | 58 | 0 | 382 | 306.69 |  |  | -0.00109 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200200 | DELTA2 CT1 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | -0.00109 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA2
200201 | DELTA2 CT2 | 18 | 230 | 58 | 0 | 224 | 179.84 |  |  | -0.00109 |  |  | 0 |  | 1 | CAPACITY | DELTA2
200195 | DELTA ST | 18 | 230 | 58 | 50 | 193 | 154.95 |  |  | -0.00109 |  |  | 0 |  | 1 | CAPACITY | DELTA
200193 | DELTA CT2 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | -0.00109 |  |  | 0 |  | 1 | CAPACITY | DELTA
200192 | DELTA CT1 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | -0.00109 |  |  | 0.04435 |  | 1 | CAPACITY | DELTA
200194 | DELTA CT3 | 13.8 | 230 | 58 | 80 | 125 | 100.36 |  |  | -0.00109 |  |  | 0 |  | 1 | CAPACITY | DELTA
901912 | W1-112E OP1 | 34.5 | 228 | 75 | 0 | 2.48 | 0 |  |  | -0.00119 |  |  | 0 |  | 1 | NEWENERGY | W1-112
207204 | 28HOL_W1-112 | 34.5 | 228 | 75 | 0 | 1.52 | 1.22 |  |  | -0.00119 |  |  | 0 |  | 1 | CAPACITY | W1-112
220911 | PERRYG51 | 18 | 232 | 57 | 10 | 140.6 | 112.88 |  |  | -0.00129 |  |  | 0.08446 |  | 1 | CAPACITY
220923 | PERRY U6 | 13.8 | 232 | 57 | 10 | 113.6 | 91.2 |  |  | -0.00129 |  |  | 0.08446 |  | 1 | CAPACITY
220910 | PERRYG34 | 13.8 | 232 | 57 | 10 | 104 | 83.5 |  |  | -0.00129 |  |  | 0.08446 |  | 1 | CAPACITY
220909 | PERRYG12 | 13.8 | 232 | 57 | 10 | 52 | 41.75 |  |  | -0.00129 |  |  | 0.08446 |  | 1 | CAPACITY
223204 | AA2-072 E | 34.5 | 232 | 75 | 0 | 1.1 | 0 |  |  | -0.00128 |  |  | 0 |  | 1 | NEWENERGY | AA2-072
223205 | Y2-100 | 34.5 | 232 | 64 | 0 | 4 | 3.21 |  |  | -0.00129 |  |  | 0 |  | 1 | CAPACITY
220904 | CRANE G2 | 20 | 232 | 12 | 60 | 195 | 0 |  |  | -0.0013 |  |  | 0.10478 |  | 1 | NEW
220905 | CRANE GT | 4.16 | 232 | 55 | 0 | 14 | 0 |  |  | -0.0013 |  |  | 0.08446 |  | 1 | NEW
220902 | BRANDNG2 | 24 | 232 | 16 | 220 | 642.7 | 516 |  |  | -0.00131 |  |  | 0.10478 |  | 1 | CAPACITY
220901 | BRANDNG1 | 24 | 232 | 16 | 220 | 638.9 | 512.95 |  |  | -0.00131 |  |  | 0.10478 |  | 1 | CAPACITY
220920 | WAGNERG4 | 24 | 232 | 23 | 60 | 397 | 318.73 |  |  | -0.00131 |  |  | 0.10478 |  | 1 | CAPACITY
200061 | HUNTR401 | 22 | 227 | 58 | 77.7 | 319.2 | 256.27 |  |  | -0.00131 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
220919 | WAGNERG3 | 18 | 232 | 14 | 130 | 306.4 | 246 |  |  | -0.00131 |  |  | 0.10478 |  | 1 | CAPACITY
200058 | HUNTR101 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | -0.00131 |  |  | 0.04435 |  | 1 | CAPACITY | HUNTERSTOWN
200060 | HUNTR301 | 18 | 227 | 58 | 62.3 | 167 | 134.08 |  |  | -0.00131 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
200059 | HUNTR201 | 18 | 227 | 58 | 0 | 167 | 134.08 |  |  | -0.00131 |  |  | 0 |  | 1 | CAPACITY | HUNTERSTOWN
220917 | WAGNERG1 | 16.5 | 232 | 68 | 20 | 128.1 | 102.85 |  |  | -0.00131 |  |  | 0.10478 |  | 1 | CAPACITY
220932 | BRESCOG1 | 13.8 | 232 | 1 | 5 | 57 | 45.76 |  |  | -0.0013 |  |  | 0.10478 |  | 1 | CAPACITY
223202 | Q-031 | 34.5 | 232 | 55 | 0 | 10 | 0 |  |  | -0.00131 |  |  | 0.08446 |  | 1 | ENERGY
220913 | PHIL G12 | 13.8 | 232 | 55 | 6 | 30.5 | 24.49 |  |  | -0.0013 |  |  | 0.08446 |  | 1 | CAPACITY
220912 | PHIL G34 | 13.8 | 232 | 55 | 6 | 30 | 24.08 |  |  | -0.0013 |  |  | 0.08446 |  | 1 | CAPACITY
220921 | WAGNR GT | 4.16 | 232 | 55 | 0 | 13.3 | 10.68 |  |  | -0.00131 |  |  | 0.08446 |  | 1 | CAPACITY
223206 | V4-038 | 34.5 | 232 | 64 | 0 | 1 | 0 |  |  | -0.0013 |  |  | 0 |  | 1 | ENERGY
223203 | V3-037 | 34.5 | 232 | 64 | 0 | 3.1 | 2.49 |  |  | -0.00132 |  |  | 0 |  | 1 | CAPACITY
200040 | C CLF G1 | 25 | 232 | 40 | 50 | 866 | 695.27 |  |  | -0.00134 |  |  | 0.01494 |  | 1 | CAPACITY
200041 | C CLF G2 | 22 | 232 | 40 | 50 | 841.8 | 675.85 |  |  | -0.00134 |  |  | 0.01494 |  | 1 | CAPACITY
226896 | D-009 | 13.8 | 233 | 55 | 0 | 10 | 0 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | ENERGY
226895 | WOAKV2-037 E | 69 | 233 | 65 | 0 | 4.5 | 0 |  |  | -0.00133 |  |  | 0 |  | 1 | ENERGY
910861 | X3-087 C | 230 | 233 | 58 | 0 | 744 | 597.33 |  |  | -0.00135 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
224047 | MORGTU2 | 24 | 233 | 16 | 203 | 619.4 | 497.29 |  |  | -0.00134 |  |  | 0.10478 |  | 1 | CAPACITY
224046 | MORGTU1 | 18 | 233 | 16 | 197 | 613.3 | 492.39 |  |  | -0.00134 |  |  | 0.10478 |  | 1 | CAPACITY
224037 | CHALK U3 | 24 | 233 | 25 | 112 | 595 | 477.7 |  |  | -0.00134 |  |  | 0.10478 |  | 1 | CAPACITY
224038 | CHALK U4 | 24 | 233 | 25 | 112 | 585.3 | 469.91 |  |  | -0.00134 |  |  | 0.10478 |  | 1 | CAPACITY
226894 | V3-017 ST1 | 18 | 233 | 58 | 75 | 338.8 | 272.01 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY | WALDORF
200305 | X4-035_ST | 19 | 233 | 58 | 0 | 330 | 264.94 |  |  | -0.00135 |  |  | 0 |  | 1 | CAPACITY | X4-035
226893 | V3-017 CT2 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY | WALDORF
226892 | V3-017 CT1 | 18 | 233 | 58 | 92 | 230.6 | 185.14 |  |  | -0.00134 |  |  | 0.04435 |  | 1 | CAPACITY | WALDORF
200303 | X4-035_G1 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | -0.00135 |  |  | 0.04435 |  | 1 | CAPACITY | X4-035
200304 | X4-035_G2 | 18 | 233 | 58 | 0 | 225 | 180.64 |  |  | -0.00135 |  |  | 0 |  | 1 | CAPACITY | X4-035
917371 | Z2-060 | 230 | 233 | 58 | 0 | 116 | 93.13 |  |  | -0.00135 |  |  | 0.04435 |  | 1 | CAPACITY | X3-087
224044 | CHALKCT6 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
224043 | CHALKCT5 | 13.8 | 233 | 57 | 65 | 109 | 87.51 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
226917 | AC2-101 E | 0.55 | 238 | 75 | 0 | 20.15 | 0 |  |  | -0.00134 |  |  | 0 |  | 1 | NEWENERGY | AC2-101
920642 | AA2-170 E | 230 | 233 | 58 | 0 | 19.1 | 0 |  |  | -0.00135 |  |  | 0.04435 |  | 1 | NEW | AA2-170
920641 | AA2-170 C | 230 | 233 | 58 | 0 | 92 | 73.86 |  |  | -0.00135 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-170
226913 | AC2-120 E | 69 | 238 | 75 | 0 | 17.05 | 0 |  |  | -0.00134 |  |  | 0 |  | 1 | NEWENERGY | AC2-120
224042 | CHALKCT4 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
224041 | CHALKCT3 | 13.8 | 233 | 57 | 33 | 86 | 69.05 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
227024 | SMECOCT | 13.8 | 238 | 57 | 30 | 80.2 | 64.39 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
224101 | PANDASC1 | 13.8 | 233 | 58 | 38.4 | 80 | 64.23 |  |  | -0.00135 |  |  | 0 |  | 1 | CAPACITY | PANDA
224051 | MORGTCT4 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
224053 | MORGTCT6 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
224052 | MORGTCT5 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
224050 | MORGTCT3 | 13.8 | 233 | 57 | 20 | 54 | 43.35 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
224099 | PANDACT1 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | -0.00135 |  |  | 0.04435 |  | 1 | CAPACITY | PANDA
224100 | PANDACT2 | 13.8 | 233 | 58 | 65.3 | 75 | 65.33 |  |  | -0.00135 |  |  | 0 |  | 1 | CAPACITY | PANDA
224040 | CHALKCT2 | 13.8 | 233 | 56 | 5 | 24.4 | 19.59 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
224039 | CHALKCT1 | 4.33 | 233 | 55 | 5 | 18 | 14.45 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
224049 | MORG CT2 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
224048 | MORG CT1 | 13.8 | 233 | 55 | 7 | 16 | 12.85 |  |  | -0.00134 |  |  | 0.08446 |  | 1 | CAPACITY
226915 | AC2-101 C | 0.55 | 238 | 75 | 0 | 12.35 | 9.92 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY | AC2-101
226912 | AC2-120 C | 69 | 238 | 75 | 0 | 10.45 | 8.39 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY | AC2-120
925012 | AB2-157 E | 69 | 233 | 75 | 0 | 1.7 | 0 |  |  | -0.00134 |  |  | 0 |  | 1 | NEWENERGY | AB2-157
226897 | H-020 | 230 | 233 | 64 | 0 | 4.6 | 3.69 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY
226891 | S-002 | 230 | 233 | 64 | 0 | 2.2 | 1.76 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY
925011 | AB2-157 C | 69 | 233 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00134 |  |  | 0 |  | 1 | CAPACITY | AB2-157
224244 | NIH23MW | 34.5 | 233 | 20 | 0 | 23.5 | 0 |  |  | -0.00135 |  |  | 0.10478 |  | 1 | ENERGY
224055 | DICKHCT2 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | -0.00136 |  |  | 0.08446 |  | 1 | CAPACITY
224054 | DICKHCT1 | 13.8 | 233 | 57 | 39 | 147 | 118.02 |  |  | -0.00136 |  |  | 0.08446 |  | 1 | CAPACITY
224056 | MCTRSH1G | 13.8 | 233 | 1 | 22 | 52 | 41.75 |  |  | -0.00136 |  |  | 0.10478 |  | 1 | CAPACITY
224034 | DICK CT1 | 13.8 | 233 | 20 | 1 | 18 | 14.45 |  |  | -0.00136 |  |  | 0.08446 |  | 1 | CAPACITY
315213 | 1X4-039 ST | 19 | 345 | 58 | 0 | 306 | 245.67 |  |  | -0.00138 |  |  | 0 |  | 1 | CAPACITY | X4-039
924772 | AB2-129 E OP | 230 | 201 | 75 | 0 | 49.6 | 0 |  |  | -0.00137 |  |  | 0 |  | 1 | NEWENERGY | AB2-129
315010 | 1POSSM6S | 18 | 345 | 58 | 116 | 251 | 201.52 |  |  | -0.00138 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
315212 | 1X4-039 GT2 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.00138 |  |  | 0 |  | 1 | CAPACITY | X4-039
315211 | 1X4-039 GT1 | 18 | 345 | 58 | 0 | 222 | 178.23 |  |  | -0.00138 |  |  | 0.04435 |  | 1 | CAPACITY | X4-039
315008 | 1POSSM6A | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00138 |  |  | 0.04435 |  | 1 | CAPACITY | POSSUM POINT
315009 | 1POSSM6B | 18 | 345 | 58 | 87 | 161 | 129.26 |  |  | -0.00138 |  |  | 0 |  | 1 | CAPACITY | POSSUM POINT
924771 | AB2-129 C OP | 230 | 201 | 75 | 0 | 30.4 | 0 |  |  | -0.00137 |  |  | 0 |  | 1 | NEW | AB2-129
315001 | 1OMF A | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00138 |  |  | 0.10478 |  | 1 | CAPACITY
315002 | 1OMF B | 13.8 | 345 | 2 | 5 | 39.45 | 31.67 |  |  | -0.00138 |  |  | 0.10478 |  | 1 | CAPACITY
315018 | 1POSSMC2 | 13.2 | 345 | 20 | 9 | 35.8 | 28.74 |  |  | -0.00138 |  |  | 0.10478 |  | 1 | CAPACITY
315015 | 1POSSMC1 | 13.2 | 345 | 20 | 9 | 35.7 | 28.66 |  |  | -0.00138 |  |  | 0.10478 |  | 1 | CAPACITY
314088 | 6VANDORN | 230 | 345 | 2 | 7 | 21 | 16.86 |  |  | -0.00138 |  |  | 0 |  | 1 | CAPACITY
219250 | CENTRALDIV E | 13.2 | 231 | 75 | 0 | 0.47 | 0 |  |  | -0.00138 |  |  | 0 |  | 1 | NEWENERGY | W2-036
313821 | 6PACIFIC | 230 | 345 | 75 | 0 | 0.09 | 0 |  |  | -0.00138 |  |  | 0 |  | 1 | NEWENERGY
219249 | CENTRALDIV C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00138 |  |  | 0 |  | 1 | CAPACITY | W2-036
315030 | 1M RUN C | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00139 |  |  | 0.08446 |  | 1 | CAPACITY
315028 | 1M RUN A | 18 | 345 | 57 | 40 | 161.8 | 129.9 |  |  | -0.00139 |  |  | 0.08446 |  | 1 | CAPACITY
315029 | 1M RUN B | 18 | 345 | 57 | 40 | 160.5 | 128.86 |  |  | -0.00139 |  |  | 0.08446 |  | 1 | CAPACITY
315023 | 1REMNGT3 | 18 | 345 | 30 | 40 | 152.3 | 122.28 |  |  | -0.00139 |  |  | 0.10478 |  | 1 | CAPACITY
315022 | 1REMNGT2 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00139 |  |  | 0.10478 |  | 1 | CAPACITY
315024 | 1REMNGT4 | 18 | 345 | 30 | 40 | 151.7 | 121.79 |  |  | -0.00139 |  |  | 0.10478 |  | 1 | CAPACITY
315021 | 1REMNGT1 | 18 | 345 | 30 | 40 | 149.7 | 120.19 |  |  | -0.00139 |  |  | 0.10478 |  | 1 | CAPACITY
923203 | AB1-124 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
923892 | AB2-029 E | 230 | 345 | 75 | 0 | 12.2 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY | AB2-029
235002 | AC1-039 C | 34.5 | 201 | 75 | 0 | 10.4 | 0 |  |  | -0.00138 |  |  | 0 |  | 1 | NEW | AC1-039
925642 | AC1-039 E | 34.5 | 201 | 75 | 0 | 9.6 | 0 |  |  | -0.00138 |  |  | 0 |  | 1 | NEWENERGY | AC1-039
923213 | AB1-125 E OP | 34.5 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
901952 | W1-116E | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.00138 |  |  | 0 |  | 1 | NEWENERGY | W1-116
923202 | AB1-124 C | 34.5 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY | AB1-124
932522 | AC2-072 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00138 |  |  | 0 |  | 1 | NEWENERGY | AC2-072
930522 | AB1-096 E | 34.5 | 201 | 75 | 0 | 6.1 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY | AB1-096
923212 | AB1-125 C OP | 34.5 | 201 | 75 | 0 | 5.7 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY | AB1-125
918902 | AA1-109 E | 34.5 | 201 | 75 | 0 | 4.5 | 0 |  |  | -0.00138 |  |  | 0 |  | 1 | NEWENERGY | AA1-109
932521 | AC2-072 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00138 |  |  | 0 |  | 1 | CAPACITY | AC2-072
314078 | 3REMNGTN | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | CAPACITY | AB2-029
237778 | 01MSM_W1-116 | 34.5 | 201 | 75 | 0 | 5.32 | 4.27 |  |  | -0.00138 |  |  | 0 |  | 1 | CAPACITY | W1-116
237798 | 01AA1-109 C | 34.5 | 201 | 75 | 0 | 4.5 | 3.61 |  |  | -0.00138 |  |  | 0 |  | 1 | CAPACITY | AA1-109
314142 | 6STAFORD | 230 | 345 | 75 | 0 | 0.68 | 0 |  |  | -0.00138 |  |  | 0 |  | 1 | NEWENERGY
930521 | AB1-096 C | 34.5 | 201 | 75 | 0 | 3.1 | 2.49 |  |  | -0.00139 |  |  | 0 |  | 1 | CAPACITY | AB1-096
314134 | 6CRANES | 230 | 345 | 64 | 0 | 2 | 1.61 |  |  | -0.00139 |  |  | 0 |  | 1 | CAPACITY
315226 | 1N ANNA2 | 22 | 345 | 40 | 185 | 948.9 | 761.83 |  |  | -0.00139 |  |  | 0.01494 |  | 1 | CAPACITY
315225 | 1N ANNA1 | 22 | 345 | 40 | 185 | 948.5 | 761.51 |  |  | -0.00139 |  |  | 0.01494 |  | 1 | CAPACITY
926740 | AC1-158 E2 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 2
926739 | AC1-158 E1 | 0.44 | 345 | 75 | 0 | 76.25 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY | AC1-158 1
315033 | 1BIRCHWDA | 18 | 345 | 13 | 85 | 238 | 191.08 |  |  | -0.00139 |  |  | 0.10478 |  | 1 | CAPACITY
926738 | AC1-158 C2 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.00139 |  |  | 0 |  | 1 | CAPACITY | AC1-158 2
926737 | AC1-158 C1 | 0.44 | 345 | 75 | 0 | 173.75 | 139.5 |  |  | -0.00139 |  |  | 0 |  | 1 | CAPACITY | AC1-158 1
315050 | 1FOURRIVERG | 18 | 345 | 57 | 20 | 170 | 136.49 |  |  | -0.0014 |  |  | 0.08446 |  | 1 | CAPACITY
315052 | 1AA1-145 CT2 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.0014 |  |  | 0.08446 |  | 1 | CAPACITY
315051 | 1AA1-145 CT1 | 18 | 345 | 57 | 0 | 170 | 136.49 |  |  | -0.0014 |  |  | 0.08446 |  | 1 | CAPACITY
315038 | 1LDYSMT2 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00139 |  |  | 0.08446 |  | 1 | CAPACITY
315037 | 1LDYSMT1 | 18 | 345 | 57 | 40 | 166 | 133.27 |  |  | -0.00139 |  |  | 0.08446 |  | 1 | CAPACITY
315041 | 1LDYSMT5 | 18 | 345 | 57 | 40 | 160.6 | 128.94 |  |  | -0.00139 |  |  | 0.08446 |  | 1 | CAPACITY
315040 | 1LDYSMT4 | 18 | 345 | 57 | 40 | 160.1 | 128.54 |  |  | -0.00139 |  |  | 0.08446 |  | 1 | CAPACITY
315039 | 1LDYSMT3 | 18 | 345 | 57 | 40 | 159.8 | 128.3 |  |  | -0.00139 |  |  | 0.08446 |  | 1 | CAPACITY
315176 | 1LOISA E | 18 | 345 | 57 | 48 | 158 | 126.85 |  |  | -0.0014 |  |  | 0.08446 |  | 1 | CAPACITY
925022 | AB2-158 E | 230 | 345 | 75 | 0 | 27.2 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AB2-158
208907 | HOLT 697 | 13.2 | 229 | 60 | 0 | 133.2 | 106.94 |  |  | -0.00139 |  |  | 0.07484 |  | 1 | CAPACITY
315048 | 1FOUR RIVERF | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315045 | 1FOUR RIVERC | 13.8 | 345 | 58 | 70 | 132 | 105.98 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315047 | 1FOUR RIVERE | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | Doswell 6
315043 | 1FOUR RIVERA | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.0014 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 5
315044 | 1FOUR RIVERB | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | Doswell 5
315046 | 1FOUR RIVERD | 13.8 | 345 | 58 | 30 | 108 | 86.71 |  |  | -0.0014 |  |  | 0.04435 |  | 1 | CAPACITY | Doswell 6
316149 | AD1-046 E | 230 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AD1-044
315174 | 1LOISA C | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.0014 |  |  | 0.08446 |  | 1 | CAPACITY
315173 | 1LOISA B | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.0014 |  |  | 0.08446 |  | 1 | CAPACITY
315175 | 1LOISA D | 13.8 | 345 | 57 | 23 | 77.5 | 62.22 |  |  | -0.0014 |  |  | 0.08446 |  | 1 | CAPACITY
315172 | 1LOISA A | 13.8 | 345 | 57 | 23 | 77.1 | 61.9 |  |  | -0.0014 |  |  | 0.08446 |  | 1 | CAPACITY
905554 | W4-102 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | W4-102
925021 | AB2-158 C | 230 | 345 | 75 | 0 | 61 | 48.97 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AB2-158
208904 | HOLT 696 | 13.2 | 229 | 60 | 23 | 58.4 | 46.89 |  |  | -0.00139 |  |  | 0.07484 |  | 1 | CAPACITY
923193 | AB1-123 E OP | 34.5 | 201 | 75 | 0 | 11.4 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
208903 | HOLT 695 | 13.2 | 229 | 60 | 26 | 53.2 | 42.71 |  |  | -0.00139 |  |  | 0.07484 |  | 1 | CAPACITY
235025 | AB2-097 E | 34.5 | 201 | 75 | 0 | 10 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AB2-097
315177 | 1S ANNAG1 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.0014 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 1
315179 | 1S ANNAG2 | 13.8 | 345 | 58 | 62.6 | 72 | 62.72 |  |  | -0.0014 |  |  | 0.04435 |  | 1 | CAPACITY | South Anna 2
237799 | 01AA2-159 C | 34.5 | 201 | 75 | 0 | 8.7 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
920562 | AA2-159 E | 34.5 | 201 | 75 | 0 | 7.3 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AA2-159
923192 | AB1-123 C OP | 34.5 | 201 | 75 | 0 | 7 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AB1-123
926472 | AC1-118 E | 230 | 345 | 75 | 0 | 6.8 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AC1-118
938962 | AE1-124 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AE1-124
933252 | AC2-136 E | 138 | 201 | 75 | 0 | 6.3 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY | AC2-136
316148 | AD1-046 C | 230 | 345 | 75 | 0 | 30.7 | 24.65 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AD1-044
316078 | AC2-138 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AC2-138
923872 | AB2-027 E | 34.5 | 201 | 75 | 0 | 5.5 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY | AB2-027
315034 | 1NORNECKC1 | 13.2 | 345 | 20 | 0 | 24.9 | 19.99 |  |  | -0.0014 |  |  | 0.10478 |  | 1 | CAPACITY
315178 | 1S ANNAS1 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | South Anna 1
315180 | 1S ANNAS2 | 13.8 | 345 | 58 | 32.2 | 37 | 32.23 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | South Anna 2
315035 | 1NORNECKC2 | 13.2 | 345 | 20 | 0 | 24 | 19.27 |  |  | -0.0014 |  |  | 0.10478 |  | 1 | CAPACITY
918732 | AA1-092 E | 34.5 | 201 | 75 | 0 | 4 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AA1-092
918762 | AA1-095 E | 34.5 | 201 | 75 | 0 | 3.33 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AA1-095
235006 | AB2-027 C | 34.5 | 201 | 75 | 0 | 3.3 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEW | AB2-027
919535 | V4-027 E | 0 | 229 | 75 | 0 | 3.1 | 0 |  |  | -0.00139 |  |  | 0 |  | 1 | NEWENERGY | V4-027
938961 | AE1-124 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AE1-124
314766 | 6LOUISA | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY
314190 | 6WESTMOR | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AC1-118
314172 | 6DUNNSVL | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY
314131 | 6ARNOLDS | 230 | 345 | 64 | 0 | 8.7 | 6.98 |  |  | -0.00139 |  |  | 0 |  | 1 | CAPACITY
235004 | AA1-092 C | 34.5 | 201 | 75 | 0 | 8 | 6.42 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AA1-092
237779 | 01MDS_W4-102 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | W4-102
316077 | AC2-138 C | 115 | 345 | 75 | 0 | 6.3 | 5.06 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AC2-138
933251 | AC2-136 C | 138 | 201 | 75 | 0 | 5.5 | 4.41 |  |  | -0.00139 |  |  | 0 |  | 1 | CAPACITY | AC2-136
208923 | BUSO V4-027 | 12.5 | 229 | 75 | 0 | 4.9 | 3.93 |  |  | -0.00139 |  |  | 0 |  | 1 | CAPACITY | V4-027
208474 | KINZ 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00139 |  |  | 0 |  | 1 | CAPACITY
235020 | AA1-095 C | 34.5 | 201 | 75 | 0 | 2.9 | 2.33 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AA1-095
237772 | 01MILVL HY | 34.5 | 201 | 60 | 0 | 2.6 | 2.09 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY
237768 | 01DAM 4 HY | 34.5 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00139 |  |  | 0 |  | 1 | CAPACITY
237769 | 01DAM 5 HY | 34.5 | 201 | 60 | 0 | 1.1 | 0.88 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY
316136 | AC1-107 G3 | 23 | 345 | 58 | 0 | 533.4 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEW | AC1-107
316135 | AC1-107 G2 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEW | AC1-107
316134 | AC1-107 G1 | 23 | 345 | 58 | 0 | 533.3 | 0 |  |  | -0.0014 |  |  | 0.04435 |  | 1 | NEW | AC1-107
916042 | Z1-036 E | 230 | 345 | 74 | 0 | 261.3 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | Z1-036
901082 | W1-029 E | 230 | 345 | 74 | 0 | 261 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | W1-029
315116 | 1SURRY 1 | 22 | 345 | 40 | 189 | 844.6 | 678.09 |  |  | -0.00141 |  |  | 0.01494 |  | 1 | CAPACITY
315233 | 1SURRY 2 | 22 | 345 | 40 | 189 | 843.5 | 677.21 |  |  | -0.00141 |  |  | 0.01494 |  | 1 | CAPACITY
315092 | 1YORKTN3 | 25 | 345 | 26 | 190 | 788.9 | 633.38 |  |  | -0.0014 |  |  | 0.10478 |  | 1 | CAPACITY
315273 | 1WARREN S1 | 19 | 345 | 58 | 0 | 526.7 | 422.86 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
926785 | AC1-164 E | 0.44 | 345 | 75 | 0 | 99.2 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AC1-164
316114 | AB2-068 ST | 22 | 345 | 58 | 0 | 492 | 395.01 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AB2-068
924814 | AB2-134 E | 0.6 | 345 | 75 | 0 | 70.6 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-134
316113 | AB2-068 CT2 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AB2-068
316112 | AB2-068 CT1 | 20 | 345 | 58 | 0 | 284 | 228.01 |  |  | -0.0014 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-068
315271 | 1WARREN G2 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
315270 | 1WARREN G1 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.0014 |  |  | 0.04435 |  | 1 | CAPACITY | WARREN COUNTY CC
315272 | 1WARREN G3 | 21 | 345 | 58 | 173 | 281.1 | 225.68 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | WARREN COUNTY CC
316109 | AB2-160 E | 0.55 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-160
925332 | AB2-190 E | 230 | 345 | 75 | 0 | 48 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AB2-190
926784 | AC1-164 C | 0.44 | 345 | 75 | 0 | 220.8 | 177.27 |  |  | -0.0014 |  |  | 0 |  | 1 | NEW | AC1-164
315086 | 1SPRUNCD | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.0014 |  |  | 0.10478 |  | 1 | NEW
315085 | 1SPRUNCC | 13.8 | 345 | 11 | 16 | 43 | 0 |  |  | -0.0014 |  |  | 0.10478 |  | 1 | NEW
315073 | 1STONECA | 13.2 | 345 | 1 | 0 | 38.4 | 0 |  |  | -0.0014 |  |  | 0.10478 |  | 1 | ENERGY
314189 | 6PAPERMILL | 230 | 345 | 1 | 12 | 37 | 0 |  |  | -0.0014 |  |  | 0.10478 |  | 1 | ENERGY
919152 | AA1-139 E | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AA1-139
925865 | AC1-065 E | 0.39 | 345 | 75 | 0 | 31 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AC1-065
316084 | AB2-161 E | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-161
315061 | 1CHESTG7 | 13.8 | 345 | 58 | 68 | 130.7 | 104.93 |  |  | -0.0014 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 7
315063 | 1CHESTG8 | 13.8 | 345 | 58 | 63 | 128.6 | 103.25 |  |  | -0.0014 |  |  | 0.04435 |  | 1 | CAPACITY | Chesterfield 8
315080 | 1HOPHCF4 | 13.8 | 345 | 58 | 57 | 126 | 101.16 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
314525 | 6KINGFORK | 230 | 345 | 75 | 0 | 24.3 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314550 | 6HICKORY | 230 | 345 | 75 | 0 | 22.93 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
316132 | AB2-190 C | 230 | 345 | 75 | 0 | 112 | 89.92 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AB2-190
315110 | 1ELIZAR3 | 13.8 | 345 | 30 | 26 | 110.8 | 88.96 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
315108 | 1ELIZAR1 | 13.8 | 345 | 30 | 26 | 109.4 | 87.83 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
315109 | 1ELIZAR2 | 13.8 | 345 | 30 | 26 | 107.5 | 86.31 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
315120 | 1GRAVEL4 | 13.8 | 345 | 29 | 40 | 86.9 | 69.77 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
315122 | 1GRAVEL6 | 13.8 | 345 | 29 | 40 | 86.8 | 69.69 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
315070 | 1DARBY 4 | 13.8 | 345 | 29 | 40 | 86 | 69.05 |  |  | -0.0014 |  |  | 0.10478 |  | 1 | CAPACITY
315069 | 1DARBY 3 | 13.8 | 345 | 29 | 40 | 85.9 | 68.97 |  |  | -0.0014 |  |  | 0.10478 |  | 1 | CAPACITY
315119 | 1GRAVEL3 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
315121 | 1GRAVEL5 | 13.8 | 345 | 29 | 40 | 85.8 | 68.89 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
315068 | 1DARBY 2 | 13.8 | 345 | 29 | 40 | 85.6 | 68.72 |  |  | -0.0014 |  |  | 0.10478 |  | 1 | CAPACITY
315067 | 1DARBY 1 | 13.8 | 345 | 29 | 40 | 85.5 | 68.64 |  |  | -0.0014 |  |  | 0.10478 |  | 1 | CAPACITY
315078 | 1HOPHCF2 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315079 | 1HOPHCF3 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | HOPEWELL HCF
315077 | 1HOPHCF1 | 13.8 | 345 | 58 | 37 | 83 | 66.64 |  |  | -0.0014 |  |  | 0.04435 |  | 1 | CAPACITY | HOPEWELL HCF
315603 | 6AA1-139SOLA | 230 | 345 | 75 | 0 | 78.7 | 63.18 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AA1-139
316033 | AB2-134 C | 0.6 | 345 | 75 | 0 | 71.8 | 57.65 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB2-134
315064 | 1CHESTS8 | 13.8 | 345 | 58 | 9 | 66.2 | 53.15 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 8
913392 | Y1-086 E | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | Y1-086
314466 | 6FENTRES | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314632 | 6AYDLETOLD | 230 | 345 | 75 | 0 | 12.4 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
313717 | 6SLIGO L2192 | 230 | 345 | 75 | 0 | 12.34 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314331 | 6POE | 230 | 345 | 75 | 0 | 12.27 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
315062 | 1CHESTS7 | 13.8 | 345 | 58 | 32 | 60 | 48.17 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | Chesterfield 7
916192 | Z1-068 E | 230 | 345 | 74 | 0 | 10.5 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | Z1-068
315076 | 1HOPPOLC | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.0014 |  |  | 0.10478 |  | 1 | CAPACITY
934363 | AD1-060 E | 0.41 | 201 | 75 | 0 | 9.3 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AD1-060
925863 | AC1-065 C | 0.39 | 345 | 75 | 0 | 41.8 | 33.56 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AC1-065
939312 | AE1-162 E | 230 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AE1-162
935212 | AD1-156 E | 230 | 345 | 75 | 0 | 7.92 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AD1-156
315605 | 6W1-029WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | W1-029
315611 | 6Z1-036WIND | 230 | 345 | 74 | 0 | 39 | 31.31 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | Z1-036
316076 | AC2-137 E | 230 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AC2-137
926662 | AC1-147 E | 115 | 345 | 75 | 0 | 7.4 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AC1-147
923832 | AB2-022 E | 230 | 345 | 75 | 0 | 7 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-022
316145 | AE1-027 E | 230 | 345 | 75 | 0 | 6.9 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AE1-027
316157 | AD2-030 E | 115 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AD2-030
938552 | AE1-074 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AE1-074
933732 | AC2-196 E | 230 | 345 | 75 | 0 | 6.66 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AC2-196
925522 | AC1-027 E | 115 | 345 | 75 | 0 | 6.4 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AC1-027
923842 | AB2-024 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AB2-024
923862 | AB2-026 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-026
933572 | AC2-174 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AC2-174
917162 | Z2-030 E | 138 | 201 | 75 | 0 | 6.2 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | Z2-030
923852 | AB2-025 E | 230 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-025
926412 | AC1-112 E | 230 | 345 | 75 | 0 | 6.1 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AC1-112
930122 | AB1-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AB1-027
934392 | AD1-063 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AD1-063
917122 | Z2-027 E | 230 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | Z2-027
316108 | AB2-160 C | 0.55 | 345 | 75 | 0 | 30.4 | 24.41 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB2-160
938562 | AE1-075 E | 230 | 345 | 75 | 0 | 5.9 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AE1-075
315117 | 1GRAVELC | 13.8 | 345 | 20 | 0 | 29.6 | 23.76 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
935112 | AD1-144 E | 230 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AD1-144
316158 | AD2-164 | 230 | 345 | 57 | 0 | 26.7 | 21.44 |  |  | -0.00141 |  |  | 0.08446 |  | 1 | CAPACITY
316151 | AD2-215 E | 230 | 345 | 75 | 0 | 5.2 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AD2-215
316147 | AE1-028 E | 230 | 345 | 75 | 0 | 4.4 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AE1-028
314333 | 6POWHATN | 230 | 345 | 75 | 0 | 3.97 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB2-026
314184 | 3SHACKLE | 115 | 345 | 65 | 0 | 20 | 16.06 |  |  | -0.0014 |  |  | 0.12623 |  | 1 | CAPACITY
932502 | AC2-070 E | 230 | 345 | 75 | 0 | 3.8 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY | AC2-070
933571 | AC2-174 C | 138 | 201 | 75 | 0 | 3.8 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEW | AC2-174
316083 | AB2-161 C | 0.55 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB2-161
314651 | 6WINFALL | 230 | 345 | 75 | 0 | 3.35 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314645 | 6SLIGO L269 | 230 | 345 | 75 | 0 | 3.22 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314243 | 3PROV 92 | 115 | 345 | 65 | 0 | 16.3 | 13.09 |  |  | -0.0014 |  |  | 0.12623 |  | 1 | CAPACITY
315261 | 1GOSPORTB | 13.8 | 345 | 2 | 0 | 15.2 | 12.2 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
314643 | 3O INLET | 115 | 345 | 65 | 0 | 15 | 12.04 |  |  | -0.00141 |  |  | 0.12623 |  | 1 | CAPACITY
237577 | 01ROUTE 16 | 34.5 | 201 | 65 | 0 | 15 | 12.04 |  |  | -0.0014 |  |  | 0.12623 |  | 1 | CAPACITY
314309 | 6IRON208 | 230 | 345 | 65 | 0 | 14.9 | 11.96 |  |  | -0.0014 |  |  | 0.12623 |  | 1 | CAPACITY
315098 | 1CHESPKA | 13.8 | 345 | 20 | 0 | 14.9 | 11.96 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
938551 | AE1-074 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AE1-074
316156 | AD2-030 C | 115 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AD2-030
316144 | AE1-027 C | 230 | 345 | 75 | 0 | 13.1 | 10.52 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AE1-027
313526 | AB2-022 C | 230 | 345 | 75 | 0 | 13 | 10.44 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB2-022
315262 | 1GOSPORTC | 13.8 | 345 | 2 | 0 | 12.9 | 10.36 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
926661 | AC1-147 C | 115 | 345 | 75 | 0 | 12.6 | 10.12 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AC1-147
316258 | AE1-162 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AE1-162
938561 | AE1-075 C | 230 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AE1-075
315260 | 1GOSPORTA | 13.8 | 345 | 2 | 0 | 11.9 | 9.55 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
935211 | AD1-156 C | 230 | 345 | 75 | 0 | 11.82 | 9.49 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AD1-156
316075 | AC2-137 C | 230 | 345 | 75 | 0 | 11.4 | 9.15 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AC2-137
314507 | 3THOMPSN | 115 | 345 | 65 | 0 | 11.28 | 9.05 |  |  | -0.00141 |  |  | 0.12623 |  | 1 | CAPACITY
314250 | 6ROCKVILLE | 230 | 345 | 65 | 0 | 11 | 8.83 |  |  | -0.0014 |  |  | 0.12623 |  | 1 | CAPACITY
314375 | 6CORRCTN | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AB2-024
314533 | 6SMITFLD | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314435 | 6SAPONY | 230 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB2-025
314187 | 3WAN 176 | 115 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY
314314 | 3LOCKS | 115 | 345 | 65 | 0 | 10 | 8.03 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY
933731 | AC2-196 C | 230 | 345 | 75 | 0 | 10 | 8.03 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AC2-196
316150 | AD2-215 C | 230 | 345 | 76 | 0 | 9.8 | 7.87 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AD2-215
935111 | AD1-144 C | 230 | 345 | 75 | 0 | 9.7 | 7.79 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AD1-144
314491 | 3PENDLTN | 115 | 345 | 75 | 0 | 1.89 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AC1-027
314241 | 6OLDCHRC | 230 | 345 | 75 | 0 | 1.82 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AB1-027
932501 | AC2-070 C | 230 | 345 | 75 | 0 | 9.2 | 7.39 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AC2-070
934391 | AD1-063 C | 230 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AD1-063
314176 | 6HARMONY | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY
316146 | AE1-028 C | 230 | 345 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AE1-028
942852 | AE2-304 E | 230 | 345 | 75 | 0 | 1.4 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AE2-304
314236 | 6NRTHEST | 230 | 345 | 64 | 0 | 6.2 | 4.98 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY
934362 | AD1-060 C | 0.41 | 201 | 75 | 0 | 5.7 | 4.58 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY | AD1-060
314648 | 6SUNBURY | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
235447 | 01WINZ1-113 | 138 | 201 | 55 | 0 | 4.9 | 3.93 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY
314421 | 6WINCHST | 230 | 345 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY
314229 | 6MT RD221 | 230 | 345 | 64 | 0 | 4 | 3.21 |  |  | -0.0014 |  |  | 0 |  | 1 | CAPACITY
235464 | 01DTGZ2-030 | 138 | 201 | 75 | 0 | 3.8 | 3.05 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | Z2-030
942851 | AE2-304 C | 230 | 345 | 75 | 0 | 3.3 | 2.65 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AE2-304
314734 | 6CASHSCORNER | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY
314638 | 6ELIZ CT | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | Y1-086
314662 | 6S HERTFORD | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
237315 | 01FLF_U1-044 | 138 | 201 | 54 | 0 | 2 | 1.61 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY
314639 | 6TANGLEW | 230 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | Z2-027
314177 | 3HAYES89 | 115 | 345 | 75 | 0 | 0.31 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY
314295 | 6BIRDNECK | 230 | 345 | 74 | 0 | 1.5 | 1.2 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | Z1-068
314294 | 6ENON | 230 | 345 | 75 | 0 | 0.23 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY
235033 | 01WHY_Z2-039 | 138 | 201 | 60 | 0 | 0.7 | 0.56 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY
313812 | 6ROCKLANDING | 230 | 345 | 75 | 0 | 0.11 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314453 | 6CHRHLND | 230 | 345 | 75 | 0 | 0.08 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
313828 | 3WHITEMARSH | 115 | 345 | 75 | 0 | 0.05 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY
314640 | 6KITTY HAWK | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314487 | 3MCLAUGH | 115 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314222 | 6HANOVER | 230 | 345 | 75 | 0 | 0.01 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY
314213 | 3CARVER | 115 | 345 | 75 | 0 | 0 | 0 |  |  | -0.0014 |  |  | 0 |  | 1 | NEWENERGY
315244 | 1Z1-086 ST | 24 | 345 | 58 | 314.5 | 598 | 480.11 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315105 | 1BRUNSWICKS1 | 19 | 345 | 58 | 69.2 | 563 | 452.01 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315153 | 1CLOVER1 | 24 | 345 | 15 | 135 | 441.5 | 354.46 |  |  | -0.00142 |  |  | 0.10478 |  | 1 | CAPACITY
315154 | 1CLOVER2 | 24 | 345 | 15 | 135 | 437.1 | 350.93 |  |  | -0.00142 |  |  | 0.10478 |  | 1 | CAPACITY
923262 | AB1-132 C OP | 230 | 345 | 75 | 0 | 84 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
315219 | 1CUNINGD | 22 | 345 | 58 | 60 | 401.5 | 322.35 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315242 | 1Z1-086 GT2 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315243 | 1Z1-086 GT3 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | Z1-086
315241 | 1Z1-086 GT1 | 20 | 345 | 58 | 182.5 | 344 | 276.18 |  |  | -0.00141 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-086
920042 | AA2-088 E OP | 115 | 345 | 75 | 0 | 62 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AA2-088
315103 | 1BRUNSWICKG2 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315102 | 1BRUNSWICKG1 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00141 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNSWICK COUNTY
315104 | 1BRUNSWICKG3 | 21 | 345 | 58 | 34.6 | 271 | 217.57 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | BRUNSWICK COUNTY
316103 | AB2-015 C | 0.6 | 345 | 75 | 0 | 50 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEW | AB2-015
917512 | Z2-088 E OP1 | 230 | 345 | 75 | 0 | 49.6 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | Z2-088
315193 | 1BEARGRDN S1 | 22 | 345 | 58 | 30 | 247 | 198.31 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
923991 | AB2-040 C O1 | 115 | 345 | 75 | 0 | 44 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEW | AB2-040
316104 | AB2-015 E | 0.6 | 345 | 75 | 0 | 41 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-015
316088 | AB2-174 E | 0.35 | 345 | 75 | 0 | 38 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-174
315191 | 1BEARGRDN G1 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00141 |  |  | 0.04435 |  | 1 | CAPACITY | BEAR GARDEN
315192 | 1BEARGRDN G2 | 18 | 345 | 58 | 30 | 191 | 153.35 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | BEAR GARDEN
923992 | AB2-040 E O1 | 115 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-040
923263 | AB1-132 E OP | 230 | 345 | 75 | 0 | 36 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB1-132
315217 | 1CUNINGB | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315218 | 1CUNINGC | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | FLUVANNA
315216 | 1CUNINGA | 18 | 345 | 58 | 30 | 179.5 | 144.11 |  |  | -0.00141 |  |  | 0.04435 |  | 1 | CAPACITY | FLUVANNA
314539 | 3UNCAMP | 115 | 345 | 56 | 0 | 35 | 0 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | ENERGY
925122 | AB2-169 E | 115 | 345 | 75 | 0 | 35 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AB2-169
924022 | AB2-043 E O1 | 0.55 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AB2-043
924162 | AB2-060 E OP | 115 | 345 | 75 | 0 | 25.6 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AB2-060
920692 | AA2-178 E | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AA2-178
918512 | AA1-065 E OP | 0.69 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AA1-065
918492 | AA1-063AE OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AA1-063A
208916 | SAHA8910 | 13.8 | 229 | 61 | -3 | 114.5 | 91.93 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
919692 | AA2-053 E OP | 115 | 345 | 75 | 0 | 22.5 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AA2-053
315139 | 1GASTONA | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.00141 |  |  | 0.07484 |  | 1 | CAPACITY
315141 | 1GASTONB | 14.4 | 345 | 61 | 10 | 110 | 88.31 |  |  | -0.00141 |  |  | 0.07484 |  | 1 | CAPACITY
919702 | AA2-057 E OP | 115 | 345 | 75 | 0 | 21.1 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AA2-057
925785 | AC1-054 E | 0.38 | 345 | 75 | 0 | 20.5 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AC1-054
237093 | AD1-085_E | 0.6 | 201 | 75 | 0 | 19.99 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AD1-085
316097 | AB2-100 E1 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 1
316099 | AB2-100 E2 | 0.55 | 345 | 75 | 0 | 16.5 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-100 2
315136 | 1ROSEMG1 | 13.8 | 345 | 58 | 30 | 76.6 | 61.5 |  |  | -0.00142 |  |  | 0.04435 |  | 1 | CAPACITY | ROSEMARY
208917 | SAHA1112 | 13.8 | 229 | 61 | -2 | 76.5 | 61.42 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
930822 | AB1-127 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB1-127
930832 | AB1-128 E | 34.5 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB1-128
315614 | AA2-178 C | 0.69 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AA2-178
315606 | 3AA2-053SOLA | 115 | 345 | 75 | 0 | 54.8 | 44 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AA2-053
316131 | AB2-060 C | 115 | 345 | 75 | 0 | 54.4 | 43.67 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AB2-060
315602 | 1HOLLOMANSOL | 0.69 | 345 | 75 | 0 | 53.6 | 43.03 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AA1-065
315115 | 1S HAMPT1 | 13.8 | 345 | 2 | 15 | 53.1 | 42.63 |  |  | -0.00141 |  |  | 0.10478 |  | 1 | CAPACITY
315601 | 1CONETOE2SOL | 0.69 | 345 | 75 | 0 | 53 | 42.55 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | Z2-088
315607 | 3AA1-063SOLA | 115 | 345 | 75 | 0 | 50.9 | 40.87 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AA1-063A
315126 | 1ROARAP2 | 14.4 | 345 | 60 | 10 | 50.3 | 40.38 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
315292 | 1DOMTR78 | 13.8 | 345 | 57 | 0 | 50 | 40.14 |  |  | -0.00141 |  |  | 0.19858 |  | 1 | CAPACITY
314713 | 3PAMPLIN | 115 | 345 | 75 | 0 | 9.73 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
314807 | 3MT JACK | 115 | 345 | 75 | 0 | 9.7 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
315128 | 1ROARAP4 | 14.4 | 345 | 60 | 10 | 48 | 38.54 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
315137 | 1ROSEMS1 | 13.8 | 345 | 58 | 18 | 47.5 | 38.13 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
925612 | AC1-036 E | 115 | 345 | 75 | 0 | 9.3 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AC1-036
316143 | AD1-160 E | 115 | 345 | 75 | 0 | 9.1 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AD1-160
313719 | 3CHESTNUT | 115 | 345 | 75 | 0 | 44.7 | 35.89 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AA2-057
316129 | AC1-054 C | 0.38 | 345 | 75 | 0 | 44.5 | 35.73 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AC1-054
235723 | 01GUILF1 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00142 |  |  | 0.08446 |  | 1 | CAPACITY
235724 | 01GUILF2 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00142 |  |  | 0.08446 |  | 1 | CAPACITY
316087 | AB2-174 C | 0.35 | 345 | 75 | 0 | 42 | 33.72 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB2-174
924312 | AB2-078 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AB2-078
924322 | AB2-079 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AB2-079
924302 | AB2-077 E O1 | 115 | 345 | 75 | 0 | 8 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AB2-077
313506 | AB1-173 C OP | 115 | 345 | 75 | 0 | 40.4 | 32.44 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB1-173
926452 | AC1-116 E | 230 | 345 | 75 | 0 | 7.8 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AC1-116
925121 | AB2-169 C | 115 | 345 | 75 | 0 | 39 | 31.31 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AB2-169
315608 | 3AA2-088SOLA | 115 | 345 | 75 | 0 | 38 | 30.51 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AA2-088
315138 | 1ROSEMG2 | 13.8 | 345 | 58 | 14 | 35.9 | 28.82 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | ROSEMARY
932512 | AC2-071 E | 230 | 345 | 75 | 0 | 6.7 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AC2-071
316098 | AB2-100 C2 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB2-100 2
316096 | AB2-100 C1 | 0.55 | 345 | 75 | 0 | 33.5 | 26.9 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB2-100 1
924032 | AB2-045 E | 230 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-045
923573 | AB1-173 E OP | 115 | 345 | 75 | 0 | 6.3 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB1-173
935222 | AD1-157 E | 115 | 345 | 75 | 0 | 6 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AD1-157
314574 | 6EVERETS | 230 | 345 | 75 | 0 | 5.89 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
316155 | AE1-099 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AE1-099
316153 | AE1-098 E | 115 | 345 | 75 | 0 | 5.3 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AE1-098
932542 | AC2-074 E | 115 | 345 | 75 | 0 | 5.25 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AC2-074
314578 | 3HORNRTN | 115 | 345 | 75 | 0 | 5.15 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
314589 | 3MURPHYS | 115 | 345 | 75 | 0 | 4.66 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | V4-068
918532 | AA1-067 E | 230 | 345 | 75 | 0 | 4.5 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AA1-067
314541 | 3WATKINS | 115 | 345 | 1 | 0 | 4 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | ENERGY
313853 | 3PONTONDP | 115 | 345 | 2 | 0 | 4 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | ENERGY
314579 | 6HORNRTN | 230 | 345 | 75 | 0 | 3.91 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
313527 | AB2-043 C | 0.55 | 345 | 75 | 0 | 18.9 | 15.17 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AB2-043
314429 | 3JTRSVLE | 115 | 345 | 65 | 0 | 16 | 12.85 |  |  | -0.00142 |  |  | 0.12623 |  | 1 | CAPACITY
932511 | AC2-071 C | 230 | 345 | 75 | 0 | 13.3 | 10.68 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AC2-071
314572 | 3EMPORIA | 115 | 345 | 60 | 0 | 2.5 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEW
314266 | 6NORTHAMPTON | 230 | 345 | 75 | 0 | 2.47 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
237092 | AD1-085_C | 0.6 | 201 | 75 | 0 | 12.3 | 9.88 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AD1-085
924311 | AB2-078 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00142 |  |  | 0 |  | 1 | NEW | AB2-078
924301 | AB2-077 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00142 |  |  | 0 |  | 1 | NEW | AB2-077
924321 | AB2-079 C O1 | 115 | 345 | 75 | 0 | 12 | 9.64 |  |  | -0.00142 |  |  | 0 |  | 1 | NEW | AB2-079
314704 | 3LAWRENC | 115 | 345 | 64 | 0 | 11 | 8.83 |  |  | -0.00142 |  |  | 0.12623 |  | 1 | CAPACITY
314603 | 3SCOT NK | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
314617 | 3TUNIS | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314593 | 3PARMELE | 115 | 345 | 75 | 0 | 2.14 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
314677 | 6BUCKING | 230 | 345 | 75 | 0 | 2.12 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB2-045
932541 | AC2-074 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AC2-074
316154 | AE1-099 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AE1-099
316152 | AE1-098 C | 115 | 345 | 75 | 0 | 10.4 | 8.35 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AE1-098
935221 | AD1-157 C | 115 | 345 | 75 | 0 | 9 | 7.23 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AD1-157
900672 | V4-068 E | 115 | 345 | 75 | 0 | 1.77 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | V4-068
925611 | AC1-036 C | 115 | 345 | 75 | 0 | 8.6 | 6.9 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AC1-036
314637 | 6EDENTON | 230 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AA2-059
314568 | 3EARLEYS | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314566 | 3CRESWEL | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
316141 | AB2-099 E | 115 | 345 | 75 | 0 | 1.5 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY | AB2-099
235041 | AB1-128 C | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB1-128
235040 | 01AB1-127 | 34.5 | 201 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB1-127
316142 | AD1-160 C | 115 | 345 | 75 | 0 | 6.6 | 5.3 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AD1-160
314559 | 3CAROLNA | 115 | 345 | 75 | 0 | 1.21 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
314620 | 6CASHIE | 230 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314551 | 3AHOSKIE | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314626 | 3WOODLND | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314596 | 3POPLR C | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
314582 | 3KELFORD | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | Z2-043
926451 | AC1-116 C | 230 | 345 | 75 | 0 | 4.7 | 3.77 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AC1-116
316140 | AB2-099 C | 115 | 345 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY | AB2-099
314594 | 6PLYMOTH | 230 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314604 | 3SEABORD | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
314762 | 3JAMES R | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
235039 | 01LHY_Z2-039 | 138 | 201 | 60 | 0 | 1.4 | 1.12 |  |  | -0.00141 |  |  | 0 |  | 1 | CAPACITY
235035 | 01NHY_Z2-039 | 138 | 201 | 60 | 0 | 1.3 | 1.04 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY
314629 | 3MARTNCO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
314798 | 3MERCK5 | 115 | 345 | 75 | 0 | 0.16 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
235034 | 01SHY_Z2-039 | 138 | 201 | 60 | 0 | 0.8 | 0.64 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY
313826 | 6HYDRAULIC | 230 | 345 | 75 | 0 | 0.04 | 0 |  |  | -0.00141 |  |  | 0 |  | 1 | NEWENERGY
235097 | GREENL_K11_E | 0.69 | 201 | 74 | 0 | 225.8 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | K11
315252 | 1MT STM2 | 22 | 345 | 15 | 265 | 553 | 443.98 |  |  | -0.00143 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM2
315251 | 1MT STM1 | 22 | 345 | 15 | 265 | 548.2 | 440.13 |  |  | -0.00143 |  |  | 0.10478 |  | 1 | CAPACITY | MTSTM1
315253 | 1MT STM3 | 24 | 345 | 15 | 300 | 522.9 | 419.81 |  |  | -0.00143 |  |  | 0.10478 |  | 1 | CAPACITY
315206 | 1BATH 6F | 20.5 | 345 | 62 | 207 | 503.8 | 404.48 |  |  | -0.00142 |  |  | 0.0316 |  | 1 | CAPACITY
315205 | 1BATH 5E | 20.5 | 345 | 62 | 207 | 502.8 | 403.68 |  |  | -0.00142 |  |  | 0.0316 |  | 1 | CAPACITY
315203 | 1BATH 3C | 20.5 | 345 | 62 | 207 | 502.3 | 403.27 |  |  | -0.00142 |  |  | 0.0316 |  | 1 | CAPACITY
315204 | 1BATH 4D | 20.5 | 345 | 62 | 207 | 502.2 | 403.2 |  |  | -0.00142 |  |  | 0.0316 |  | 1 | CAPACITY
315201 | 1BATH 1A | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00142 |  |  | 0.0316 |  | 1 | CAPACITY
315202 | 1BATH 2B | 20.5 | 345 | 62 | 207 | 502 | 403.03 |  |  | -0.00142 |  |  | 0.0316 |  | 1 | CAPACITY
292559 | T-157 E | 34.5 | 345 | 74 | 0 | 82 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | T157
315616 | AA1-038 C | 230 | 345 | 74 | 0 | 76.6 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEW | AA1-038
918232 | AA1-038 E | 230 | 345 | 74 | 0 | 66.7 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AA1-038
314860 | 4E MILL | 138 | 345 | 2 | 0 | 50 | 0 |  |  | -0.00142 |  |  | 0.10478 |  | 1 | ENERGY
924152 | AB2-059 E OP | 115 | 345 | 75 | 0 | 34 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AB2-059
922923 | AB1-081 E OP | 115 | 345 | 75 | 0 | 24 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AB1-081
925997 | AC1-075 E | 0.6 | 345 | 75 | 0 | 21.7 | 0 |  |  | -0.00143 |  |  | 0 |  | 1 | NEWENERGY | AC1-075
208915 | SAHA 567 | 13.8 | 229 | 61 | -3 | 97 | 77.88 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
926274 | AC1-105 E | 0.57 | 345 | 75 | 0 | 16.95 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | AC1-105
316020 | AB2-059 C OP | 115 | 345 | 75 | 0 | 66 | 52.99 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AB2-059
208914 | SAHA 34 | 13.8 | 229 | 61 | -2 | 64.5 | 51.78 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
208913 | SAHA 12 | 13.8 | 229 | 61 | -2 | 64 | 51.38 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
922922 | AB1-081 C OP | 115 | 345 | 75 | 0 | 56 | 44.96 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AB1-081
315266 | 1PLYWOOD A | 13.8 | 345 | 2 | 0 | 45.6 | 36.61 |  |  | -0.00142 |  |  | 0.10478 |  | 1 | CAPACITY
315159 | 1KERR 2 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
315161 | 1KERR 4 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
315163 | 1KERR 6 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
315162 | 1KERR 5 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
315164 | 1KERR 7 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
315160 | 1KERR 3 | 13.8 | 345 | 61 | 17 | 42 | 33.72 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
316123 | AC1-075 C | 0.6 | 345 | 75 | 0 | 38.3 | 30.75 |  |  | -0.00143 |  |  | 0 |  | 1 | CAPACITY | AC1-075
235838 | 01GRNGAP | 0.69 | 201 | 74 | 0 | 38.2 | 30.67 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | K11
926024 | AC1-080 E | 0.6 | 345 | 75 | 0 | 7.2 | 0 |  |  | -0.00143 |  |  | 0 |  | 1 | NEWENERGY | AC1-080
316118 | AC1-105 C | 0.57 | 345 | 75 | 0 | 34.5 | 27.7 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | AC1-105
314608 | 3TARBORO | 115 | 345 | 75 | 0 | 6.2 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
237329 | 01CHBRG_I12 | 69 | 201 | 65 | 0 | 29.5 | 23.68 |  |  | -0.00143 |  |  | 0.12623 |  | 1 | CAPACITY
315188 | 1LOWMORC | 13.2 | 345 | 20 | 0 | 25.2 | 20.23 |  |  | -0.00142 |  |  | 0.10478 |  | 1 | CAPACITY
315186 | 1LOWMORA | 13.2 | 345 | 20 | 0 | 25.1 | 20.15 |  |  | -0.00142 |  |  | 0.10478 |  | 1 | CAPACITY
315604 | 1NEW CREEK | 34.5 | 345 | 74 | 0 | 20.5 | 16.46 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | T157
917342 | Z2-044 E | 115 | 345 | 75 | 0 | 3.6 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY | Z2-044
315158 | 1KERR 1 | 13.8 | 345 | 60 | 9 | 15 | 12.04 |  |  | -0.00142 |  |  | 0.07484 |  | 1 | CAPACITY
926023 | AC1-080 C | 0.6 | 345 | 75 | 0 | 12.8 | 10.28 |  |  | -0.00143 |  |  | 0 |  | 1 | CAPACITY | AC1-080
314623 | 3WITAKRS | 115 | 345 | 75 | 0 | 2.51 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY | Z2-044
208769 | SISO | 12.5 | 229 | 2 | 0 | 2.48 | 0 |  |  | -0.00143 |  |  | 0 |  | 1 | ENERGY
315254 | 1MT STMG | 13.8 | 345 | 52 | 0 | 11.9 | 9.55 |  |  | -0.00143 |  |  | 0.08446 |  | 1 | CAPACITY
314554 | 3BTLEBRO | 115 | 345 | 75 | 0 | 1.61 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
313738 | 3CUSHAW | 115 | 345 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00142 |  |  | 0 |  | 1 | CAPACITY
314549 | 3TOT1 | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
314557 | 3BETHELC | 115 | 345 | 75 | 0 | 1.07 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
208876 | WLAN | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00143 |  |  | 0 |  | 1 | CAPACITY
314607 | 3TAR RVR | 115 | 345 | 75 | 0 | 0.54 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
314205 | 3HEARTS | 115 | 345 | 75 | 0 | 0.41 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
314545 | 3TOT5 | 115 | 345 | 75 | 0 | 0.32 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
314560 | 3CNETO | 115 | 345 | 75 | 0 | 0.21 | 0 |  |  | -0.00142 |  |  | 0 |  | 1 | NEWENERGY
CBM South 2 | LTFEXP_CBM-S2->PJM |  |  | LTF |  | 1044 |  |  |  | -0.0014
CPLE | LTFEXP_CPLE->PJM |  |  | LTF |  | 68.3 |  |  |  | -0.0014
246844 | 05SMG2 | 13.8 | 205 | 62 | 0 | 193 | 154.95 |  |  | -0.00144 |  |  | 0.0316 |  | 1 | CAPACITY
246846 | 05SMG4 | 13.8 | 205 | 62 | 0 | 190 | 152.54 |  |  | -0.00144 |  |  | 0.0316 |  | 1 | CAPACITY
926646 | AC1-145 E | 0.6 | 345 | 75 | 0 | 31 | 0 |  |  | -0.00144 |  |  | 0 |  | 1 | NEWENERGY | AC1-145
246845 | 05SMG3 | 13.8 | 205 | 62 | 0 | 121 | 97.14 |  |  | -0.00144 |  |  | 0.0316 |  | 1 | CAPACITY
205908 | AC1-048 E | 0.39 | 227 | 75 | 0 | 21.7 | 0 |  |  | -0.00143 |  |  | 0 |  | 1 | NEWENERGY | AC1-048
246847 | 05SMG5 | 13.8 | 205 | 62 | 0 | 74 | 59.41 |  |  | -0.00144 |  |  | 0.0316 |  | 1 | CAPACITY
246843 | 05SMG1 | 13.8 | 205 | 62 | 0 | 71 | 57 |  |  | -0.00144 |  |  | 0.0316 |  | 1 | CAPACITY
205907 | AC1-048 C | 0.39 | 227 | 75 | 0 | 13.3 | 0 |  |  | -0.00143 |  |  | 0 |  | 1 | NEW | AC1-048
205910 | AC2-053 E | 0.39 | 227 | 74 | 0 | 12.4 | 0 |  |  | -0.00143 |  |  | 0 |  | 1 | NEWENERGY | AC2-053
244012 | 05PINNACLE | 4 | 205 | 1 | 0 | 11 | 0 |  |  | -0.00144 |  |  | 0.10478 |  | 1 | ENERGY
315156 | 1HALLBR1 | 13.8 | 345 | 2 | 15 | 52.4 | 42.07 |  |  | -0.00144 |  |  | 0.10478 |  | 1 | CAPACITY
247284 | 05LEESVG | 13.8 | 205 | 60 | 0 | 49.9 | 40.06 |  |  | -0.00144 |  |  | 0.07484 |  | 1 | CAPACITY
205909 | AC2-053 C | 0.39 | 227 | 74 | 0 | 7.6 | 0 |  |  | -0.00143 |  |  | 0 |  | 1 | NEW | AC2-053
926645 | AC1-145 C | 0.6 | 345 | 75 | 0 | 19 | 15.25 |  |  | -0.00144 |  |  | 0 |  | 1 | CAPACITY | AC1-145
235098 | U2-073A E | 0.57 | 201 | 74 | 0 | 116.1 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEWENERGY | U2-073 A
235520 | 01WVACO_S38 | 13.8 | 201 | 2 | 0 | 60 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEW
235099 | U2-073B E | 0.57 | 201 | 74 | 0 | 50.9 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEWENERGY | U2-073 B
236001 | 01WARRIOR RN | 18 | 201 | 12 | 72 | 180 | 144.51 |  |  | -0.00144 |  |  | 0.10478 |  | 1 | CAPACITY
926462 | AC1-117 E | 138 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00144 |  |  | 0 |  | 1 | NEWENERGY | AC1-117
237084 | AD1-018 E | 0.38 | 201 | 75 | 0 | 12.4 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEWENERGY | AD1-018
235526 | 01WR_AA1-100 | 138 | 201 | 76 | -11 | 11 | 0 |  |  | -0.00144 |  |  | 0.05 |  | 1 | MTX | AA1-100
926461 | AC1-117 C | 138 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00144 |  |  | 0 |  | 1 | NEW | AC1-117
237089 | AD1-018 C | 0.38 | 201 | 75 | 0 | 7.6 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEW | AD1-018
242906 | 05CLAY-1 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00145 |  |  | 0.07484 |  | 1 | CAPACITY
242907 | 05CLAY-2 | 11 | 205 | 60 | 0 | 37.6 | 30.19 |  |  | -0.00145 |  |  | 0.07484 |  | 1 | CAPACITY
235530 | 01TR_U2-073A | 0.57 | 201 | 74 | 0 | 25.9 | 20.79 |  |  | -0.00145 |  |  | 0 |  | 1 | CAPACITY | U2-073 A
209030 | FRFA O01 | 12.5 | 229 | 2 | 0 | 3.2 | 0 |  |  | -0.00144 |  |  | 0 |  | 1 | NEW
235531 | 01TR_U2-073B | 0.57 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00145 |  |  | 0 |  | 1 | CAPACITY | U2-073 B
270148 | AE1-018 E | 138 | 205 | 75 | 0 | 2.2 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEWENERGY | AE1-018
237507 | 01CROSSCHOOL | 34.5 | 201 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00145 |  |  | 0 |  | 1 | CAPACITY | N47
903052 | W2-094 E | 115 | 227 | 75 | 0 | 1.9 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEWENERGY | W2-094
247723 | 05PHILPOTT | 138 | 205 | 60 | 0 | 8 | 6.42 |  |  | -0.00144 |  |  | 0 |  | 1 | CAPACITY
205911 | 27W2-094 | 115 | 227 | 75 | 0 | 1.1 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEWENERGY | W2-094
247619 | Y1-049 | 34.5 | 205 | 64 | 0 | 4.1 | 3.29 |  |  | -0.00145 |  |  | 0 |  | 1 | CAPACITY
242889 | 05REUSENS | 34.5 | 205 | 60 | 0 | 4 | 3.21 |  |  | -0.00144 |  |  | 0 |  | 1 | CAPACITY
217203 | FBANKSOLAR E | 13.2 | 231 | 75 | 0 | 0.63 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEWENERGY | X2-087
270147 | AE1-018 C | 138 | 205 | 75 | 0 | 2.8 | 2.25 |  |  | -0.00145 |  |  | 0 |  | 1 | CAPACITY | AE1-018
208835 | TUHI V3-051 | 12.5 | 229 | 74 | 0 | 0.4 | 0.32 |  |  | -0.00144 |  |  | 0 |  | 1 | CAPACITY | V3-051
217202 | FBANKSOLAR C | 13.2 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.00145 |  |  | 0 |  | 1 | CAPACITY | X2-087
LAGN | LTFEXP_LAGN->PJM |  |  | LTF |  | 175 |  |  |  | -0.0015
TVA | LTFEXP_TVA->PJM |  |  | LTF |  | 140 |  |  |  | -0.0015
246895 | 05VACITY | 23 | 205 | 16 | 300 | 610.3 | 489.98 |  |  | -0.00146 |  |  | 0.10478 |  | 1 | CAPACITY
913035 | Y1-006 E | 0.65 | 205 | 74 | 0 | 62.64 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEWENERGY | Y1-006
292401 | K-028 E | 0.69 | 201 | 74 | 0 | 58.6 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEWENERGY | K28
290229 | S-014 E | 0.66 | 201 | 74 | 0 | 56 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEWENERGY | S14
929522 | U2-030 E | 0.66 | 201 | 74 | 0 | 52.2 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEWENERGY | U2-030
CBM South 1 | LTFEXP_CBM-S1->PJM |  |  | LTF |  | 38 |  |  |  | -0.0015
242899 | 05CRG1H | 15.5 | 205 | 13 | 33 | 127.4 | 102.28 |  |  | -0.00146 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
242901 | 05CRG2H | 15.5 | 205 | 13 | 33 | 125.9 | 101.08 |  |  | -0.00146 |  |  | 0.10478 |  | 1 | CAPACITY | CRG1
885642 | T-016 E | 0.69 | 201 | 74 | 0 | 24 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEWENERGY | K28
242900 | 05CRG1L | 15.5 | 205 | 13 | 27 | 106.7 | 85.67 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY
242902 | 05CRG2L | 15.5 | 205 | 13 | 27 | 105.6 | 84.78 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY
204647 | 27HUNTR CT | 13.8 | 227 | 56 | 9 | 60 | 48.17 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247347 | 05WLF1G3 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247349 | 05WLF1G5 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247348 | 05WLF1G4 | 13.8 | 205 | 57 | 25 | 48.8 | 39.18 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247351 | 05WLF2G1 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247352 | 05WLF2G2 | 13.8 | 205 | 56 | 25 | 48.8 | 39.18 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
913034 | Y1-006 C | 0.65 | 205 | 74 | 0 | 9.36 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | NEW | Y1-006
242677 | 05INDDRV | 138 | 205 | 64 | 0 | 45 | 36.13 |  |  | -0.00146 |  |  | 0.12623 |  | 1 | CAPACITY
244165 | 05FRIES | 69 | 205 | 60 | 0 | 5.2 | 0 |  |  | -0.00145 |  |  | 0.07484 |  | 1 | ENERGY
270167 | AD2-205 E | 69 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00145 |  |  | 0 |  | 1 | MTX | AD2-205
204649 | 27ORTAN CT | 13.8 | 227 | 56 | 0 | 19.5 | 15.66 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
235854 | 01KL_K28_T16 | 0.69 | 201 | 74 | 0 | 17.4 | 13.97 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY | K28
244160 | 05BYLLESBY | 13 | 205 | 60 | 0 | 14.1 | 11.32 |  |  | -0.00145 |  |  | 0.07484 |  | 1 | CAPACITY
237312 | 01DANS_S-014 | 0.66 | 201 | 74 | 0 | 14 | 11.24 |  |  | -0.00145 |  |  | 0 |  | 1 | CAPACITY | S14
923761 | AB2-010 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEW | AB2-010
923762 | AB2-010 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEWENERGY | AB2-010
923772 | AB2-011 E | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEWENERGY | AB2-011
923771 | AB2-011 C | 138 | 205 | 75 | 0 | 2.5 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEW | AB2-011
244159 | 05BUCK | 13 | 205 | 60 | 0 | 9.7 | 7.79 |  |  | -0.00145 |  |  | 0 |  | 1 | CAPACITY
237319 | 01FMR_U2-030 | 0.66 | 201 | 74 | 0 | 7.8 | 6.26 |  |  | -0.00145 |  |  | 0 |  | 1 | CAPACITY | U2-030
270132 | AB1-180 C | 46 | 205 | 64 | 0 | 1.3 | 1.04 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY
CBM West 2 | LTFEXP_CBM-W2->PJM |  |  | LTF |  | 896 |  |  |  | -0.0015
237085 | AD2-192 GEN | 23 | 201 | 57 | 0 | 600 | 0 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | NEW
293798 | W4-005 E | 0.69 | 222 | 74 | 0 | 305.37 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | W4-005
243187 | 05GVG2 | 26 | 205 | 18 | 500 | 1396 | 1120.79 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | GVG2
243186 | 05GVG1 | 26 | 205 | 18 | 500 | 1371 | 1100.72 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | GVG1
243442 | 05RKG1 | 26 | 205 | 18 | 522 | 1356 | 1088.67 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | RKG1
242894 | 05MTG1 | 26 | 205 | 18 | 500 | 1356 | 1088.67 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | MTG1
242893 | 05AMG3 | 26 | 205 | 18 | 781.2 | 1330 | 1067.8 |  |  | -0.00146 |  |  | 0.10478 |  | 1 | CAPACITY | AMG3
243443 | 05RKG2 | 26 | 205 | 18 | 548.8 | 1300 | 1043.71 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | RKG2
274654 | BRAIDWOOD;1U | 25 | 222 | 45 | 657.6 | 1183 | 949.78 |  |  | -0.00147 |  |  | 0.01494 |  | 1 | CAPACITY
274656 | BYRON ;1U | 25 | 222 | 45 | 700 | 1168.5 | 938.14 |  |  | -0.00147 |  |  | 0.01494 |  | 1 | CAPACITY
274655 | BRAIDWOOD;2U | 25 | 222 | 45 | 658.1 | 1154 | 926.5 |  |  | -0.00147 |  |  | 0.01494 |  | 1 | CAPACITY
274657 | BYRON ;2U | 25 | 222 | 45 | 700 | 1141.5 | 916.46 |  |  | -0.00147 |  |  | 0.01494 |  | 1 | CAPACITY
274661 | LASCO STA;2U | 25 | 222 | 49 | 150 | 1135.9 | 911.97 |  |  | -0.00147 |  |  | 0.01494 |  | 1 | CAPACITY
274660 | LASCO STA;1U | 25 | 222 | 49 | 150 | 1131.2 | 908.19 |  |  | -0.00147 |  |  | 0.01494 |  | 1 | CAPACITY
290108 | LEEDK;1U E | 0.57 | 222 | 74 | 0 | 200 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Q57
918472 | AA1-062 E | 138 | 201 | 74 | 0 | 195 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEWENERGY | AA1-062
276621 | X2-022 GEN | 0.69 | 222 | 74 | 0 | 185 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | X2-022
274663 | QUAD CITI;2U | 18 | 222 | 48 | 150 | 911.7 | 731.97 |  |  | -0.00147 |  |  | 0.01494 |  | 1 | CAPACITY
274662 | QUAD CITI;1U | 18 | 222 | 48 | 150 | 911.1 | 731.48 |  |  | -0.00147 |  |  | 0.01494 |  | 1 | CAPACITY
274658 | DRESDEN ;2U | 18 | 222 | 48 | 150 | 902.5 | 724.58 |  |  | -0.00147 |  |  | 0.01494 |  | 1 | CAPACITY
274659 | DRESDEN ;3U | 18 | 222 | 48 | 150 | 895.5 | 718.96 |  |  | -0.00147 |  |  | 0.01494 |  | 1 | CAPACITY
917502 | Z2-087 E | 345 | 222 | 74 | 0 | 174 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Z2-087
930042 | AB1-006 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AB1-006
247958 | 05WLD G2 E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | U3-002 2
247963 | 05HDWTR1G E | 0.69 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | U2-090
247935 | V3-007 E | 345 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | V3-007
290021 | O50 E | 0.69 | 222 | 74 | 0 | 160 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | O50
247906 | 05MDL-1G E | 0.6 | 205 | 74 | 0 | 159.7 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | S06
247904 | 05FR-3G E | 0.69 | 205 | 74 | 0 | 159.6 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Q01 3
MEC | LTFEXP_MEC->PJM |  |  | LTF |  | 158.9 |  |  |  | -0.0015
290261 | S-027 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | S27
290265 | S-028 E | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | S28
293645 | O22 E2 | 0.69 | 222 | 74 | 0 | 158.4 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | O22 2
242892 | 05AMG2 | 26 | 205 | 17 | 330.8 | 800 | 642.29 |  |  | -0.00146 |  |  | 0.10478 |  | 1 | CAPACITY
242891 | 05AMG1 | 26 | 205 | 17 | 339.4 | 800 | 642.29 |  |  | -0.00146 |  |  | 0.10478 |  | 1 | CAPACITY
294392 | P-010 E | 0.57 | 222 | 74 | 0 | 152.4 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | P10
274678 | POWERTON ;6U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
274677 | POWERTON ;5U | 25 | 222 | 16 | 350 | 769 | 617.4 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
251968 | 08ZIMRHP | 26 | 212 | 17 | 420 | 734 | 589.3 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | ZIMM
293799 | PILOT HIL;1E | 0.7 | 222 | 74 | 0 | 140 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | S36
275149 | KELLYCK ;1E | 34.5 | 222 | 74 | 0 | 140 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | S37
235853 | 01AC1-140 | 26 | 201 | 16 | 280 | 710 | 570.03 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
918052 | AA1-018 E OP | 345 | 222 | 74 | 0 | 130.5 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AA1-018
235586 | 01HARRN2 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
235587 | 01HARRN3 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
235585 | 01HARRN1 | 20 | 201 | 16 | 450 | 653.4 | 524.59 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
247905 | 05FR-4G E | 0.69 | 205 | 74 | 0 | 125 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Q01 4
990901 | L-005 E | 0.69 | 222 | 74 | 0 | 124 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | ENERGY | L05_CE22
253314 | AC1-085 A_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 A
253317 | AC1-085 B_E | 0.6 | 209 | 75 | 0 | 124 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AC1-085 B
293778 | CAYUG;2U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | O51 2
293777 | CAYUG;1U E | 0.69 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | O51 1
293061 | N-015 E | 0.57 | 222 | 74 | 0 | 120 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | N15
251969 | 08ZIMRLP | 22 | 212 | 18 | 230 | 586 | 470.47 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | ZIMM
927091 | AC1-204 GEN1 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-204
927093 | AC1-204 GEN2 | 23 | 222 | 58 | 0 | 557.95 | 447.95 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AC1-204
274651 | KINCAID ;2U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
274650 | KINCAID ;1U | 20 | 222 | 15 | 240 | 556 | 446.39 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
235583 | 01FMRTN1 | 22 | 201 | 15 | 320 | 552 | 443.18 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
235584 | 01FMRTN2 | 22 | 201 | 15 | 220 | 545.5 | 437.96 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
274676 | JOLIET 29;8U | 24 | 222 | 15 | 100 | 518 | 415.88 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
274675 | JOLIET 29;7U | 24 | 222 | 15 | 70 | 518 | 415.88 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
342960 | 1SPURLK2G | 22 | 320 | 15 | 280 | 510 | 409.46 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
251950 | 08M.FRT7 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
251951 | 08M.FRT8 | 22 | 212 | 15 | 239 | 510 | 409.46 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
274687 | WILL CNTY;4U | 20 | 222 | 15 | 0 | 510 | 409.46 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | WILL4
274860 | EASYR;U2 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | P36 2
274859 | EASYR;U1 E | 0.69 | 222 | 74 | 0 | 96 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | P36 1
926105 | AC1-089 E | 0.39 | 205 | 75 | 0 | 93 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AC1-089
293715 | O-029 E | 0.69 | 222 | 74 | 0 | 87.71 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | O29 1
290051 | GSG-6; E | 0.69 | 222 | 74 | 0.9 | 87.6 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | P26
235092 | P59+W2-57 E | 0.69 | 201 | 74 | 0 | 85.9 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEWENERGY | P59
923384 | M24 E | 0.69 | 201 | 74 | 0 | 85.5 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEWENERGY | M24
247902 | 05FR-21G E | 0.6 | 205 | 74 | 0 | 82.3 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Q01 21
293516 | O-009 E1 | 0.69 | 222 | 74 | 0 | 82.04 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | O09 1
293644 | O22 E1 | 0.69 | 222 | 74 | 0 | 81.6 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | O22 1
294410 | BSHIL;2U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | P11 2
294401 | BSHIL;1U E | 0.69 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | P11 1
294763 | P-046 E | 12 | 222 | 74 | 0 | 80 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | P46
247907 | 05MDL-2G E | 12 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | T126 2
247913 | 05MDL-4G E | 0.6 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | T127 4
247943 | T-127 E | 0.74 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | T127 5
247912 | 05MDL-3G E | 0.69 | 205 | 74 | 0 | 80 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | T126 3
247903 | 05FR-22G E | 0.69 | 205 | 75 | 0 | 78.8 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Q01 22
247900 | 05FR-11G E | 0.6 | 205 | 75 | 0 | 78.3 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Q01 11
930062 | AB1-014 E | 138 | 212 | 75 | 0 | 77.5 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AB1-014
251947 | 08EBND2 | 20 | 212 | 16 | 522 | 600 | 522.66 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
247901 | 05FR-12G E | 0.6 | 205 | 74 | 0 | 77 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Q01 12
274683 | WAUKEGAN ;8U | 18 | 222 | 14 | 155 | 354.4 | 284.53 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK8
276615 | W2-048 GEN | 0.69 | 222 | 74 | 0 | 65 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | W2-048
274682 | WAUKEGAN ;7U | 18 | 222 | 14 | 130 | 328 | 263.34 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | WAUK7
253357 | AB1-169 CT2 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253355 | AB1-169 CT1 | 25 | 209 | 58 | 0 | 320.8 | 257.56 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-169
LGEE | LTFEXP_LGEE->PJM |  |  | LTF |  | 62.8 |  |  |  | -0.0015
243764 | 05BSG1 | 22 | 205 | 13 | 100 | 305 | 244.87 |  |  | -0.00146 |  |  | 0.10478 |  | 1 | CAPACITY
293771 | O-035 E | 0.69 | 222 | 74 | 0 | 59.2 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | O35
342957 | 1SPURLK1G | 22 | 320 | 14 | 100 | 300 | 240.86 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
247247 | 05HRKG1S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
247250 | 05HRKG2S | 18 | 205 | 58 | 100 | 297.4 | 238.77 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
252500 | Z1-079 CT | 21 | 212 | 58 | 143.4 | 294 | 236.04 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | Z1-079
274674 | JOLIET 9 ;6U | 18 | 222 | 13 | 90 | 281 | 225.6 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
247269 | 05LAWG2S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247266 | 05LAWG1S | 18 | 205 | 58 | 100 | 275.35 | 221.07 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
342963 | 1SPURLK3G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
342966 | 1SPURLK4G | 18 | 320 | 14 | 80 | 268 | 215.16 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
293716 | O-029 E | 0.57 | 222 | 74 | 0 | 48.09 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | O29 2
295109 | WESTBROOK E | 138 | 222 | 74 | 0 | 46.9 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | NQ71
293518 | O-009 E3 | 0.57 | 222 | 74 | 0 | 45.89 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | O09 3
916221 | Z1-073 E | 0.7 | 222 | 74 | 0 | 45.5 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Z1-073
253356 | AB1-169 ST1 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AB1-169
253358 | AB1-169 ST2 | 25 | 209 | 58 | 0 | 229.2 | 184.02 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AB1-169
916211 | Z1-072 E | 0.6 | 222 | 74 | 0 | 44.8 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Z1-072
342903 | 1COOPER2 G | 20 | 320 | 31 | 75 | 225 | 180.64 |  |  | -0.00146 |  |  | 0.10478 |  | 1 | CAPACITY
293717 | O-029 E | 0.6 | 222 | 74 | 0 | 44.2 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | O29 3
931012 | AB1-150 E | 138 | 201 | 74 | 0 | 43.9 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEWENERGY | AB1-150
235091 | U2-061_E | 34.5 | 201 | 74 | 0 | 43.5 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEWENERGY | U2-061
252501 | Z1-079 ST | 18 | 212 | 58 | 100.4 | 219 | 175.82 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Z1-079
293517 | O-009 E2 | 0.6 | 222 | 74 | 0 | 41.67 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | O09 2
247245 | 05HRKG1A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00146 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 1
247248 | 05HRKG2A | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00146 |  |  | 0.04435 |  | 1 | CAPACITY | Hanging Rock 2
247249 | 05HRKG2B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 2
247246 | 05HRKG1B | 18 | 205 | 58 | 100 | 186.3 | 149.57 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY | Hanging Rock 1
274708 | KENDALL ;3C | 18 | 222 | 58 | 140 | 184.3 | 147.97 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 3
274706 | KENDALL ;2C | 18 | 222 | 58 | 119 | 182.3 | 146.36 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 2
274704 | KENDALL ;1C | 18 | 222 | 58 | 120 | 182.3 | 146.36 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 1
274710 | KENDALL ;4C | 18 | 222 | 58 | 138 | 182.3 | 146.36 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | Kendall 4
274701 | CORDOVA ;1S | 18 | 222 | 58 | 0 | 180 | 144.51 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
247225 | 05FTHLG2 | 18 | 205 | 57 | 120 | 173.8 | 139.54 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247224 | 05FTHLG1 | 18 | 205 | 57 | 120 | 173.7 | 139.46 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247267 | 05LAWG2A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 2
247268 | 05LAWG2B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 2
247264 | 05LAWG1A | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | Lawrenceburg 1
247265 | 05LAWG1B | 18 | 205 | 58 | 90 | 172.4 | 138.41 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Lawrenceburg 1
247230 | 05RIVRG1 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247231 | 05RIVRG2 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247232 | 05RIVRG3 | 18 | 205 | 57 | 120 | 171.5 | 137.69 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
274717 | NELSON EC;2C | 18 | 222 | 58 | 0 | 169.6 | 136.16 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | NELSON
274715 | NELSON EC;1C | 18 | 222 | 58 | 0 | 168.3 | 135.12 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | NELSON
247220 | 05FLATG5 | 18 | 205 | 57 | 0 | 167.3 | 134.32 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247217 | 05FLATG2 | 18 | 205 | 57 | 0 | 167.1 | 134.16 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247219 | 05FLATG4 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247216 | 05FLATG1 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247218 | 05FLATG3 | 18 | 205 | 57 | 0 | 167 | 134.08 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274725 | ZION EC ;1P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274726 | ZION EC ;2P | 18 | 222 | 57 | 100 | 165 | 132.47 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274727 | ZION EC ;3P | 18 | 222 | 30 | 100 | 165 | 132.47 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
274723 | RIVER EC ;12 | 16 | 222 | 57 | 105 | 164.1 | 131.75 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
236845 | 01BR_BAT_M24 | 34.5 | 201 | 76 | -32 | 32 | 0 |  |  | -0.00146 |  |  | 0.05 |  | 1 | MTX | M24 BAT
274724 | RIVER EC ;11 | 16 | 222 | 57 | 105 | 162 | 130.06 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274699 | CORDOVA ;1C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | CORDOVA
274700 | CORDOVA ;2C | 18 | 222 | 58 | 0 | 160 | 128.46 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | CORDOVA
WEC | LTFEXP_WEC->PJM |  |  | LTF |  | 31.5 |  |  |  | -0.0015
919221 | AA1-146 | 345 | 222 | 58 | 0 | 157 | 126.05 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
292981 | N-007 E | 138 | 201 | 74 | 0 | 30.4 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEWENERGY | N07
274738 | AURORA EC;3P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274740 | AURORA EC;4P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274737 | AURORA EC;1P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274739 | AURORA EC;2P | 18 | 222 | 57 | 50 | 152 | 122.03 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274729 | ELWOOD EC;1P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274731 | ELWOOD EC;2P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274735 | ELWOOD EC;4P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274733 | ELWOOD EC;3P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274730 | ELWOOD EC;6P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274728 | ELWOOD EC;5P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274736 | ELWOOD EC;9P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274734 | ELWOOD EC;8P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274732 | ELWOOD EC;7P | 18 | 222 | 57 | 110 | 150 | 120.43 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
235801 | 01WM_AA1_062 | 138 | 201 | 74 | 0 | 29 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEW | AA1-062
276591 | L-013 2 | 34.5 | 222 | 56 | 0 | 29 | 0 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | ENERGY
248022 | 06CLIFTY 5HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | CLIF5
248014 | 06CLIFTY 1HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | CLIF1
248024 | 06CLIFTY 6HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | CLIF6
248020 | 06CLIFTY 4HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | CLIF4
248018 | 06CLIFTY 3HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | CLIF3
248016 | 06CLIFTY 2HP | 15.5 | 206 | 18 | 50 | 124.7 | 100.12 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF2
248026 | 06KYGER 1HP | 15.5 | 206 | 17 | 50 | 124.2 | 99.72 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | KYG1
274718 | NELSON EC;2S | 13.8 | 222 | 58 | 0 | 123.9 | 99.47 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | NELSON
248030 | 06KYGER 3HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | KYG3
248028 | 06KYGER 2HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | KYG2
248032 | 06KYGER 4HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | KYG4
248034 | 06KYGER 5HP | 15.5 | 206 | 17 | 50 | 123.4 | 99.07 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | KYG5
274716 | NELSON EC;1S | 13.8 | 222 | 58 | 0 | 122.8 | 98.59 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | NELSON
274705 | KENDALL ;1S | 13.8 | 222 | 58 | 60 | 121.9 | 97.87 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Kendall 1
274707 | KENDALL ;2S | 13.8 | 222 | 58 | 58 | 121.9 | 97.87 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Kendall 2
274709 | KENDALL ;3S | 13.8 | 222 | 58 | 63 | 121.9 | 97.87 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Kendall 3
274711 | KENDALL ;4S | 13.8 | 222 | 58 | 65 | 121.9 | 97.87 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Kendall 4
274818 | ELGIN EC ;1P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274820 | ELGIN EC ;2P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274821 | ELGIN EC ;4P | 13.8 | 222 | 57 | 79 | 121 | 97.14 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274819 | ELGIN EC ;3P | 13.8 | 222 | 57 | 79 | 120.1 | 96.42 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
342900 | 1COOPER1 G | 13.8 | 320 | 31 | 35 | 116 | 93.13 |  |  | -0.00146 |  |  | 0.10478 |  | 1 | CAPACITY
295111 | SUBLETTE E | 138 | 222 | 74 | 0 | 22.8 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | NQ72
274836 | EQUISTAR ; R | 13.8 | 222 | 58 | 18 | 115.4 | 92.65 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | EQUISTAR MORRIS
342921 | 1JKCT 2G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
342918 | 1JKCT 1G | 13.8 | 320 | 57 | 0 | 110 | 88.31 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
342924 | 1JKCT 3G | 13.8 | 320 | 57 | 0 | 109.5 | 87.91 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
274696 | ROCKY RD ;4P | 13.8 | 222 | 57 | 75.6 | 104 | 83.5 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274695 | ROCKY RD ;2P | 13.8 | 222 | 57 | 72.7 | 101.6 | 81.57 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
920072 | AA2-103 E | 138 | 201 | 76 | -20 | 20 | 0 |  |  | -0.00146 |  |  | 0.05 |  | 1 | MTX | AA2-103
920272 | AA2-123 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00147 |  |  | 0.05 |  | 1 | MTX | AA2-123
276170 | Z1-108 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00147 |  |  | 0.05 |  | 1 | MTX | Z1-108
276169 | Z1-107 E | 34.5 | 222 | 76 | -20 | 20 | 0 |  |  | -0.00147 |  |  | 0.05 |  | 1 | MTX | Z1-107
276592 | O-012 C | 138 | 222 | 64 | 0 | 20 | 0 |  |  | -0.00147 |  |  | 0.12623 |  | 1 | ENERGY
274828 | WAUKEGAN ;BP | 138 | 222 | 57 | 1 | 100.8 | 80.93 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274693 | ROCKY RD ;1P | 13.8 | 222 | 57 | 71.2 | 100.6 | 80.77 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274823 | ROCKFORD ;21 | 16 | 222 | 57 | 133.1 | 153 | 133.28 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274826 | FISK ;BP | 12.5 | 222 | 53 | 1 | 99.9 | 80.21 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274822 | ROCKFORD ;11 | 16 | 222 | 57 | 129.7 | 149.1 | 129.88 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274824 | ROCKFORD ;12 | 16 | 222 | 57 | 128.6 | 147.8 | 128.75 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
243415 | 05WWVSTA | 69 | 205 | 61 | 60 | 96 | 77.08 |  |  | -0.00147 |  |  | 0.07484 |  | 1 | CAPACITY
274765 | LEE CO EC;6U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274764 | LEE CO EC;5U | 13.8 | 222 | 57 | 45 | 85.1 | 68.32 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274761 | LEE CO EC;2U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274760 | LEE CO EC;1U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274762 | LEE CO EC;3U | 13.8 | 222 | 57 | 45 | 84.9 | 68.16 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274763 | LEE CO EC;4U | 13.8 | 222 | 57 | 45 | 84.1 | 67.52 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274766 | LEE CO EC;7U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274767 | LEE CO EC;8U | 13.8 | 222 | 57 | 45 | 83.9 | 67.36 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
251967 | 08WSDLE6 | 13.8 | 212 | 57 | 5 | 81.6 | 65.51 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274837 | EQUISTAR ; B | 13.8 | 222 | 58 | 34 | 81.5 | 65.43 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | EQUISTAR MORRIS
251964 | 08WSDLE3 | 13.8 | 212 | 57 | 5 | 80.8 | 64.87 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
251963 | 08WSDLE2 | 13.8 | 212 | 57 | 5 | 80.1 | 64.31 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
244467 | 05SUMMERVL | 69 | 205 | 61 | 0 | 80 | 64.23 |  |  | -0.00146 |  |  | 0.07484 |  | 1 | CAPACITY
235555 | 01GRANT | 13.8 | 201 | 11 | 32 | 80 | 64.23 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
251966 | 08WSDLE5 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
251962 | 08WSDLE1 | 13.8 | 212 | 57 | 5 | 79.6 | 63.91 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
251965 | 08WSDLE4 | 13.8 | 212 | 57 | 5 | 77.4 | 62.14 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274776 | LINCOLN ;7U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274774 | LINCOLN ;5U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274775 | LINCOLN ;6U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274772 | LINCOLN ;3U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274777 | LINCOLN ;8U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274773 | LINCOLN ;4U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274770 | LINCOLN ;1U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274771 | LINCOLN ;2U | 13.8 | 222 | 57 | 0 | 77 | 61.82 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
246861 | 05CER G3 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
246865 | 05CER G6 | 13.8 | 205 | 57 | 0 | 76.1 | 61.1 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
342942 | 1JKCT 10G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
342939 | 1JKCT 9G | 13.8 | 320 | 57 | 0 | 76 | 61.02 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
250166 | HLCRST AB114 | 138 | 212 | 75 | 0 | 76 | 61.02 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AB1-014
253316 | AC1-085 B_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AC1-085 B
253313 | AC1-085 A_C | 0.6 | 209 | 75 | 0 | 76 | 61.02 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AC1-085 A
246862 | 05CER G4 | 13.8 | 205 | 57 | 0 | 75.9 | 60.94 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
246859 | 05CER G2 | 13.8 | 205 | 57 | 0 | 75.7 | 60.78 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
246858 | 05CER G1 | 13.8 | 205 | 57 | 0 | 75.6 | 60.7 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
246864 | 05CER G5 | 13.8 | 205 | 57 | 0 | 75.4 | 60.53 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
274751 | CRETE EC ;1U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274753 | CRETE EC ;3U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274754 | CRETE EC ;4U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274752 | CRETE EC ;2U | 13.8 | 222 | 57 | 0 | 75.2 | 60.38 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
248025 | 06CLIFTY 6LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF6
248019 | 06CLIFTY 3LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF3
248017 | 06CLIFTY 2LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | CLIF2
248023 | 06CLIFTY 5LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF5
248021 | 06CLIFTY 4LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF4
248015 | 06CLIFTY 1LP | 15.5 | 206 | 18 | 30 | 73.3 | 58.85 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | CLIF1
247287 | 05AND G3 | 13.8 | 205 | 57 | 45 | 73.2 | 58.77 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
342927 | 1JKCT 4G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
342936 | 1JKCT 7G | 13.8 | 320 | 57 | 0 | 73 | 58.61 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
342933 | 1JKCT 6G | 13.8 | 320 | 57 | 0 | 72.9 | 58.53 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
248027 | 06KYGER 1LP | 15.5 | 206 | 17 | 30 | 72.8 | 58.45 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | KYG1
342930 | 1JKCT 5G | 13.8 | 320 | 57 | 0 | 72.6 | 58.29 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
248029 | 06KYGER 2LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | KYG2
248035 | 06KYGER 5LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | KYG5
248033 | 06KYGER 4LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY | KYG4
248031 | 06KYGER 3LP | 15.5 | 206 | 17 | 30 | 72.6 | 58.29 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | KYG3
251958 | 08MADSN7 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
251956 | 08MADSN5 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
251957 | 08MADSN6 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
251959 | 08MADSN8 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
251953 | 08MADSN2 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
251955 | 08MADSN4 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
251952 | 08MADSN1 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
251954 | 08MADSN3 | 13.8 | 212 | 57 | 50 | 72 | 57.81 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274827 | FISK ;RP | 12.5 | 222 | 53 | 1 | 70.8 | 56.84 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
342945 | 1LAUREL 1G | 13.8 | 320 | 61 | 0 | 70 | 56.2 |  |  | -0.00146 |  |  | 0.07484 |  | 1 | CAPACITY
251944 | 08D.CRK1 | 10 | 212 | 57 | 5 | 69 | 55.4 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
342948 | 1LOVE HYDRO | 4.16 | 320 | 61 | 0 | 65.9 | 52.91 |  |  | -0.00147 |  |  | 0.07484 |  | 1 | CAPACITY
251828 | CLNTESP1 | 34.5 | 212 | 76 | 0 | 12 | 0 |  |  | -0.00147 |  |  | 0.05 |  | 1 | MTX | Z1-080
926103 | AC1-089 C | 0.39 | 205 | 75 | 0 | 57 | 45.76 |  |  | -0.00147 |  |  | 0.05 |  | 1 | NEW | AC1-089
243827 | 05SUNCOKE | 69 | 205 | 11 | 0 | 55 | 44.16 |  |  | -0.00147 |  |  | 0.10478 |  | 1 | CAPACITY
274798 | UNIV PARK;1U | 13.8 | 222 | 57 | 25 | 53.6 | 43.03 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
SIGE | LTFEXP_SIGE->PJM |  |  | LTF |  | 10.5 |  |  |  | -0.0015
274801 | UNIV PARK;4U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274800 | UNIV PARK;3U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274799 | UNIV PARK;2U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274802 | UNIV PARK;5U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274803 | UNIV PARK;6U | 13.8 | 222 | 57 | 25 | 53.2 | 42.71 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
276168 | Z1-106 E1 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00147 |  |  | 0.05 |  | 1 | MTX | Z1-106
276167 | Z1-106 E2 | 34.5 | 222 | 76 | -10 | 10 | 0 |  |  | -0.00147 |  |  | 0.05 |  | 1 | MTX | Z1-106
251973 | 08YANKGE | 13.8 | 212 | 2 | 0 | 50.5 | 40.54 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | MIDDLETOWN COKE
247322 | 05GRNGG3 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247321 | 05GRNGG2 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247325 | 05GRNGG6 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247324 | 05GRNGG5 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247320 | 05GRNGG1 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
247323 | 05GRNGG4 | 13.8 | 205 | 57 | 25 | 50 | 40.14 |  |  | -0.00146 |  |  | 0.08446 |  | 1 | CAPACITY
243084 | 05RUTLAN | 138 | 205 | 60 | 0 | 46.7 | 37.49 |  |  | -0.00147 |  |  | 0.07484 |  | 1 | CAPACITY
244761 | 05RACINE | 69 | 205 | 60 | 0 | 46 | 36.93 |  |  | -0.00147 |  |  | 0.07484 |  | 1 | CAPACITY
274880 | RADFORD R;1U | 0.69 | 222 | 74 | 0 | 45.6 | 36.61 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | W4-005
274872 | LEE DEKAL;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Q57
274879 | MINONK ;1U | 0.69 | 222 | 74 | 0 | 40 | 32.12 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | O50
274854 | TWINGROVE;U2 | 0.69 | 222 | 74 | 0 | 35.8 | 28.74 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | S28
251972 | 08MELDL3 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00147 |  |  | 0.07484 |  | 1 | CAPACITY
251970 | 08MELDL1 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00147 |  |  | 0.07484 |  | 1 | CAPACITY
251971 | 08MELDL2 | 13.8 | 212 | 61 | 14.4 | 35.3 | 28.34 |  |  | -0.00147 |  |  | 0.07484 |  | 1 | CAPACITY
274862 | TOP CROP ;2U | 0.69 | 222 | 74 | 0 | 35.1 | 28.18 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | O22 2
247286 | 05AND G2 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247285 | 05AND G1 | 13.8 | 205 | 56 | 15 | 35 | 28.1 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274887 | PILOT HIL;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | S36
274888 | KELLY CRK;1U | 0.69 | 222 | 74 | 0 | 35 | 28.1 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | S37
274853 | TWINGROVE;U1 | 0.69 | 222 | 74 | 0 | 34.8 | 27.94 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | S27
247289 | 05RICHG2 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247288 | 05RICHG1 | 13.8 | 205 | 56 | 15 | 34.5 | 27.7 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274807 | UNIV PK N;3U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274811 | UNIV PK N;7U | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274816 | UNIV PK N;YU | 13.8 | 222 | 56 | 43.2 | 49.6 | 43.21 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274808 | UNIV PK N;4U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274810 | UNIV PK N;6U | 13.8 | 222 | 56 | 43 | 49.4 | 43.03 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274815 | UNIV PK N;XU | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274805 | UNIV PK N;1U | 13.8 | 222 | 56 | 42.9 | 49.3 | 42.95 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274813 | UNIV PK N;9U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274812 | UNIV PK N;8U | 13.8 | 222 | 56 | 42.8 | 49.2 | 42.86 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274814 | UNIV PK N;0U | 13.8 | 222 | 56 | 42.6 | 49 | 42.68 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274809 | UNIV PK N;5U | 13.8 | 222 | 56 | 42.5 | 48.9 | 42.6 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274806 | UNIV PK N;2U | 13.8 | 222 | 56 | 42.5 | 48.8 | 42.51 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
251827 | WILLYESP | 34.5 | 212 | 76 | 0 | 6 | 0 |  |  | -0.00147 |  |  | 0.05 |  | 1 | MTX | Z1-065
251946 | 08D.CRK4 | 13.8 | 212 | 55 | 6 | 30 | 24.08 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
925972 | AC1-073 E | 138 | 201 | 74 | 0 | 5.9 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEWENERGY | AC1-073
925971 | AC1-073 C | 138 | 201 | 74 | 0 | 5.8 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | NEW | AC1-073
274742 | AURORA EC;6P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274745 | AURORA EC;9P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274743 | AURORA EC;7P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274744 | AURORA EC;8P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274741 | AURORA EC;5P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274746 | AURORA EC;0P | 13.8 | 222 | 56 | 39.2 | 45 | 39.2 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
243873 | 05FR-4G C | 0.69 | 205 | 74 | 0 | 29.1 | 23.36 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Q01 4
910542 | X3-005 E | 13.2 | 222 | 75 | 0 | 5.6 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | X3-005
274697 | ROCKY RD ;3P | 13.8 | 222 | 56 | 20.3 | 27.6 | 22.16 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274847 | GR RIDGE ;BU | 0.57 | 222 | 74 | 0 | 27.4 | 22 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | N15
251961 | 08MFTGT2 | 13.8 | 212 | 52 | 6 | 27 | 21.68 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274848 | CAMPGROVE;RU | 0.57 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | L05_CE22
274889 | BRIGHTSTK;1U | 0.7 | 222 | 74 | 0 | 26 | 20.87 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Z2-087
930041 | AB1-006 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AB1-006
247543 | V3-007 C | 345 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | V3-007
243795 | 05HDWTR1G C | 0.69 | 205 | 74 | 0 | 26 | 20.87 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | U2-090
246909 | 05MDL-1G C | 0.6 | 205 | 74 | 0 | 25.9 | 20.79 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | S06
243859 | 05FR-11G C | 0.6 | 205 | 74 | 0 | 25.7 | 20.63 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Q01 11
251960 | 08MFTGT1 | 13.8 | 212 | 52 | 6 | 25 | 20.07 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
274863 | CAYUGA RI;1U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | O51 1
274864 | CAYUGA RI;2U | 0.69 | 222 | 74 | 0 | 22.5 | 18.06 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | O51 2
276158 | O-029 C | 0.69 | 222 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | O29 1
274855 | GSG-6 ;RU | 0.69 | 222 | 74 | 5.6 | 21.9 | 17.58 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | P26
293513 | O-009 C1 | 0.69 | 222 | 74 | 0 | 20.5 | 16.46 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | O09 1
247556 | 05MDL-5G | 0.69 | 205 | 74 | 0 | 20.2 | 16.22 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | T127 5
274877 | BISHOP HL;1U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | P11 1
274878 | BISHOP HL;2U | 0.69 | 222 | 74 | 0 | 20 | 16.06 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | P11 2
274891 | OTTER CRK;1U | 0.69 | 222 | 74 | 0 | 19.5 | 15.66 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AA1-018
274856 | ECOGROVE ;U1 | 12 | 222 | 74 | 0 | 19.4 | 15.58 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | P46
274861 | TOP CROP ;1U | 0.69 | 222 | 74 | 0 | 18.4 | 14.77 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | O22 1
246976 | 05MDL-3G C | 0.69 | 205 | 74 | 4.8 | 15.3 | 12.28 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | T126 3
274858 | BIG SKY ;U2 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | P36 2
274857 | BIG SKY ;U1 | 0.69 | 222 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | P36 1
246910 | 05MDL-2G C | 12 | 205 | 74 | 0 | 15.2 | 12.2 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | T126 2
235780 | 01BEECHRIDGE | 0.69 | 201 | 74 | 0 | 15 | 12.04 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY | M24
244873 | 05WINFIELD | 69 | 205 | 60 | 0 | 14.8 | 11.88 |  |  | -0.00146 |  |  | 0.07484 |  | 1 | CAPACITY
244891 | 05LONDON | 46 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00146 |  |  | 0.07484 |  | 1 | CAPACITY
244861 | 05MARMETHY | 4 | 205 | 60 | 0 | 14.4 | 11.56 |  |  | -0.00146 |  |  | 0.07484 |  | 1 | CAPACITY
274850 | MENDOTA H;RU | 0.69 | 222 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Z1-073
276173 | Z2-081 | 138 | 222 | 2 | 0 | 13.3 | 10.68 |  |  | -0.00147 |  |  | 0.12623 |  | 1 | CAPACITY
246991 | 05WLD G1 C | 0.69 | 205 | 74 | 0 | 13.2 | 10.6 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | U3-002 1
243866 | 05FR-22G C | 0.69 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Q01 22
243864 | 05FR-21G C | 0.6 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Q01 21
251945 | 08D.CRK3 | 13.8 | 212 | 55 | 3 | 12.9 | 10.36 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247255 | 05WLD G2 C | 0.69 | 205 | 74 | 0 | 12.8 | 10.28 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | U3-002 2
243862 | 05FR-12G C | 0.6 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Q01 12
243870 | 05FR-3G C | 0.69 | 205 | 74 | 0 | 12.5 | 10.04 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Q01 3
904211 | W3-135 | 34.5 | 222 | 60 | 0 | 12.1 | 9.71 |  |  | -0.00147 |  |  | 0.07484 |  | 1 | CAPACITY
276157 | O-029 C | 0.57 | 222 | 74 | 0 | 12 | 9.64 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | O29 2
246979 | 05MDL-4G C | 0.6 | 205 | 74 | 0 | 11.8 | 9.47 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | T127 4
237511 | 01LEADS_P59 | 0.69 | 201 | 74 | 0 | 11.7 | 9.39 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY | P59
293515 | O-009 C3 | 0.57 | 222 | 74 | 0 | 11.5 | 9.23 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | O09 3
276156 | O-029 C | 0.6 | 222 | 74 | 0 | 11.1 | 8.91 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | O29 3
904201 | W3-134 | 34.5 | 222 | 60 | 0 | 10.6 | 8.51 |  |  | -0.00147 |  |  | 0.07484 |  | 1 | CAPACITY
293514 | O-009 C2 | 0.6 | 222 | 74 | 0 | 10.4 | 8.35 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | O09 2
274851 | PROVIDENC;RU | 0.69 | 222 | 74 | 0 | 10.3 | 8.27 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | O35
274871 | GR RIDGE ;2U | 0.57 | 222 | 74 | 0 | 10.2 | 8.19 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | P10
930192 | AB1-055 E | 138 | 205 | 76 | -2 | 2 | 0 |  |  | -0.00146 |  |  | 0 |  | 1 | MTX | AB1-055
250165 | 08BKJDB2 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | MTX | Y3-100
250164 | 08BKJDB1 | 138 | 212 | 76 | -2 | 2 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | MTX | Y3-099
274849 | CRESCENT ;1U | 0.6 | 222 | 74 | 0 | 10 | 8.03 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Z1-072
276162 | X1-087 | 138 | 222 | 64 | 0 | 9.6 | 7.71 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
235625 | 01BACKB | 34.5 | 201 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY | K19
235000 | N-007 C | 138 | 201 | 74 | 0 | 7.6 | 6.1 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY | N07
295108 | WESTBROOK C | 138 | 222 | 74 | 0 | 7.1 | 5.7 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | NQ71
931011 | AB1-150 C | 138 | 201 | 74 | 0 | 6.7 | 5.38 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY | AB1-150
237512 | 01ROTHROCK | 34.5 | 201 | 74 | 0 | 6.5 | 5.22 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY | U2-061
276590 | R-018 | 4.16 | 222 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
247968 | Z2-115 E | 12 | 205 | 74 | 0 | 1.25 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Z2-115
276159 | W4-082 | 138 | 222 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
247535 | R-076 | 138 | 205 | 60 | 0 | 5.5 | 4.41 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY
342550 | 4BAVARIAN LF | 138 | 320 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
251830 | BIOENGRY | 34.5 | 212 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
276164 | X3-005 C | 13.2 | 222 | 75 | 0 | 3.4 | 2.73 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | X3-005
342070 | 2PINE GROVE | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY
341584 | 2GRIFFIN | 69 | 320 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
295110 | SUBLETTE C | 138 | 222 | 74 | 0 | 3.2 | 2.57 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | NQ72
244773 | 05BRIDGE | 69 | 205 | 64 | 0 | 3.18 | 2.55 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY
341329 | 2COLESBURG | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY
342031 | 2PACTOLUS | 69 | 320 | 2 | 0 | 2.4 | 1.93 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
341200 | 2BROMLEYEK | 69 | 320 | 2 | 0 | 2 | 1.61 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
247642 | Z2-115 C | 12 | 205 | 75 | 0 | 1.25 | 1 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Z2-115
342442 | 2W GLASGOW | 69 | 320 | 2 | 0 | 1 | 0.8 |  |  | -0.00146 |  |  | 0 |  | 1 | CAPACITY
CBM West 1 | LTFEXP_CBM-W1->PJM |  |  | LTF |  | 1402 |  |  |  | -0.0015
247932 | U2-072 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | U2-072
247919 | U2-041 E | 345 | 205 | 74 | 0 | 261 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | U2-041
243441 | 05CKG2 | 26 | 205 | 45 | 600 | 1148 | 921.68 |  |  | -0.00147 |  |  | 0.01494 |  | 1 | CAPACITY
243440 | 05CKG1 | 26 | 205 | 45 | 600 | 1014.5 | 814.5 |  |  | -0.00147 |  |  | 0.01494 |  | 1 | CAPACITY
243188 | 05MLG1 | 26 | 205 | 16 | 420.7 | 770.1 | 618.28 |  |  | -0.00148 |  |  | 0.10478 |  | 1 | CAPACITY
235027 | AA2-173 OP | 500 | 201 | 58 | 0 | 664.7 | 533.66 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-173
893022 | V2-006 E | 138 | 205 | 74 | 0 | 130.5 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEWENERGY | V2-006
247911 | 05TIMB G E | 0.69 | 205 | 74 | 0 | 120.8 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | R49
270119 | AB2-067 GEN1 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-067
270120 | AB2-067 GEN2 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AB2-067
270166 | AC1-044 GEN3 | 23 | 205 | 58 | 0 | 612 | 491.35 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | AC1-044
270164 | T-131 E | 0.7 | 205 | 74 | 0 | 120 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | T131
933596 | AC2-176 E | 0.69 | 205 | 74 | 0 | 113.1 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AC2-176
247929 | S-071 E | 138 | 205 | 74 | 0 | 96 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | S71
247910 | 05BLCK-3 E | 0.69 | 205 | 74 | 0 | 94.4 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | R60 3
247908 | 05BLCK-1 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | R60 1
247909 | 05BLCK-2 E | 0.69 | 205 | 74 | 0 | 92.8 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | R60 2
247959 | V1-011 E | 34.5 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | V1-011
270143 | AA2-116_CT2 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AA2-116
270142 | AA2-116_CT1 | 25 | 205 | 58 | 0 | 376 | 301.88 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-116
247240 | 05WTRG1S | 22 | 205 | 58 | 150 | 364.8 | 292.88 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
253222 | 09TAIT E | 69 | 209 | 57 | 164 | 335 | 268.96 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
926866 | AC1-173 E | 0.65 | 205 | 74 | 0 | 66 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AC1-173
270144 | AA2-116_ST | 23.5 | 205 | 58 | 0 | 333 | 267.35 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AA2-116
235757 | 01RONCO3 | 18 | 201 | 58 | 141 | 318.8 | 255.95 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | RONCO
247204 | 05WSHG1S | 18 | 205 | 58 | 0 | 297 | 238.45 |  |  | -0.00148 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
270102 | X2-052 ST | 18 | 205 | 58 | 0 | 251 | 201.52 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | X2-052
253223 | 09TAIT W | 69 | 209 | 57 | 123 | 241 | 193.49 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
270101 | X2-052 CT2 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | X2-052
270100 | X2-052 CT1 | 18 | 205 | 58 | 0 | 232 | 186.26 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | X2-052
247236 | 05DREG1S | 18 | 205 | 58 | 150 | 225.4 | 180.96 |  |  | -0.00148 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
270165 | U1-059 E | 69 | 205 | 74 | 0 | 43.5 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEWENERGY | U1-059
247530 | 05COVRT3 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 3
247528 | 05COVRT1 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 1
247529 | 05COVRT2 | 16 | 205 | 58 | 150 | 219.8 | 176.47 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | Covert 2
253028 | 09GRNVIL | 69 | 209 | 57 | 80 | 202.9 | 162.9 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247506 | U2-041 C | 345 | 205 | 74 | 0 | 39 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | U2-041
247202 | 05WSHG1A | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00148 |  |  | 0.04435 |  | 1 | CAPACITY | WASHINGTON
247203 | 05WSHG1B | 18 | 205 | 58 | 0 | 186.5 | 149.73 |  |  | -0.00148 |  |  | 0 |  | 1 | CAPACITY | WASHINGTON
235623 | 01OGROV1 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
235624 | 01OGROV2 | 18 | 201 | 57 | 100 | 176.5 | 141.7 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
235756 | 01RONCO2 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | RONCO
235755 | 01RONCO1 | 18 | 201 | 58 | 82.5 | 175.3 | 140.74 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | RONCO
247234 | 05DREG1A | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.00148 |  |  | 0.04435 |  | 1 | CAPACITY | DRESDEN
247235 | 05DREG1B | 18 | 205 | 58 | 75 | 169 | 135.68 |  |  | -0.00148 |  |  | 0 |  | 1 | CAPACITY | DRESDEN
247238 | 05WTRG1B | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247239 | 05WTRG1C | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | WATERFORD
247237 | 05WTRG1A | 18 | 205 | 58 | 105 | 168 | 134.88 |  |  | -0.00147 |  |  | 0.04435 |  | 1 | CAPACITY | WATERFORD
253351 | AC2-067 E | 0.38 | 209 | 75 | 0 | 31 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AC2-067
247270 | 05RPMNG1 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247272 | 05RPMNG3 | 18 | 205 | 57 | 75 | 149.8 | 120.27 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247271 | 05RPMNG2 | 18 | 205 | 57 | 75 | 149.7 | 120.19 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247533 | 05COVRT6 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Covert 3
247531 | 05COVRT4 | 16.5 | 205 | 58 | 90 | 132.2 | 106.14 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Covert 1
247532 | 05COVRT5 | 16.5 | 205 | 58 | 90 | 131.2 | 105.33 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Covert 2
239069 | 02RICHG6 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.00148 |  |  | 0.08446 |  | 1 | CAPACITY
239068 | 02RICHG5 | 13.8 | 202 | 57 | 40 | 119.67 | 96.08 |  |  | -0.00148 |  |  | 0.08446 |  | 1 | CAPACITY
239067 | 02RICHG4 | 13.8 | 202 | 57 | 40 | 119.66 | 96.07 |  |  | -0.00148 |  |  | 0.08446 |  | 1 | CAPACITY
902531 | W2-040 C | 69 | 209 | 75 | 0 | 20 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEW | W2-040
253097 | 09YANKEE | 69 | 209 | 55 | 8.4 | 100.5 | 80.69 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
893021 | V2-006 C | 138 | 205 | 74 | 0 | 19.5 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEWENERGY | V2-006
927184 | AC1-212 GENE | 0.48 | 209 | 76 | -18 | 18 | 0 |  |  | -0.00147 |  |  | 0.05 |  | 1 | MTX | AC1-212
253344 | AC1-166 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AC1-166
253339 | AC1-165 E | 0.36 | 209 | 75 | 0 | 16.3 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AC1-165
270160 | DARBY CT5 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
270157 | DARBY CT2 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
270156 | DARBY CT1 | 13.8 | 205 | 57 | 38 | 82 | 65.83 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247942 | W1-056 E | 69 | 205 | 74 | 0 | 16 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEWENERGY | W1-056
270158 | DARBY CT3 | 13.8 | 205 | 57 | 38 | 81 | 65.03 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
253326 | AC1-069 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AC1-069
253334 | AC1-068 E | 0.36 | 209 | 75 | 0 | 15.9 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AC1-068
270159 | DARBY CT4 | 13.8 | 205 | 57 | 38 | 80 | 64.23 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
270161 | DARBY CT6 | 13.8 | 205 | 57 | 38 | 79 | 63.43 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
902532 | W2-040 E | 69 | 209 | 75 | 0 | 12.4 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | W2-040
247948 | V3-028 E | 345 | 205 | 75 | 0 | 12.4 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | V3-028
247295 | 05KEY G4 | 13.8 | 205 | 57 | 20 | 59.9 | 48.09 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247294 | 05KEY G3 | 13.8 | 205 | 57 | 20 | 59.7 | 47.93 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247293 | 05KEY G2 | 13.8 | 205 | 57 | 20 | 58.1 | 46.65 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247292 | 05KEY G1 | 13.8 | 205 | 57 | 20 | 57.8 | 46.41 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
247522 | U1-059 C | 69 | 205 | 74 | 0 | 9.6 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEWENERGY | U1-059
247540 | U2-072 C | 345 | 205 | 74 | 0 | 39 | 31.31 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | U2-072
247549 | V3-028 C | 345 | 205 | 75 | 0 | 7.6 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | V3-028
930262 | AB1-065 E | 34.5 | 201 | 75 | 0 | 6.8 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
253325 | AC1-069 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AC1-069
253333 | AC1-068 C | 0.36 | 209 | 75 | 0 | 34 | 27.3 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AC1-068
253338 | AC1-165 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AC1-165
253343 | AC1-166 C | 0.36 | 209 | 75 | 0 | 33.6 | 26.98 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AC1-166
932312 | AC2-045 E | 69 | 205 | 75 | 0 | 6.2 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | AC2-045
247521 | T131 | 0.69 | 205 | 74 | 22.4 | 30 | 24.08 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | T131
253349 | AC2-067 C | 0.38 | 209 | 75 | 0 | 26.5 | 21.28 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AC2-067
235571 | 01LAKEL2 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00148 |  |  | 0.07484 |  | 1 | CAPACITY
235570 | 01LAKEL1 | 11 | 201 | 60 | 16 | 26 | 20.87 |  |  | -0.00148 |  |  | 0.07484 |  | 1 | CAPACITY
247536 | 05BLUFF P WF | 138 | 205 | 74 | 0 | 24 | 19.27 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | S71
246953 | 05TIMB G C | 0.69 | 205 | 74 | 0 | 22.9 | 18.39 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | R49
239065 | 02RICHG2&3 | 13.2 | 202 | 55 | 10 | 22 | 17.66 |  |  | -0.00148 |  |  | 0.08446 |  | 1 | CAPACITY
236841 | 01S70BUS1 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00147 |  |  | 0.07484 |  | 1 | CAPACITY
236842 | 01S70BUS2 | 6.9 | 201 | 60 | 2.4 | 21.6 | 17.34 |  |  | -0.00147 |  |  | 0.07484 |  | 1 | CAPACITY
235013 | 01AB1-065 C | 34.5 | 201 | 75 | 0 | 4.1 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEWENERGY | AB1-065
247965 | Y1-063 E | 34.5 | 205 | 76 | -4 | 4 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | MTX
204646 | 27HAM CT | 13.8 | 227 | 56 | 3 | 19.6 | 15.74 |  |  | -0.00148 |  |  | 0.08446 |  | 1 | CAPACITY
932311 | AC2-045 C | 69 | 205 | 75 | 0 | 3.8 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEW | AC2-045
253060 | 09OHH W. | 69 | 209 | 56 | 22.9 | 26.3 | 22.91 |  |  | -0.00147 |  |  | 0.08446 |  | 1 | CAPACITY
933594 | AC2-176 C | 0.69 | 205 | 74 | 0 | 16.9 | 13.57 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AC2-176
246938 | 05BLCK-3 C | 0.69 | 205 | 74 | 0 | 16.5 | 13.25 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | R60 3
246937 | 05BLCK-2 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | R60 2
246936 | 05BLCK-1 C | 0.69 | 205 | 74 | 0 | 16.4 | 13.17 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | R60 1
247607 | V1-011 C | 34.5 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | V1-011
253261 | 09MON D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00147 |  |  | 0.12623 |  | 1 | CAPACITY
253265 | 09SID D | 4.2 | 209 | 65 | 0 | 12 | 9.64 |  |  | -0.00147 |  |  | 0.12623 |  | 1 | CAPACITY
247966 | 05WTRV SLR E | 138 | 205 | 75 | 0 | 2.3 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Z2-113
294740 | P44 | 138 | 205 | 65 | 0 | 2.3 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | ENERGY
239064 | 02RICHG1 | 13.2 | 202 | 20 | 5 | 11 | 8.83 |  |  | -0.00148 |  |  | 0.10478 |  | 1 | CAPACITY
253263 | 09TAIT D | 4.2 | 209 | 65 | 0 | 10 | 8.03 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
926865 | AC1-173 C | 0.65 | 205 | 75 | 0 | 9.9 | 7.95 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AC1-173
AC1-212 | BATTERY_AC1-212->PJM |  |  | LTF |  | 1.9 |  |  |  | -0.0015
904722 | V4-073 E | 69 | 209 | 75 | 0 | 1.55 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | V4-073
247969 | Z2-116 E | 138 | 205 | 76 | 0 | 1.3 | 0 |  |  | -0.00147 |  |  | 0 |  | 1 | NEWENERGY | Z2-116
245417 | 05SOMRSET8 | 69 | 205 | 64 | 0 | 6.4 | 5.14 |  |  | -0.00148 |  |  | 0 |  | 1 | CAPACITY
243071 | 05BERRINSP G | 69 | 205 | 60 | 0 | 6 | 4.82 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
246422 | 05MAYFLWER | 69 | 205 | 64 | 0 | 5.8 | 4.66 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
247620 | Y3-023 | 138 | 205 | 64 | 0 | 4.5 | 3.61 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
245413 | 05S FULTHA | 69 | 205 | 65 | 0 | 0.85 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | ENERGY
246416 | 05TWIN BRCH1 | 34.5 | 205 | 60 | 0 | 3.9 | 3.13 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
247604 | X1-042 | 12 | 205 | 64 | 0 | 3 | 2.41 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
246431 | 05BUCHANAN | 34.5 | 205 | 60 | 0 | 2.8 | 2.25 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
246397 | 05ELKHART HY | 34.5 | 205 | 64 | 0 | 2.6 | 2.09 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
247555 | W1-056 C | 69 | 205 | 74 | 0 | 2.4 | 1.93 |  |  | -0.00148 |  |  | 0 |  | 1 | CAPACITY | W1-056
244412 | 05WTRV SLR C | 138 | 205 | 75 | 0 | 2.3 | 1.85 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Z2-113
247621 | Y3-024 | 69 | 205 | 64 | 0 | 2.2 | 1.76 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
927183 | AC1-212 GENC | 0.48 | 209 | 76 | -1.9 | 1.9 | 1.53 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | AC1-212
246536 | 05MOTTVILL | 34.5 | 205 | 60 | 0 | 1.5 | 1.2 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY
247643 | Z2-116 C | 138 | 205 | 75 | 0 | 1.3 | 1.04 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | Z2-116
904721 | V4-073 C | 69 | 209 | 75 | 0 | 0.95 | 0.76 |  |  | -0.00147 |  |  | 0 |  | 1 | CAPACITY | V4-073
237076 | AB1-069 ST1 | 22 | 201 | 58 | 0 | 419.4 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEW | AB1-069
237074 | AB1-069 CT1 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00148 |  |  | 0.04435 |  | 1 | NEW | AB1-069
237075 | AB1-069 CT2 | 19 | 201 | 58 | 0 | 265.3 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEW | AB1-069
247947 | V4-010 E | 138 | 205 | 74 | 0 | 174 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEWENERGY | V4-010
243189 | 05MLG2 | 26 | 205 | 16 | 448.6 | 790.2 | 634.42 |  |  | -0.00148 |  |  | 0.10478 |  | 1 | CAPACITY
238670 | 02DVBSG1 | 25 | 202 | 40 | 779.5 | 896 | 780.51 |  |  | -0.00149 |  |  | 0.01494 |  | 1 | CAPACITY
924440 | AB2-093 CT | 24 | 205 | 58 | 0 | 485 | 389.39 |  |  | -0.00148 |  |  | 0.04435 |  | 1 | CAPACITY | AB2-093
247940 | U4-028 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEWENERGY | U4-028
247941 | U4-029 E | 138 | 205 | 74 | 0 | 87 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEWENERGY | U4-029
238603 | 02FRMENG 3 | 23 | 202 | 58 | 206 | 364.2 | 292.4 |  |  | -0.00149 |  |  | 0 |  | 1 | CAPACITY | FREMONT
241900 | 02Y1-069_1S | 19 | 202 | 58 | 0 | 326.2 | 261.89 |  |  | -0.00148 |  |  | 0 |  | 1 | CAPACITY | OREGON
241948 | AB1-107 ST1 | 19 | 202 | 58 | 0 | 309.8 | 248.73 |  |  | -0.00148 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241947 | AB1-107 CT2 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00148 |  |  | 0 |  | 1 | CAPACITY | AB1-107
241946 | AB1-107 CT1 | 20 | 202 | 58 | 0 | 275.1 | 220.87 |  |  | -0.00148 |  |  | 0.04435 |  | 1 | CAPACITY | AB1-107
241898 | 02Y1-069_1A | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00148 |  |  | 0.04435 |  | 1 | CAPACITY | OREGON
241899 | 02Y1-069_1B | 19 | 202 | 58 | 0 | 250.7 | 201.27 |  |  | -0.00148 |  |  | 0 |  | 1 | CAPACITY | OREGON
238601 | 02FRMENG 1 | 18 | 202 | 58 | 104 | 170 | 136.49 |  |  | -0.00149 |  |  | 0.04435 |  | 1 | CAPACITY | FREMONT
238602 | 02FRMENG 2 | 18 | 202 | 58 | 104 | 166.4 | 133.6 |  |  | -0.00149 |  |  | 0 |  | 1 | CAPACITY | FREMONT
238885 | 02LEMOG1 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00148 |  |  | 0.10478 |  | 1 | CAPACITY
238886 | 02LEMOG2 | 18 | 202 | 30 | 90 | 160 | 128.46 |  |  | -0.00148 |  |  | 0.10478 |  | 1 | CAPACITY
238888 | 02LEMOG4 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00148 |  |  | 0.08446 |  | 1 | CAPACITY
238887 | 02LEMOG3 | 18 | 202 | 57 | 90 | 160 | 128.46 |  |  | -0.00148 |  |  | 0.08446 |  | 1 | CAPACITY
238564 | 02BAYSG1 | 18 | 202 | 12 | 75 | 136 | 109.19 |  |  | -0.00148 |  |  | 0.10478 |  | 1 | CAPACITY
247548 | V4-010 C | 138 | 205 | 74 | 0 | 26 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEW | V4-010
240997 | 02BG10 | 69 | 202 | 75 | 0 | 20 | 0 |  |  | -0.00148 |  |  | 0 |  | 1 | NEWENERGY
235615 | 01GANS 8 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00148 |  |  | 0.08446 |  | 1 | CAPACITY
235616 | 01GANS 9 | 13.8 | 201 | 53 | 8 | 44 | 35.33 |  |  | -0.00148 |  |  | 0.08446 |  | 1 | CAPACITY
901242 | W1-045 E OP1 | 23 | 226 | 75 | 0 | 8.37 | 0 |  |  | -0.00149 |  |  | 0 |  | 1 | NEWENERGY | W1-045
204648 | 27MOUNT CT | 13.8 | 227 | 56 | 6 | 39.5 | 31.71 |  |  | -0.00149 |  |  | 0.08446 |  | 1 | CAPACITY
204650 | 27TOLNA CT | 13.8 | 227 | 56 | 6 | 38.7 | 31.07 |  |  | -0.00149 |  |  | 0.08446 |  | 1 | CAPACITY
204639 | 27GLATFLTR | 13.2 | 227 | 11 | 0 | 35 | 28.1 |  |  | -0.00149 |  |  | 0.10478 |  | 1 | CAPACITY
936011 | AD2-002_GEN | 13.8 | 201 | 29 | 0 | 20 | 16.06 |  |  | -0.00149 |  |  | 0.10478 |  | 1 | CAPACITY
235344 | 01HANNIB | 138 | 201 | 60 | 0.5 | 19 | 15.25 |  |  | -0.00148 |  |  | 0.07484 |  | 1 | CAPACITY
239293 | 02BS-PKR | 4.16 | 202 | 20 | 2 | 13.3 | 10.68 |  |  | -0.00148 |  |  | 0.10478 |  | 1 | CAPACITY
247551 | U4-028 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00148 |  |  | 0 |  | 1 | NEW | U4-028
247552 | U4-029 C | 138 | 205 | 74 | 0 | 13 | 10.44 |  |  | -0.00148 |  |  | 0 |  | 1 | NEW | U4-029
239202 | 02STRYCT | 13.2 | 202 | 20 | 5 | 12.7 | 10.19 |  |  | -0.00148 |  |  | 0.10478 |  | 1 | CAPACITY
200870 | 26C_T85_W218 | 23 | 226 | 64 | 3.2 | 5.6 | 4.5 |  |  | -0.00149 |  |  | 0 |  | 1 | CAPACITY
237505 | 01ELLIOTTS | 34.5 | 201 | 74 | 0 | 5.5 | 4.41 |  |  | -0.00148 |  |  | 0 |  | 1 | CAPACITY | N32
203905 | 26W1-045 C | 23 | 226 | 75 | 0 | 5.13 | 4.12 |  |  | -0.00149 |  |  | 0 |  | 1 | CAPACITY | W1-045
237082 | AA2-121 | 345 | 201 | 58 | 0 | 830 | 666.37 |  |  | -0.0015 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-121
243185 | 05CDG3 | 26 | 205 | 16 | 350 | 620.4 | 498.09 |  |  | -0.00149 |  |  | 0.10478 |  | 1 | CAPACITY
243190 | 05CDG1 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00149 |  |  | 0.10478 |  | 1 | CAPACITY
243191 | 05CDG2 | 24 | 205 | 15 | 320 | 585 | 469.67 |  |  | -0.00149 |  |  | 0.10478 |  | 1 | CAPACITY
270105 | Y2-050_ST1 | 18 | 205 | 58 | 58.4 | 272 | 218.38 |  |  | -0.00149 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270104 | Y2-050_CT2 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00149 |  |  | 0 |  | 1 | CAPACITY | Y2-050
270103 | Y2-050_CT1 | 18 | 205 | 58 | 71.6 | 200 | 160.57 |  |  | -0.00149 |  |  | 0.04435 |  | 1 | CAPACITY | Y2-050
239172 | 02WLORG-3 | 13.8 | 202 | 57 | 45 | 77.5 | 62.22 |  |  | -0.0015 |  |  | 0.08446 |  | 1 | CAPACITY
239175 | 02WLORG-6 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.0015 |  |  | 0.08446 |  | 1 | CAPACITY
239174 | 02WLORG-5 | 13.8 | 202 | 57 | 45 | 76.2 | 61.18 |  |  | -0.0015 |  |  | 0.08446 |  | 1 | CAPACITY
239173 | 02WLORG-4 | 13.8 | 202 | 57 | 45 | 75.8 | 60.86 |  |  | -0.0015 |  |  | 0.08446 |  | 1 | CAPACITY
239171 | 02WLORG-2 | 13.8 | 202 | 57 | 45 | 75.1 | 60.29 |  |  | -0.0015 |  |  | 0.08446 |  | 1 | CAPACITY
238572 | 02BEAVGB | 13.8 | 202 | 65 | 5 | 51.1 | 41.03 |  |  | -0.0015 |  |  | 0.12623 |  | 1 | CAPACITY
238571 | 02BEAVGA | 13.8 | 202 | 65 | 5 | 49.6 | 39.82 |  |  | -0.0015 |  |  | 0.12623 |  | 1 | CAPACITY
204638 | 27CAT TRAC | 13.2 | 227 | 58 | 0 | 32.3 | 25.93 |  |  | -0.00149 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
204642 | 27YK SOLID | 13.8 | 227 | 1 | 0 | 30 | 24.08 |  |  | -0.0015 |  |  | 0.10478 |  | 1 | CAPACITY
204555 | 27QUEEN ST | 115 | 227 | 74 | 0 | 5 | 0 |  |  | -0.00149 |  |  | 0 |  | 1 | NEWENERGY
241908 | 02LLF_W4-004 | 4.16 | 202 | 64 | 0.6 | 14 | 11.24 |  |  | -0.0015 |  |  | 0.12623 |  | 1 | CAPACITY
204706 | 27CAT TRC2 | 13.2 | 227 | 58 | 0 | 13.9 | 11.16 |  |  | -0.00149 |  |  | 0.04435 |  | 1 | CAPACITY | CAT TRACTOR NUG
200841 | 26DEEPCRK2 | 11.5 | 226 | 60 | 1.6 | 10 | 8.03 |  |  | -0.00149 |  |  | 0 |  | 1 | CAPACITY
200840 | 26DEEPCRK1 | 11.5 | 226 | 60 | 2 | 9.9 | 7.95 |  |  | -0.00149 |  |  | 0 |  | 1 | CAPACITY
236578 | 01GRABLE_P34 | 25 | 201 | 64 | 0 | 4 | 3.21 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY
241912 | 02EL_AA1-006 | 69 | 202 | 54 | 0 | 2.3 | 1.85 |  |  | -0.00149 |  |  | 0 |  | 1 | CAPACITY
253900 | 15BVRVL1 | 22 | 215 | 44 | 843.9 | 970 | 844.97 |  |  | -0.0015 |  |  | 0.01494 |  | 1 | CAPACITY
238555 | 02AVONG9 | 20 | 202 | 16 | 240 | 627.1 | 503.47 |  |  | -0.0015 |  |  | 0.04435 |  | 1 | CAPACITY | AVON LAKE
239090 | 02SAMMG6 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.0015 |  |  | 0.10478 |  | 1 | CAPACITY
239091 | 02SAMMG7 | 20 | 202 | 16 | 275 | 600 | 481.71 |  |  | -0.0015 |  |  | 0.10478 |  | 1 | CAPACITY
253901 | 15BVRVL2 | 22 | 215 | 44 | 782.4 | 899.3 | 783.39 |  |  | -0.0015 |  |  | 0.01494 |  | 1 | CAPACITY
254063 | 15CHSWK1 | 24 | 215 | 15 | 200 | 567.5 | 455.62 |  |  | -0.0015 |  |  | 0.10478 |  | 1 | CAPACITY
241939 | AA1-044 ST | 21 | 202 | 58 | 0 | 410 | 329.17 |  |  | -0.00151 |  |  | 0 |  | 1 | CAPACITY | AA1-044
235084 | T174 ST | 20 | 201 | 58 | 215 | 326 | 261.73 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | T-174
241943 | AA1-123_CT1 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | AA1-123
241944 | AA1-123_CT2 | 25 | 202 | 58 | 0 | 312.3 | 250.73 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | AA1-123
235082 | T174 CT1 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.0015 |  |  | 0.04435 |  | 1 | CAPACITY | T-174
235083 | T174 CT2 | 20 | 201 | 58 | 185 | 307 | 246.48 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | T-174
240072 | 02Z2-028_1S | 19 | 202 | 58 | 0 | 300.6 | 241.34 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | Z2-028
241937 | AA1-044 CT1 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00151 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-044
241938 | AA1-044 CT2 | 21 | 202 | 58 | 0 | 295 | 236.84 |  |  | -0.00151 |  |  | 0 |  | 1 | CAPACITY | AA1-044
239089 | 02SAMMG5 | 24 | 202 | 13 | 152 | 291.3 | 233.87 |  |  | -0.0015 |  |  | 0.10478 |  | 1 | CAPACITY
240070 | 02Z2-028_1A | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.0015 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-028
240071 | 02Z2-028_1B | 19 | 202 | 58 | 0 | 281.7 | 226.16 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | Z2-028
241940 | AA1-123_ST1 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.0015 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-123
241941 | AA1-123_ST2 | 18 | 202 | 58 | 0 | 240.2 | 192.85 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | AA1-123
239024 | 02NWCAG5 | 16.5 | 202 | 58 | 23 | 141 | 113.2 |  |  | -0.00151 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
253972 | 15BI4 | 13.8 | 215 | 58 | 40 | 101.6 | 81.57 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | BRUNOT ISLAND
253970 | 15BI2 | 13.8 | 215 | 58 | 60 | 96.2 | 77.24 |  |  | -0.0015 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
239023 | 02NWCAG4 | 14.4 | 202 | 58 | 20 | 92 | 73.86 |  |  | -0.00151 |  |  | 0 |  | 1 | CAPACITY | NEW CASTLE
240077 | AB1-015 E | 138 | 202 | 56 | 0 | 16.5 | 0 |  |  | -0.0015 |  |  | 0.10478 |  | 1 | ENERGY
254302 | Y3-103-STG2 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254301 | Y3-103-STG1 | 13.8 | 215 | 58 | 0 | 54.5 | 43.76 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | Y3-103
253971 | 15BI3 | 13.8 | 215 | 58 | 30 | 48.7 | 39.1 |  |  | -0.0015 |  |  | 0.04435 |  | 1 | CAPACITY | BRUNOT ISLAND
933532 | AC2-168 E | 138 | 215 | 75 | 0 | 7.3 | 0 |  |  | -0.0015 |  |  | 0 |  | 1 | NEWENERGY | AC2-168
254300 | Y3-103-CTG3 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | Y3-103
254250 | Y3-103-CTG1 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.0015 |  |  | 0.04435 |  | 1 | CAPACITY | Y3-103
254251 | Y3-103-CTG2 | 13.8 | 215 | 58 | 0 | 32 | 25.69 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | Y3-103
239214 | 02NILE-A | 13.8 | 202 | 65 | 3 | 24.6 | 19.75 |  |  | -0.0015 |  |  | 0.12623 |  | 1 | CAPACITY
239267 | 02AVG10 | 13.8 | 202 | 65 | 2 | 21 | 16.86 |  |  | -0.0015 |  |  | 0.12623 |  | 1 | CAPACITY
240195 | 02CARBONLM | 69 | 202 | 64 | 0.6 | 20.5 | 16.46 |  |  | -0.00151 |  |  | 0.12623 |  | 1 | CAPACITY
253969 | 15BI1 | 13.8 | 215 | 55 | 2 | 18.1 | 14.53 |  |  | -0.0015 |  |  | 0.08446 |  | 1 | CAPACITY
933531 | AC2-168 C | 138 | 215 | 75 | 0 | 7.55 | 6.06 |  |  | -0.0015 |  |  | 0 |  | 1 | CAPACITY | AC2-168
240213 | 02MHNGLFH093 | 69 | 202 | 64 | 1 | 4 | 3.21 |  |  | -0.00151 |  |  | 0 |  | 1 | CAPACITY
238995 | 02NCUNTD | 23 | 202 | 65 | 0 | 2.5 | 2.01 |  |  | -0.00151 |  |  | 0 |  | 1 | CAPACITY
236523 | 01WDPWR_K20 | 25 | 201 | 74 | 0 | 1.7 | 1.37 |  |  | -0.00151 |  |  | 0 |  | 1 | CAPACITY | K20
920571 | AA2-161 C | 138 | 201 | 58 | 0 | 513 | 411.86 |  |  | -0.00151 |  |  | 0.04435 |  | 1 | NEW | AA2-161
200105 | AA1-076 ST | 23.5 | 225 | 58 | 0 | 440 | 353.26 |  |  | -0.00152 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200104 | AA1-076 CT2 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00152 |  |  | 0 |  | 1 | CAPACITY | AA1-076
200103 | AA1-076 CT1 | 25 | 225 | 58 | 0 | 330 | 264.94 |  |  | -0.00152 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-076
239022 | 02NWCAG3 | 14.4 | 202 | 58 | 20 | 92.3 | 74.11 |  |  | -0.00151 |  |  | 0.04435 |  | 1 | CAPACITY | NEW CASTLE
916032 | Z1-035 E | 69 | 202 | 74 | 0 | 15.66 | 0 |  |  | -0.00151 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
905502 | W4-060 E OP1 | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00152 |  |  | 0 |  | 1 | NEWENERGY | W4-060
241916 | 02Z1-035 | 69 | 202 | 74 | 0 | 2.34 | 0 |  |  | -0.00151 |  |  | 0 |  | 1 | NEWENERGY | Z1-035
207169 | 28W4-060COL | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.00152 |  |  | 0 |  | 1 | CAPACITY | W4-060
204660 | 27YK H STA | 115 | 227 | 60 | 16.5 | 19 | 16.55 |  |  | -0.00152 |  |  | 0.07484 |  | 1 | CAPACITY
200813 | 26YOUGH | 4 | 226 | 60 | 1 | 6 | 4.82 |  |  | -0.00153 |  |  | 0 |  | 1 | CAPACITY
239035 | 02PERRG1 | 22 | 202 | 41 | 1084.9 | 1247 | 1086.27 |  |  | -0.00153 |  |  | 0.01494 |  | 1 | CAPACITY
913142 | Y1-033 E OP1 | 115 | 226 | 74 | 0 | 34.02 | 0 |  |  | -0.00154 |  |  | 0 |  | 1 | NEWENERGY | Y1-033
202652 | 26RGH_Y1-033 | 0.69 | 226 | 74 | 0 | 5 | 4.01 |  |  | -0.00154 |  |  | 0 |  | 1 | CAPACITY | Y1-033
240358 | 02GEN-Y1-012 | 36 | 202 | 64 | 0 | 3.8 | 3.05 |  |  | -0.00154 |  |  | 0 |  | 1 | CAPACITY
200032 | KEYS G1 | 20 | 226 | 17 | 434 | 853.3 | 685.08 |  |  | -0.00155 |  |  | 0.10478 |  | 1 | CAPACITY | Keys1
200033 | KEYS G2 | 20 | 226 | 17 | 434 | 853.1 | 684.92 |  |  | -0.00155 |  |  | 0.10478 |  | 1 | CAPACITY | Keys2
200030 | CONE G1 | 22 | 226 | 17 | 400 | 850.6 | 682.91 |  |  | -0.00154 |  |  | 0.10478 |  | 1 | CAPACITY | Cone1
200031 | CONE G2 | 22 | 226 | 17 | 400 | 850 | 682.43 |  |  | -0.00154 |  |  | 0.10478 |  | 1 | CAPACITY | Cone2
237094 | AD2-114 G1 | 24 | 201 | 58 | 0 | 400 | 321.14 |  |  | -0.00155 |  |  | 0.04435 |  | 1 | CAPACITY | AD2-114
235620 | 01SBEND2 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00155 |  |  | 0.08446 |  | 1 | CAPACITY
235621 | 01SBEND3 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00155 |  |  | 0.08446 |  | 1 | CAPACITY
235622 | 01SBEND4 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00155 |  |  | 0.08446 |  | 1 | CAPACITY
235619 | 01SBEND1 | 18 | 201 | 57 | 90 | 192.5 | 154.55 |  |  | -0.00155 |  |  | 0.08446 |  | 1 | CAPACITY
235614 | 01SPRGD5 | 16.5 | 201 | 58 | 140 | 182.2 | 146.28 |  |  | -0.00154 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235612 | 01SPRGD3 | 16.5 | 201 | 58 | 118.7 | 175.2 | 140.66 |  |  | -0.00154 |  |  | 0.04435 |  | 1 | CAPACITY | AE SPRINGDALE
235613 | 01SPRGD4 | 16.5 | 201 | 58 | 118.7 | 172.2 | 138.25 |  |  | -0.00154 |  |  | 0 |  | 1 | CAPACITY | AE SPRINGDALE
235610 | 01SPRGD1 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.00154 |  |  | 0.08446 |  | 1 | CAPACITY
235611 | 01SPRGD2 | 13.8 | 201 | 53 | 6.9 | 48 | 38.54 |  |  | -0.00154 |  |  | 0.08446 |  | 1 | CAPACITY
208902 | BRIS G3 | 24 | 229 | 16 | 334 | 749 | 601.34 |  |  | -0.00156 |  |  | 0.10478 |  | 1 | CAPACITY
208901 | BRIS G2 | 18 | 229 | 14 | 138 | 366.1 | 293.93 |  |  | -0.00156 |  |  | 0.10478 |  | 1 | CAPACITY | Bris2
208900 | BRIS G1 | 18 | 229 | 14 | 138 | 309.4 | 248.4 |  |  | -0.00156 |  |  | 0.10478 |  | 1 | CAPACITY | Bris1
235776 | 01AL DAM5 | 4.16 | 201 | 60 | 0 | 6.9 | 5.54 |  |  | -0.00155 |  |  | 0 |  | 1 | CAPACITY
292350 | K-023 | 0.6 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00156 |  |  | 0 |  | 1 | NEWENERGY | K23
292542 | L-013 1 | 0.57 | 226 | 74 | 0 | 32 | 0 |  |  | -0.00156 |  |  | 0 |  | 1 | NEWENERGY | L13
293902 | O-048 E | 24.9 | 226 | 74 | 0 | 28.8 | 0 |  |  | -0.00156 |  |  | 0 |  | 1 | NEWENERGY | O48
203915 | 26BF_Z2-108 | 0.45 | 226 | 76 | -18 | 18 | 0 |  |  | -0.00156 |  |  | 0.05 |  | 1 | MTX
206755 | 28CPH_W2-050 | 34.5 | 228 | 75 | 0 | 8 | 0 |  |  | -0.00156 |  |  | 0 |  | 1 | NEWENERGY | W2-050
200835 | 26ARN_Z1-066 | 25 | 226 | 76 | -8 | 8 | 0 |  |  | -0.00156 |  |  | 0.05 |  | 1 | MTX
293432 | R-040 E | 25 | 226 | 74 | 0 | 1.8 | 0 |  |  | -0.00156 |  |  | 0 |  | 1 | NEWENERGY | R40
200892 | 26LOOKOUT | 24.9 | 226 | 74 | 0 | 6.3 | 5.06 |  |  | -0.00156 |  |  | 0 |  | 1 | CAPACITY | O48
200891 | 26CSLMN_L13 | 0.57 | 226 | 74 | 0 | 5.9 | 4.74 |  |  | -0.00156 |  |  | 0 |  | 1 | CAPACITY | L13
200890 | 26BF_G21_K23 | 0.6 | 226 | 74 | 0 | 5.1 | 4.09 |  |  | -0.00156 |  |  | 0 |  | 1 | CAPACITY | K23
235134 | 01AL&D6 | 138 | 201 | 60 | 0 | 7.6 | 6.1 |  |  | -0.00157 |  |  | 0 |  | 1 | CAPACITY
202160 | 26CON.GEN2 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00158 |  |  | 0 |  | 1 | CAPACITY
200906 | 26KEYSTN#3 | 20 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.00158 |  |  | 0.12623 |  | 1 | CAPACITY
235030 | 01MHNG-T155 | 25 | 201 | 60 | 0 | 6.8 | 5.46 |  |  | -0.00159 |  |  | 0 |  | 1 | CAPACITY
202225 | 26SCI_S29B | 23 | 226 | 64 | 0 | 1.8 | 1.45 |  |  | -0.00158 |  |  | 0 |  | 1 | CAPACITY
200834 | 26SW_E13_K22 | 23 | 226 | 74 | 0 | 0.9 | 0.72 |  |  | -0.00158 |  |  | 0 |  | 1 | CAPACITY | K22
294903 | P-060 E | 34.5 | 226 | 74 | 0 | 42 | 0 |  |  | -0.00159 |  |  | 0 |  | 1 | NEWENERGY | P60
200864 | K-013 E | 34.5 | 226 | 74 | 0 | 23.2 | 0 |  |  | -0.0016 |  |  | 0 |  | 1 | NEWENERGY | K13
208947 | WSHO CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00159 |  |  | 0.08446 |  | 1 | CAPACITY
200636 | 26IUP CO-G | 23 | 226 | 65 | -0.5 | 13 | 10.44 |  |  | -0.0016 |  |  | 0.12623 |  | 1 | CAPACITY
200889 | 26STNY CRK | 34.5 | 226 | 74 | 0 | 8.5 | 6.82 |  |  | -0.00159 |  |  | 0 |  | 1 | CAPACITY | P60
200846 | 26FORWARD | 34.5 | 226 | 74 | 0 | 3.2 | 2.57 |  |  | -0.0016 |  |  | 0 |  | 1 | CAPACITY | K13
202158 | 26CON.GEN1 | 4 | 226 | 60 | 0 | 2 | 1.61 |  |  | -0.00159 |  |  | 0 |  | 1 | CAPACITY
200833 | 26SEWRDB34 | 22 | 226 | 15 | 239 | 525.7 | 422.06 |  |  | -0.0016 |  |  | 0.10478 |  | 1 | CAPACITY
296332 | R-032 E | 34.5 | 226 | 74 | 0 | 60 | 0 |  |  | -0.00161 |  |  | 0 |  | 1 | NEWENERGY | R32
293603 | O-018 E | 34.5 | 226 | 74 | 0 | 52 | 0 |  |  | -0.00161 |  |  | 0 |  | 1 | NEWENERGY | O18
200662 | 26SCRUB GR | 13.8 | 226 | 11 | 40.4 | 85 | 68.24 |  |  | -0.00161 |  |  | 0.10478 |  | 1 | CAPACITY
200829 | 26HNSMLK 2 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00161 |  |  | 0.08446 |  | 1 | CAPACITY
200830 | 26HNSMLK 3 | 13.8 | 226 | 57 | 20 | 53.5 | 42.95 |  |  | -0.00161 |  |  | 0.08446 |  | 1 | CAPACITY
200831 | 26HNSMLK 4 | 13.8 | 226 | 57 | 17 | 53.5 | 42.95 |  |  | -0.00161 |  |  | 0.08446 |  | 1 | CAPACITY
200832 | 26HNSMLK 5 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00161 |  |  | 0.08446 |  | 1 | CAPACITY
200828 | 26HNSMLK 1 | 13.8 | 226 | 57 | 22 | 53.5 | 42.95 |  |  | -0.00161 |  |  | 0.08446 |  | 1 | CAPACITY
200608 | 26PINEY #1 | 11.5 | 226 | 60 | 4.8 | 30.2 | 24.24 |  |  | -0.00161 |  |  | 0.07484 |  | 1 | CAPACITY
200925 | 26R32 | 34.5 | 226 | 74 | 0 | 12.7 | 10.19 |  |  | -0.00161 |  |  | 0 |  | 1 | CAPACITY | R32
200794 | 26CONEMAGH | 115 | 226 | 65 | 0 | 11 | 8.83 |  |  | -0.0016 |  |  | 0.12623 |  | 1 | CAPACITY
200888 | 26HIGHLAND | 34.5 | 226 | 74 | 0 | 8.1 | 6.5 |  |  | -0.00161 |  |  | 0 |  | 1 | CAPACITY | O18
200837 | 26HOMER C1 | 20 | 226 | 16 | 350 | 620 | 497.77 |  |  | -0.00162 |  |  | 0.10478 |  | 1 | CAPACITY
293301 | N-039 E | 0.69 | 226 | 74 | 0 | 64 | 0 |  |  | -0.00162 |  |  | 0 |  | 1 | NEWENERGY | N39
294515 | O38_P22 | 0.69 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00162 |  |  | 0 |  | 1 | NEWENERGY | O38
293393 | V3-030E | 0.69 | 226 | 74 | 0 | 28.2 | 0 |  |  | -0.00162 |  |  | 0 |  | 1 | NEWENERGY | V3-030
200805 | 26COLVER13 | 13.2 | 226 | 12 | 77 | 110 | 88.31 |  |  | -0.00161 |  |  | 0.10478 |  | 1 | CAPACITY
208922 | DART W1-054 | 12.5 | 229 | 64 | 0 | 11.4 | 0 |  |  | -0.00162 |  |  | 0.12623 |  | 1 | ENERGY
208942 | HARR CT | 12.5 | 229 | 55 | 0 | 42 | 33.72 |  |  | -0.00162 |  |  | 0.08446 |  | 1 | CAPACITY
200809 | 26SITHE | 138 | 226 | 15 | 0 | 36 | 28.9 |  |  | -0.00162 |  |  | 0.10478 |  | 1 | CAPACITY
209008 | PAXT IPP | 13.8 | 229 | 65 | 0 | 12 | 9.64 |  |  | -0.00162 |  |  | 0.12623 |  | 1 | CAPACITY
200886 | 26ARWF_N39 | 0.69 | 226 | 74 | 0 | 10.7 | 8.59 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY | N39
208985 | MERR IPP | 12.5 | 229 | 2 | 0 | 10.2 | 8.19 |  |  | -0.00162 |  |  | 0.10478 |  | 1 | CAPACITY
203034 | 26NA_O38_P22 | 0.69 | 226 | 74 | 0 | 9.4 | 7.55 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY | O38
200945 | 26CT_V3-030 | 0.69 | 226 | 74 | 0 | 5.3 | 4.25 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY | V3-030
200849 | 26LAKVU GN | 4.16 | 226 | 64 | 3 | 5 | 4.02 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY
208697 | PRIN B34 | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY
208885 | WNHO | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY
210319 | WCAR 1 | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY
208348 | EELI | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00161 |  |  | 0 |  | 1 | CAPACITY
210022 | LING 2 | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY
200883 | Q-053 E | 34.5 | 226 | 74 | 0 | 48 | 0 |  |  | -0.00162 |  |  | 0 |  | 1 | NEWENERGY | Q53
204640 | 27LARA | 13.2 | 227 | 1 | 1 | 30 | 24.08 |  |  | -0.00163 |  |  | 0.10478 |  | 1 | CAPACITY
200915 | 26CHSTN_FL | 34.5 | 226 | 74 | 0 | 6.4 | 5.14 |  |  | -0.00162 |  |  | 0 |  | 1 | CAPACITY | Q53
903644 | W3-099 E OP1 | 230 | 226 | 74 | 0 | 87 | 0 |  |  | -0.00163 |  |  | 0 |  | 1 | NEWENERGY | W3-099
201144 | W3-099 C OP1 | 230 | 226 | 74 | 0 | 13 | 0 |  |  | -0.00163 |  |  | 0 |  | 1 | NEW | W3-099
200839 | 26HOMER C3 | 24 | 226 | 16 | 350 | 650 | 521.86 |  |  | -0.00164 |  |  | 0.10478 |  | 1 | CAPACITY
200838 | 26HOMER C2 | 20 | 226 | 16 | 350 | 614 | 492.95 |  |  | -0.00164 |  |  | 0.10478 |  | 1 | CAPACITY
200812 | 26ALY HYDR | 46 | 226 | 60 | 6 | 21 | 16.86 |  |  | -0.00164 |  |  | 0.07484 |  | 1 | CAPACITY
200852 | 26WARR RDG | 46 | 226 | 60 | 0 | 2.5 | 0 |  |  | -0.00164 |  |  | 0 |  | 1 | ENERGY
290086 | Q-036 E | 0.69 | 226 | 74 | 0 | 40 | 0 |  |  | -0.00166 |  |  | 0 |  | 1 | NEWENERGY | Q36
200905 | 26Q36 | 0.69 | 226 | 74 | 0 | 8.3 | 6.66 |  |  | -0.00166 |  |  | 0 |  | 1 | CAPACITY | Q36
201201 | 26WRREN CT | 13.8 | 226 | 57 | 4 | 57 | 45.76 |  |  | -0.00168 |  |  | 0.08446 |  | 1 | CAPACITY
208848 | HOLA U1-067 | 12.5 | 229 | 64 | 3.6 | 3.6 | 0 |  |  | -0.00168 |  |  | 0 |  | 1 | ENERGY
208580 | MGTN 2 | 12.5 | 229 | 2 | 0 | 4.8 | 3.85 |  |  | -0.00168 |  |  | 0 |  | 1 | CAPACITY
200642 | 26SENECA#1 | 13.8 | 226 | 62 | 75 | 234 | 187.87 |  |  | -0.0017 |  |  | 0.0316 |  | 1 | CAPACITY
200643 | 26SENECA#2 | 13.8 | 226 | 62 | 75 | 221 | 177.43 |  |  | -0.0017 |  |  | 0.0316 |  | 1 | CAPACITY
200644 | 26SENECA#3 | 13.8 | 226 | 61 | 26.1 | 30 | 26.13 |  |  | -0.0017 |  |  | 0.07484 |  | 1 | CAPACITY
204784 | 27LMR_E02 | 69 | 227 | 64 | 0 | 1.2 | 0 |  |  | -0.0017 |  |  | 0 |  | 1 | ENERGY
204785 | 27GLRA_Q45 | 69 | 227 | 64 | 0 | 2 | 1.61 |  |  | -0.0017 |  |  | 0 |  | 1 | CAPACITY
204664 | 27AES GEN3 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.0017 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204663 | 27AES GEN2 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.0017 |  |  | 0 |  | 1 | CAPACITY | IRONWOOD
204662 | 27AES GEN1 | 16 | 227 | 58 | 180 | 260 | 208.74 |  |  | -0.0017 |  |  | 0.04435 |  | 1 | CAPACITY | IRONWOOD
200913 | 26SHAW-D | 4.16 | 226 | 65 | 0 | 6 | 4.82 |  |  | -0.00171 |  |  | 0 |  | 1 | CAPACITY
200722 | 26SHAWVL 2 | 18 | 226 | 12 | 62 | 124.7 | 100.12 |  |  | -0.00172 |  |  | 0.10478 |  | 1 | CAPACITY
200715 | 26SHAWVL 1 | 18 | 226 | 12 | 62 | 122 | 97.95 |  |  | -0.00172 |  |  | 0.10478 |  | 1 | CAPACITY
236828 | 01GRAYMONT | 46 | 201 | 2 | 0 | 4 | 0 |  |  | -0.00171 |  |  | 0 |  | 1 | ENERGY
235003 | AC1-025 E | 46 | 201 | 76 | -1.5 | 1.5 | 0 |  |  | -0.00171 |  |  | 0 |  | 1 | MTX | AC1-025
200649 | 26PENNTECH | 13.8 | 226 | 2 | 12 | 42.3 | 33.96 |  |  | -0.00172 |  |  | 0.10478 |  | 1 | CAPACITY
200665 | 26SHAWVL 3 | 22 | 226 | 12 | 120 | 174.2 | 139.86 |  |  | -0.00173 |  |  | 0.10478 |  | 1 | CAPACITY
200666 | 26SHAWVL 4 | 22 | 226 | 12 | 120 | 171 | 137.29 |  |  | -0.00173 |  |  | 0.10478 |  | 1 | CAPACITY
292683 | V3-070 E | 34.5 | 228 | 75 | 0 | 4.96 | 0 |  |  | -0.00174 |  |  | 0 |  | 1 | NEWENERGY | V3-070
206738 | 28FLE_V3-070 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.00174 |  |  | 0 |  | 1 | CAPACITY | V3-070
200047 | BETH ST4 | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00181 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200050 | BETH CT7 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00181 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200045 | BETH CT2 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00181 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200049 | BETH CT6 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00181 |  |  | 0 |  | 1 | CAPACITY | BETH5678
200046 | BETH CT3 | 13.8 | 229 | 58 | 80 | 127 | 101.96 |  |  | -0.00181 |  |  | 0 |  | 1 | CAPACITY | BETH1234
200048 | BETH CT5 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00181 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
200044 | BETH CT1 | 13.8 | 229 | 58 | 80 | 118 | 94.74 |  |  | -0.00181 |  |  | 0.04435 |  | 1 | CAPACITY | BETH1234
922932 | AB1-082 OP | 46 | 201 | 55 | 0 | 19.9 | 0 |  |  | -0.00182 |  |  | 0.08446 |  | 1 | NEW
916202 | Z1-069 E | 115 | 226 | 74 | 0 | 56.7 | 0 |  |  | -0.00188 |  |  | 0 |  | 1 | NEWENERGY | Z1-069
203349 | 26Z1-069 C | 115 | 226 | 74 | 0 | 13.3 | 10.68 |  |  | -0.00188 |  |  | 0 |  | 1 | CAPACITY | Z1-069
205902 | 27AA2-115 | 23.5 | 227 | 58 | 0 | 485 | 389.39 |  |  | -0.0019 |  |  | 0.04435 |  | 1 | CAPACITY | AA2-115
204655 | 27S.RDG CT | 13.8 | 227 | 55 | 0 | 30.1 | 24.17 |  |  | -0.00189 |  |  | 0.08446 |  | 1 | CAPACITY
204865 | 27WR_V4-052 | 69 | 227 | 55 | 0 | 6 | 4.82 |  |  | -0.0019 |  |  | 0 |  | 1 | CAPACITY
903482 | W3-029 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.00192 |  |  | 0 |  | 1 | NEWENERGY | W3-029
903222 | W3-003 E | 34.5 | 228 | 75 | 0 | 10 | 0 |  |  | -0.00192 |  |  | 0 |  | 1 | NEWENERGY | W3-003
207442 | AE1-156 C | 34.5 | 228 | 75 | 0 | 4.1 | 0 |  |  | -0.00192 |  |  | 0 |  | 1 | NEW | AE1-156
207443 | AE1-156 E | 34.5 | 228 | 75 | 0 | 3.5 | 0 |  |  | -0.00192 |  |  | 0 |  | 1 | NEWENERGY | AE1-156
206744 | 28PIT_W1-132 | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.00192 |  |  | 0 |  | 1 | NEWENERGY | W1-132
902742 | W2-061 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00192 |  |  | 0 |  | 1 | NEWENERGY | W2-061
904682 | V4-069 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00192 |  |  | 0 |  | 1 | NEWENERGY | V4-069
904692 | V4-070 E | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00192 |  |  | 0 |  | 1 | NEWENERGY | V4-070
204679 | 27PC_Q59Y356 | 69 | 227 | 64 | 1.3 | 6 | 4.82 |  |  | -0.00192 |  |  | 0 |  | 1 | CAPACITY
206761 | 28MHD_W3-029 | 34.5 | 228 | 75 | 0 | 3.2 | 2.57 |  |  | -0.00192 |  |  | 0 |  | 1 | CAPACITY | W3-029
206736 | 28F1S_V4-069 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00192 |  |  | 0 |  | 1 | CAPACITY | V4-069
206737 | 28F2S_V4-070 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00192 |  |  | 0 |  | 1 | CAPACITY | V4-070
206754 | 28EAM_W2-061 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00192 |  |  | 0 |  | 1 | CAPACITY | W2-061
204641 | 27PANTHER | 13.2 | 227 | 11 | 45 | 80 | 64.23 |  |  | -0.00197 |  |  | 0.10478 |  | 1 | CAPACITY
204666 | 27ONTELCT2 | 18 | 227 | 58 | 89 | 190.4 | 152.86 |  |  | -0.002 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
204665 | 27ONTELCT1 | 18 | 227 | 58 | 88 | 190.4 | 152.86 |  |  | -0.002 |  |  | 0.04435 |  | 1 | CAPACITY | ONTELAUNEE
204667 | 27ONTELST1 | 18 | 227 | 58 | 89 | 174.3 | 139.94 |  |  | -0.002 |  |  | 0 |  | 1 | CAPACITY | ONTELAUNEE
206329 | 28S RIV G3 | 13.8 | 228 | 58 | 66.1 | 98 | 78.68 |  |  | -0.00202 |  |  | 0.08446 |  | 1 | CAPACITY
206328 | 28S RIV G2 | 13.8 | 228 | 58 | 86.9 | 99.9 | 87.02 |  |  | -0.00202 |  |  | 0.08446 |  | 1 | CAPACITY
206327 | 28S RIV G1 | 13.8 | 228 | 57 | 86.9 | 99.9 | 87.02 |  |  | -0.00202 |  |  | 0.08446 |  | 1 | CAPACITY
206359 | 28PARLN3&4 | 13.8 | 228 | 58 | 5 | 54.35 | 43.63 |  |  | -0.00203 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
206358 | 28PARLN1&2 | 13.8 | 228 | 58 | 37.4 | 54.35 | 46.17 |  |  | -0.00203 |  |  | 0.04435 |  | 1 | CAPACITY | PARLIN NUG
203261 | 26BLOSSBCT | 34.5 | 226 | 55 | 1 | 19 | 15.25 |  |  | -0.00203 |  |  | 0.08446 |  | 1 | CAPACITY
909252 | X2-075 E | 34.5 | 228 | 75 | 0 | 3.72 | 0 |  |  | -0.00203 |  |  | 0 |  | 1 | NEWENERGY | X2-075
206764 | 28JCR_X2-075 | 34.5 | 228 | 75 | 0 | 2.28 | 1.83 |  |  | -0.00203 |  |  | 0 |  | 1 | CAPACITY | X2-075
200894 | 26K02 | 34.5 | 226 | 74 | 0 | 56 | 0 |  |  | -0.00205 |  |  | 0 |  | 1 | NEWENERGY | K02
203999 | P-047 E | 34.5 | 226 | 74 | 0 | 80.5 | 0 |  |  | -0.00205 |  |  | 0 |  | 1 | NEWENERGY | P47
200887 | 26ARMNA MT | 34.5 | 226 | 74 | 0 | 15.8 | 12.69 |  |  | -0.00205 |  |  | 0 |  | 1 | CAPACITY | P47
203351 | 26GROZ1-110 | 34.5 | 226 | 56 | 0 | 21.4 | 17.18 |  |  | -0.00209 |  |  | 0.12623 |  | 1 | CAPACITY
203352 | 26CANZ2-011 | 34.5 | 226 | 65 | 0 | 21 | 16.86 |  |  | -0.00209 |  |  | 0.12623 |  | 1 | CAPACITY
208933 | HUST ST10 | 22 | 229 | 58 | 0 | 396 | 317.93 |  |  | -0.0021 |  |  | 0 |  | 1 | CAPACITY | Hummel
208931 | HUST CT12 | 18 | 229 | 58 | 0 | 242 | 194.29 |  |  | -0.0021 |  |  | 0 |  | 1 | CAPACITY | Hummel
208930 | HUST CT11 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.0021 |  |  | 0.04435 |  | 1 | CAPACITY | Hummel
208932 | HUST CT13 | 18 | 229 | 58 | 0 | 223 | 179.04 |  |  | -0.0021 |  |  | 0 |  | 1 | CAPACITY | Hummel
206364 | 28RDOAKCT3 | 18 | 228 | 58 | 109.8 | 176 | 141.3 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206363 | 28RDOAKCT2 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.00209 |  |  | 0 |  | 1 | CAPACITY | RED OAK
203350 | 26MILZ1-092 | 34.5 | 226 | 56 | 0 | 21 | 16.86 |  |  | -0.00209 |  |  | 0.12623 |  | 1 | CAPACITY
206365 | 28RDOAKST1 | 18 | 228 | 58 | 69 | 248 | 199.11 |  |  | -0.00212 |  |  | 0 |  | 1 | CAPACITY | RED OAK
206362 | 28RDOAKCT1 | 18 | 228 | 58 | 99.8 | 176 | 141.3 |  |  | -0.00212 |  |  | 0.04435 |  | 1 | CAPACITY | RED OAK
920341 | AA2-132 | 34.5 | 226 | 55 | 0 | 19.9 | 0 |  |  | -0.00216 |  |  | 0.08446 |  | 1 | NEW
919201 | AA1-144 OP | 230 | 226 | 58 | 0 | 163 | 130.87 |  |  | -0.0022 |  |  | 0.04435 |  | 1 | CAPACITY | AA1-144
203923 | X1-109 G2 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00221 |  |  | 0 |  | 1 | CAPACITY | X1-109
203922 | X1-109 G1 | 23 | 226 | 58 | 92 | 382.5 | 307.09 |  |  | -0.00221 |  |  | 0.04435 |  | 1 | CAPACITY | X1-109
203283 | 26MANOR_T86 | 34.5 | 226 | 64 | 0.8 | 1.3 | 1.04 |  |  | -0.00222 |  |  | 0 |  | 1 | CAPACITY
G-007A | LTFEXP_G-007A->PJM |  |  | LTF |  | 239.8 |  |  |  | -0.0023
206406 | 28W4-009_1S | 18 | 228 | 58 | 0 | 306 | 245.67 |  |  | -0.00225 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206405 | 28W4-009_1B | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.00225 |  |  | 0 |  | 1 | CAPACITY | RARITAN RIVER
206404 | 28W4-009_1A | 18 | 228 | 58 | 0 | 209.5 | 168.2 |  |  | -0.00225 |  |  | 0.04435 |  | 1 | CAPACITY | RARITAN RIVER
207441 | AD1-113 ST | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.00225 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
207434 | AD1-113 CT1 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.00225 |  |  | 0.04435 |  | 1 | NEW | RARITAN RIVER
207435 | AD1-113 CT2 | 18 | 228 | 58 | 0 | 25 | 0 |  |  | -0.00225 |  |  | 0 |  | 1 | NEW | RARITAN RIVER
206350 | 28RRCT1&2 | 13.8 | 228 | 57 | 97.1 | 111.6 | 97.21 |  |  | -0.00225 |  |  | 0.08446 |  | 1 | CAPACITY
206351 | 28RRCT3&4 | 13.8 | 228 | 57 | 90.9 | 104.5 | 91.03 |  |  | -0.00225 |  |  | 0.08446 |  | 1 | CAPACITY
203932 | AA2-133 GEN | 13.8 | 226 | 55 | 0 | 19.89 | 0 |  |  | -0.00229 |  |  | 0.08446 |  | 1 | NEW
209018 | SUNBIPCT | 12.5 | 229 | 55 | 0 | 36 | 28.9 |  |  | -0.00232 |  |  | 0.08446 |  | 1 | CAPACITY
212345 | PENS | 12.5 | 229 | 2 | 0 | 3 | 2.41 |  |  | -0.00232 |  |  | 0 |  | 1 | CAPACITY
200038 | SUSQ 2 | 24 | 229 | 41 | 1089 | 1251.7 | 1090.36 |  |  | -0.00232 |  |  | 0.01494 |  | 1 | CAPACITY
200083 | FRDM 11 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00235 |  |  | 0.04435 |  | 1 | CAPACITY | Z2-046
200084 | FRDM 21 | 23.5 | 229 | 58 | 0 | 490 | 393.4 |  |  | -0.00235 |  |  | 0 |  | 1 | CAPACITY | Z2-046
902292 | W2-016E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.00236 |  |  | 0 |  | 1 | NEWENERGY | W2-016
206745 | 28F3S_W2-016 | 34.5 | 228 | 75 | 0 | 3 | 2.41 |  |  | -0.00236 |  |  | 0 |  | 1 | CAPACITY | W2-016
294573 | P-028 E | 0.57 | 226 | 74 | 0 | 120 | 0 |  |  | -0.00238 |  |  | 0 |  | 1 | NEWENERGY | P28
200823 | 26MHP_X3-003 | 115 | 226 | 29 | 0 | 62 | 0 |  |  | -0.00238 |  |  | 0.10478 |  | 1 | NEW
200851 | 26MEHOOP3 | 13.2 | 226 | 29 | 24.8 | 59 | 47.37 |  |  | -0.00238 |  |  | 0.10478 |  | 1 | CAPACITY
200917 | 26MTNTP_P28 | 0.69 | 226 | 74 | 0 | 21.9 | 17.58 |  |  | -0.00238 |  |  | 0 |  | 1 | CAPACITY | P28
203347 | 26NME_Y1-047 | 34.5 | 226 | 65 | 0 | 21.4 | 17.18 |  |  | -0.00238 |  |  | 0.12623 |  | 1 | CAPACITY
212435 | SMIL | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00238 |  |  | 0 |  | 1 | CAPACITY
208945 | LOHA CT | 12.5 | 229 | 52 | 0 | 14 | 11.24 |  |  | -0.0024 |  |  | 0.08446 |  | 1 | CAPACITY
208948 | WILL CT | 12.5 | 229 | 55 | 0 | 27.4 | 22 |  |  | -0.00241 |  |  | 0.08446 |  | 1 | CAPACITY
212005 | ALWD | 12.5 | 229 | 2 | 0 | 3.2 | 2.57 |  |  | -0.00241 |  |  | 0 |  | 1 | CAPACITY
212370 | PATRIOT 2 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00244 |  |  | 0 |  | 1 | CAPACITY | MOXIE PATRIOT
212369 | PATRIOT 1 | 23 | 229 | 58 | 0 | 382.5 | 307.09 |  |  | -0.00244 |  |  | 0.04435 |  | 1 | CAPACITY | MOXIE PATRIOT
208911 | MONT G1 | 24 | 229 | 16 | 403 | 758.5 | 608.97 |  |  | -0.00246 |  |  | 0.10478 |  | 1 | CAPACITY
208912 | MONT G2 | 24 | 229 | 16 | 403 | 757.9 | 608.49 |  |  | -0.00246 |  |  | 0.10478 |  | 1 | CAPACITY
203907 | 26Y2-042 | 34.5 | 226 | 55 | 0 | 18.3 | 14.69 |  |  | -0.00252 |  |  | 0.12623 |  | 1 | CAPACITY
208981 | FOWH IPP | 13.8 | 229 | 11 | 0 | 42.7 | 34.28 |  |  | -0.00253 |  |  | 0.10478 |  | 1 | CAPACITY
209021 | WEST IPP | 13.8 | 229 | 11 | 0 | 32.5 | 26.09 |  |  | -0.00253 |  |  | 0.10478 |  | 1 | CAPACITY
212099 | COLA IPP | 13.8 | 229 | 55 | 0 | 8 | 6.42 |  |  | -0.00253 |  |  | 0 |  | 1 | CAPACITY
212174 | INGE | 0.48 | 229 | 64 | 0 | 6.1 | 4.9 |  |  | -0.00253 |  |  | 0 |  | 1 | CAPACITY
902932 | W2-080 E | 34.5 | 228 | 75 | 0 | 1.2 | 0 |  |  | -0.00262 |  |  | 0 |  | 1 | NEWENERGY | W2-080
206718 | 28STAW2-080 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00262 |  |  | 0 |  | 1 | CAPACITY | W2-080
208918 | SUSQ 1 | 24 | 229 | 41 | 1090.4 | 1253.3 | 1091.76 |  |  | -0.00263 |  |  | 0.01494 |  | 1 | CAPACITY
209013 | SCEN IPP | 13.8 | 229 | 11 | 0 | 86 | 69.05 |  |  | -0.00263 |  |  | 0.10478 |  | 1 | CAPACITY
208982 | GLBT IPP | 13.8 | 229 | 11 | 0 | 82 | 65.83 |  |  | -0.00263 |  |  | 0.10478 |  | 1 | CAPACITY
208941 | FISH CT | 12.5 | 229 | 52 | 0 | 28 | 22.48 |  |  | -0.00263 |  |  | 0.08446 |  | 1 | CAPACITY
209027 | LOR2_Q27 | 0.69 | 229 | 74 | 0 | 11.4 | 9.15 |  |  | -0.00263 |  |  | 0 |  | 1 | CAPACITY | Q27
212266 | LOR1 | 0.69 | 229 | 74 | 0 | 3.5 | 2.81 |  |  | -0.00263 |  |  | 0 |  | 1 | CAPACITY | N14
234311 | HUN GEN5 | 13.8 | 236 | 58 | 0 | 48.7 | 39.1 |  |  | -0.00269 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234312 | HUN GEN6 | 13.8 | 236 | 58 | 0 | 48.4 | 38.86 |  |  | -0.00269 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234305 | HUN GEN4 | 13.8 | 236 | 56 | 0 | 44.3 | 35.57 |  |  | -0.00269 |  |  | 0 |  | 1 | CAPACITY | HUNLOCK
234304 | HUN GEN3 | 13.2 | 236 | 58 | 0 | 29.2 | 23.44 |  |  | -0.00269 |  |  | 0.04435 |  | 1 | CAPACITY | HUNLOCK
923673 | AB1-182 E | 69 | 229 | 76 | -20 | 20 | 0 |  |  | -0.00271 |  |  | 0.05 |  | 1 | MTX | AB1-182
208944 | JENK CT | 12.5 | 229 | 55 | 0 | 28 | 22.48 |  |  | -0.00271 |  |  | 0.08446 |  | 1 | CAPACITY
208972 | BECR K09 | 0.69 | 229 | 74 | 0 | 3.3 | 2.65 |  |  | -0.00271 |  |  | 0 |  | 1 | CAPACITY | L18
211374 | AVOC | 12.5 | 229 | 2 | 0 | 17.4 | 13.97 |  |  | -0.00274 |  |  | 0 |  | 1 | CAPACITY
211375 | BEAC | 69 | 229 | 2 | 0 | 20 | 0 |  |  | -0.00278 |  |  | 0.10478 |  | 1 | ENERGY
209023 | WIENIPP1 | 13.8 | 229 | 57 | 0 | 59.5 | 47.77 |  |  | -0.00278 |  |  | 0.08446 |  | 1 | CAPACITY
209025 | WIENIPP3 | 13.8 | 229 | 56 | 0 | 58.8 | 47.21 |  |  | -0.00278 |  |  | 0.08446 |  | 1 | CAPACITY
209026 | WIENIPP4 | 13.8 | 229 | 56 | 0 | 29.6 | 23.76 |  |  | -0.00278 |  |  | 0.08446 |  | 1 | CAPACITY
208943 | HARW CT | 12.5 | 229 | 55 | 0 | 27.2 | 21.84 |  |  | -0.00278 |  |  | 0.08446 |  | 1 | CAPACITY
211591 | HARW | 12.5 | 229 | 2 | 0 | 2 | 1.61 |  |  | -0.00278 |  |  | 0 |  | 1 | CAPACITY
208055 | LAEN G1 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.0028 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G1
208053 | LAEN G3 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.0028 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G3
208052 | LAEN G2 | 23.5 | 229 | 58 | 0 | 468 | 375.74 |  |  | -0.0028 |  |  | 0.04435 |  | 1 | CAPACITY | LAEN G2
917662 | Z2-107 E | 34.5 | 229 | 76 | -10 | 10 | 0 |  |  | -0.0028 |  |  | 0.05 |  | 1 | MTX | Z2-107
209009 | PEIP 2 | 13.8 | 229 | 56 | 0 | 43.7 | 35.08 |  |  | -0.0028 |  |  | 0.08446 |  | 1 | CAPACITY
209010 | PEIP 1 | 13.8 | 229 | 29 | 0 | 26.7 | 21.43 |  |  | -0.0028 |  |  | 0.10478 |  | 1 | CAPACITY
209029 | WAYM IPP | 34.5 | 229 | 74 | 0 | 9 | 7.23 |  |  | -0.0028 |  |  | 0 |  | 1 | CAPACITY | K21
209003 | KSTN IPP | 13.8 | 229 | 65 | 0 | 4.9 | 3.93 |  |  | -0.0028 |  |  | 0 |  | 1 | CAPACITY
925955 | AC1-071 E | 0.69 | 229 | 74 | 0 | 62.1 | 0 |  |  | -0.00281 |  |  | 0 |  | 1 | NEWENERGY | AC1-071
925954 | AC1-071 C | 0.69 | 229 | 74 | 0 | 8.74 | 7.02 |  |  | -0.00281 |  |  | 0 |  | 1 | NEW | AC1-071
208940 | ALLE CT | 12.5 | 229 | 55 | 0 | 56 | 44.96 |  |  | -0.00289 |  |  | 0.08446 |  | 1 | CAPACITY
208980 | BEPO IPP | 18 | 229 | 58 | 50 | 195 | 156.56 |  |  | -0.00294 |  |  | 0.04435 |  | 1 | CAPACITY | BETH5678
209007 | NOEN IPP | 13.8 | 229 | 12 | 80 | 111.4 | 89.44 |  |  | -0.003 |  |  | 0.10478 |  | 1 | CAPACITY
921663 | AA2-017 E | 69 | 229 | 74 | 0 | 85.3 | 0 |  |  | -0.00314 |  |  | 0 |  | 1 | NEWENERGY | AA2-017
921662 | AA2-017 C | 69 | 229 | 74 | 0 | 12.7 | 0 |  |  | -0.00314 |  |  | 0 |  | 1 | NEW | AA2-017
211065 | PSPA IPP | 13.8 | 229 | 75 | 0 | 18.4 | 6.74 |  |  | -0.00325 |  |  | 0 |  | 1 | NEWENERGY | U4-014
208946 | MACR CT | 12.5 | 229 | 55 | 0 | 72 | 57.81 |  |  | -0.00358 |  |  | 0.08446 |  | 1 | CAPACITY
204689 | 27PLF_V3-044 | 34.5 | 227 | 64 | 0 | 2.9 | 2.33 |  |  | -0.00369 |  |  | 0 |  | 1 | CAPACITY
208920 | WLPK | 12.5 | 229 | 60 | 0 | 40.9 | 32.84 |  |  | -0.00369 |  |  | 0.07484 |  | 1 | CAPACITY
905762 | W4-097 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00378 |  |  | 0 |  | 1 | NEWENERGY | W4-097
206759 | 28HOL_W4-097 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00378 |  |  | 0 |  | 1 | CAPACITY | W4-097
208909 | MACR G3 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00385 |  |  | 0.10478 |  | 1 | CAPACITY
208910 | MACR G4 | 24 | 229 | 35 | 250 | 850 | 682.43 |  |  | -0.00385 |  |  | 0.10478 |  | 1 | CAPACITY
208908 | LMBE ST1 | 16.5 | 229 | 58 | 135 | 239.8 | 192.53 |  |  | -0.00385 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
208905 | LMBE CT1 | 16.5 | 229 | 58 | 101 | 200 | 160.57 |  |  | -0.00385 |  |  | 0.04435 |  | 1 | CAPACITY | LOWER MT BETHEL
208906 | LMBE CT2 | 16.5 | 229 | 58 | 102 | 200 | 160.57 |  |  | -0.00385 |  |  | 0 |  | 1 | CAPACITY | LOWER MT BETHEL
207438 | AD2-070 E | 34.5 | 228 | 75 | 0 | 4.3 | 0 |  |  | -0.00385 |  |  | 0 |  | 1 | NEWENERGY | AD2-070
207437 | AD2-070 C | 34.5 | 228 | 75 | 0 | 3.5 | 2.81 |  |  | -0.00385 |  |  | 0 |  | 1 | CAPACITY | AD2-070
206330 | 28GILCT9 | 18 | 228 | 57 | 89.8 | 152 | 122.03 |  |  | -0.00388 |  |  | 0.08446 |  | 1 | CAPACITY
206341 | 28GIL 8 | 13.8 | 228 | 58 | 69.9 | 90 | 72.26 |  |  | -0.00388 |  |  | 0.04435 |  | 1 | CAPACITY | GILBERT
206342 | 28GIL 6&7 | 13.8 | 228 | 58 | 87 | 100 | 87.11 |  |  | -0.00388 |  |  | 0 |  | 1 | CAPACITY | GILBERT
206340 | 28GIL 4&5 | 13.8 | 228 | 58 | 85.3 | 98 | 85.37 |  |  | -0.00388 |  |  | 0 |  | 1 | CAPACITY | GILBERT
207402 | 28AA2-082 E | 34.5 | 228 | 76 | -20 | 20 | 0 |  |  | -0.00391 |  |  | 0.05 |  | 1 | MTX | AA2-082
905602 | W4-073 E | 34.5 | 228 | 75 | 0 | 10.5 | 0 |  |  | -0.004 |  |  | 0 |  | 1 | NEWENERGY | W4-073
206719 | 28W4-073 | 34.5 | 228 | 75 | 0 | 6.4 | 5.14 |  |  | -0.004 |  |  | 0 |  | 1 | CAPACITY
902062 | W1-127E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00403 |  |  | 0 |  | 1 | NEWENERGY | W1-127
290131 | U2-059E | 34.5 | 228 | 75 | 0 | 1.24 | 0 |  |  | -0.00403 |  |  | 0 |  | 1 | NEWENERGY | U2-059
925462 | AC1-018 E | 34.5 | 228 | 75 | 0 | 0.9 | 0 |  |  | -0.00403 |  |  | 0 |  | 1 | NEWENERGY | AC1-018
925461 | AC1-018 C | 34.5 | 228 | 75 | 0 | 0.5 | 0 |  |  | -0.00403 |  |  | 0 |  | 1 | NEW | AC1-018
206751 | 28HRM_W1-127 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00403 |  |  | 0 |  | 1 | CAPACITY | W1-127
206741 | 28FR_U2-059 | 34.5 | 228 | 75 | 0 | 0.8 | 0.64 |  |  | -0.00403 |  |  | 0 |  | 1 | CAPACITY | U2-059
204628 | 27N BANGR8 | 34.5 | 227 | 55 | 0 | 4 | 3.21 |  |  | -0.00422 |  |  | 0 |  | 1 | CAPACITY
904002 | V4-001 E | 34.5 | 228 | 75 | 0 | 2 | 0 |  |  | -0.00422 |  |  | 0 |  | 1 | NEWENERGY | V4-001
206743 | 28GAR_V4-001 | 34.5 | 228 | 75 | 0 | 0.76 | 0.61 |  |  | -0.00422 |  |  | 0 |  | 1 | CAPACITY | V4-001
903962 | W3-077 E | 34.5 | 228 | 75 | 0 | 9.3 | 0 |  |  | -0.00425 |  |  | 0 |  | 1 | NEWENERGY | W3-077
207408 | W3-077 C | 34.5 | 228 | 75 | 0 | 5.7 | 4.58 |  |  | -0.00425 |  |  | 0 |  | 1 | CAPACITY | W3-077
206757 | 28RH_W2-091 | 34.5 | 228 | 75 | 0 | 3.6 | 2.89 |  |  | -0.00425 |  |  | 0 |  | 1 | CAPACITY | W2-091
204654 | 27SHAW CT | 13.8 | 227 | 56 | 0 | 20 | 16.06 |  |  | -0.00433 |  |  | 0.08446 |  | 1 | CAPACITY
204651 | 27PORT CT | 13.8 | 227 | 56 | 4 | 35 | 28.1 |  |  | -0.00446 |  |  | 0.08446 |  | 1 | CAPACITY
903632 | W3-044 E OP1 | 34.5 | 228 | 75 | 0 | 12.4 | 0 |  |  | -0.00459 |  |  | 0 |  | 1 | NEWENERGY | W3-044
206749 | 28WA_W3-044 | 34.5 | 228 | 75 | 0 | 7.6 | 6.1 |  |  | -0.00459 |  |  | 0 |  | 1 | CAPACITY | W3-044
204661 | 27PORT 5CT | 13.8 | 227 | 57 | 72.5 | 134 | 107.58 |  |  | -0.00464 |  |  | 0.08446 |  | 1 | CAPACITY
206345 | 28N27_Y2-018 | 13.8 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00469 |  |  | 0 |  | 1 | NEWENERGY | Y2-018
206747 | 28DSM_X3-029 | 34.5 | 228 | 29 | 0 | 11.15 | 0 |  |  | -0.00471 |  |  | 0.10478 |  | 1 | ENERGY
206671 | 28HOFFMAN | 34.5 | 228 | 55 | 0 | 5 | 0 |  |  | -0.00471 |  |  | 0.08446 |  | 1 | ENERGY
905442 | W4-046 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00479 |  |  | 0 |  | 1 | NEWENERGY | W4-046
206748 | 28DL_W4-046 | 34.5 | 228 | 75 | 0 | 2.4 | 1.93 |  |  | -0.00479 |  |  | 0 |  | 1 | CAPACITY | W4-046
206337 | 28KITTGEN1 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00497 |  |  | 0.0316 |  | 1 | CAPACITY
206338 | 28KITTGEN2 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00497 |  |  | 0.0316 |  | 1 | CAPACITY
206339 | 28KITTGEN3 | 14.4 | 228 | 62 | 70 | 140 | 112.4 |  |  | -0.00497 |  |  | 0.0316 |  | 1 | CAPACITY
933322 | AC2-144 E | 34.5 | 228 | 76 | -0.3 | 0.25 | 0 |  |  | -0.0053 |  |  | 0 |  | 1 | MTX | AC2-144
907394 | X1-095 E OP1 | 34.5 | 228 | 75 | 0 | 1.86 | 0 |  |  | -0.00574 |  |  | 0 |  | 1 | NEWENERGY | X1-095
206767 | 28BRNX1-095 | 34.5 | 228 | 75 | 0 | 1.14 | 0.92 |  |  | -0.00574 |  |  | 0 |  | 1 | CAPACITY | X1-095
905542 | W4-064 E | 34.5 | 228 | 75 | 0 | 1.9 | 0 |  |  | -0.00619 |  |  | 0 |  | 1 | NEWENERGY | W4-064
206758 | 28AU_W4-064 | 34.5 | 228 | 75 | 0 | 1.1 | 0.88 |  |  | -0.00619 |  |  | 0 |  | 1 | CAPACITY | W4-064
907012 | X1-012 E | 34.5 | 228 | 75 | 0 | 6.2 | 0 |  |  | -0.00622 |  |  | 0 |  | 1 | NEWENERGY | X1-012
206762 | 28FRD_X1-012 | 34.5 | 228 | 75 | 0 | 3.7 | 2.97 |  |  | -0.00622 |  |  | 0 |  | 1 | CAPACITY | X1-012
207413 | 28AA2-061 E | 34.5 | 228 | 76 | -8 | 8 | 0 |  |  | -0.00623 |  |  | 0.05 |  | 1 | MTX | AA2-061
207412 | 28AA2-060 E | 34.5 | 228 | 76 | -6 | 6 | 0 |  |  | -0.00623 |  |  | 0.05 |  | 1 | MTX | AA2-060
206742 | 28SUX_V3-011 | 34.5 | 228 | 64 | 0 | 2 | 0 |  |  | -0.00623 |  |  | 0 |  | 1 | CAPACITY
903672 | W3-106 E | 34.5 | 228 | 75 | 0 | 6.18 | 0 |  |  | -0.00624 |  |  | 0 |  | 1 | NEWENERGY | W3-106
903682 | W3-110 E | 34.5 | 228 | 75 | 0 | 4.65 | 0 |  |  | -0.00624 |  |  | 0 |  | 1 | NEWENERGY | W3-110
933582 | AC2-175 E | 34.5 | 228 | 75 | 0 | 1.6 | 0 |  |  | -0.00624 |  |  | 0 |  | 1 | NEWENERGY | AC2-175
207440 | AE1-081 E O1 | 34.5 | 228 | 75 | 0 | 1.34 | 0 |  |  | -0.00624 |  |  | 0 |  | 1 | NEWENERGY | AE1-081
206746 | 28WNG_W3-110 | 34.5 | 228 | 75 | 0 | 2.85 | 2.29 |  |  | -0.00624 |  |  | 0 |  | 1 | CAPACITY | W3-110
207439 | AE1-081 C O1 | 34.5 | 228 | 75 | 0 | 0.96 | 0.77 |  |  | -0.00624 |  |  | 0 |  | 1 | CAPACITY | AE1-081
206763 | 28BVR_Y1-020 | 34.5 | 228 | 75 | 0 | 3.72 | 2.99 |  |  | -0.00626 |  |  | 0 |  | 1 | CAPACITY | Y1-020
933332 | AC2-145 E | 34.5 | 228 | 76 | -0.2 | 0.2 | 0 |  |  | -0.00696 |  |  | 0 |  | 1 | MTX | AC2-145
937512 | AD2-210 E | 34.5 | 228 | 76 | -2 | 2 | 0 |  |  | -0.00734 |  |  | 0 |  | 1 | MTX | AD2-210
217205 | WCALDSOLAR E | 13.2 | 231 | 75 | 0 | 0.7 | 0 |  |  | -0.00974 |  |  | 0 |  | 1 | NEWENERGY | AB1-021
217204 | WCALDSOLAR C | 13.2 | 231 | 75 | 0 | 0.3 | 0.24 |  |  | -0.00974 |  |  | 0 |  | 1 | CAPACITY | AB1-021
CBM North | LTFEXP_CBM-N->PJM |  |  | LTF |  | 120 |  |  |  | -0.0129
217193 | NEC_ST | 18 | 231 | 58 | 51.5 | 259 | 207.94 |  |  | -0.01487 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217192 | NEC_CT2 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.01487 |  |  | 0 |  | 1 | CAPACITY | DELANCY STREET
217191 | NEC_CT1 | 18 | 231 | 58 | 110.5 | 223 | 179.04 |  |  | -0.01487 |  |  | 0.04435 |  | 1 | CAPACITY | DELANCY STREET
217186 | ESSEX_G9 | 13.8 | 231 | 57 | 70.5 | 81 | 70.56 |  |  | -0.01487 |  |  | 0.08446 |  | 1 | CAPACITY
217073 | ESSEX_CTG2 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.01487 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217060 | ESSEX_CTG1 | 13.8 | 231 | 58 | 33.6 | 43 | 34.52 |  |  | -0.01487 |  |  | 0.04435 |  | 1 | CAPACITY | NEWARK BAY
217080 | ESSEX_STG3 | 13.8 | 231 | 58 | 0 | 34.2 | 27.46 |  |  | -0.01487 |  |  | 0 |  | 1 | CAPACITY | NEWARK BAY
217121 | ECCF | 26.4 | 231 | 55 | 0 | 2.3 | 1.85 |  |  | -0.01487 |  |  | 0 |  | 1 | CAPACITY
217216 | BARNGR HS E | 26.4 | 231 | 75 | 0 | 0.34 | 0 |  |  | -0.01487 |  |  | 0 |  | 1 | NEWENERGY | V3-065
217206 | BARNGR HS C | 26.4 | 231 | 75 | 0 | 0.21 | 0.17 |  |  | -0.01487 |  |  | 0 |  | 1 | CAPACITY | V3-065
217195 | REDH E | 13 | 231 | 75 | 0 | 3.1 | 0 |  |  | -0.01533 |  |  | 0 |  | 1 | NEWENERGY | V2-025
217167 | KRNY_14 | 13.8 | 231 | 57 | 60 | 94.8 | 76.11 |  |  | -0.01608 |  |  | 0.08446 |  | 1 | CAPACITY
217083 | KRNY_132 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.01608 |  |  | 0.08446 |  | 1 | CAPACITY
217086 | KRNY_131 | 13.8 | 231 | 57 | 60 | 94.65 | 75.99 |  |  | -0.01608 |  |  | 0.08446 |  | 1 | CAPACITY
217147 | KRNY_1212 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.01608 |  |  | 0.08446 |  | 1 | CAPACITY
217146 | KRNY_1234 | 13.8 | 231 | 56 | 60 | 89.35 | 71.74 |  |  | -0.01608 |  |  | 0.08446 |  | 1 | CAPACITY
217140 | BERGEN_2ST | 18 | 231 | 58 | 80 | 252.2 | 202.48 |  |  | -0.02056 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217138 | BERGEN_2CT1 | 18 | 231 | 58 | 60 | 178.9 | 143.63 |  |  | -0.02056 |  |  | 0.04435 |  | 1 | CAPACITY | BERGEN2
217139 | BERGEN_2CT2 | 18 | 231 | 58 | 80 | 178.9 | 143.63 |  |  | -0.02056 |  |  | 0 |  | 1 | CAPACITY | BERGEN2
217249 | HACKENSOLA E | 26.4 | 231 | 75 | 0 | 0.62 | 0 |  |  | -0.02056 |  |  | 0 |  | 1 | NEWENERGY | X1-072
217201 | HACKENSOLA C | 26.4 | 231 | 75 | 0 | 0.38 | 0.31 |  |  | -0.02056 |  |  | 0 |  | 1 | CAPACITY | X1-072
217831 | PB_NUTCLIF | 26 | 231 | 2 | 0 | 10.7 | 8.59 |  |  | -0.02575 |  |  | 0 |  | 1 | CAPACITY
217207 | PARK ELE E | 13.2 | 231 | 75 | 0 | 0.27 | 0 |  |  | -0.02773 |  |  | 0 |  | 1 | NEWENERGY | V3-066
217208 | PARK ELE C | 13.2 | 231 | 75 | 0 | 0.16 | 0.13 |  |  | -0.02773 |  |  | 0 |  | 1 | CAPACITY | V3-066
217168 | METRODIV E | 13.2 | 231 | 75 | 0 | 1.63 | 0 |  |  | -0.05331 |  |  | 0 |  | 1 | NEWENERGY | W4-059
217169 | METRODIV C | 13.2 | 231 | 75 | 0 | 0.23 | 0.18 |  |  | -0.05331 |  |  | 0 |  | 1 | CAPACITY | W4-059
218092 | PRIMEENG_G | 26.4 | 231 | 29 | 10 | 70.3 | 56.44 |  |  | -0.10343 |  |  | 0.10478 |  | 1 | CAPACITY
217850 | MONTCLAIR_U | 26 | 231 | 2 | 0 | 10.6 | 8.51 |  |  | -0.10998 |  |  | 0 |  | 1 | CAPACITY
217176 | GREATFALLS | 4.2 | 231 | 60 | 0 | 5.9 | 4.74 |  |  | -0.10998 |  |  | 0 |  | 1 | CAPACITY
934302 | AD1-054 E | 13.2 | 231 | 75 | 0 | 1.5 | 0 |  |  | -0.15725 |  |  | 0 |  | 1 | NEWENERGY | AD1-054