## Summary
2028 RTEP PJM Generation Deliverability Result (Summer)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Comment
28-GD-S2-S1 | 218306 | DEANS | 218304 | BRUNSWCK | 1 | 230 | 231 | 887 | 1117.7 | 1094.1 | 126.01 | 123.35 | PJM500_PS_P2-3_BRBG5_4-5 | Breaker | Conductor Rating is the same as basecase model | Yes
28-GD-S2-S2 | 218306 | DEANS | 218304 | BRUNSWCK | 1 | 230 | 231 | 887 | 1117.7 | 1094.1 | 126.01 | 123.35 | PJM500_P2-3_BRBG5_3-4 | Breaker | Conductor Rating is the same as basecase model | Yes
28-GD-S2-S134 | 227934 | CARDIFF2 | 227945 | LEWIS #2 | 1 | 138 | 234 | 400 | 462.7 | 452.4 | 115.67 | 113.1 | AE_P7-1 AE3TOWER | Tower | Conductor Rating is the same as basecase model | Yes
28-GD-S2-S3 | 206316 | 28WINDSOR | 219752 | CLRKSVLL_1 | 1 | 230 | 228/231 | 813 | 882 | 877.5 | 108.49 | 107.94 | PJM500_PS_P2-3_DEAN5_3-4 | Breaker | SN/SE = 709/869 | Yes
28-GD-S2-S136 | 218343 | TOSCO_2 | 218441 | VFT_2 | 1 | 230 | 231 | 1081 | 1165.4 | 1141.6 | 107.81 | 105.6 | PS_P7-1_H2286+W2249_LT | Tower | Conductor Rating is the same as basecase model | No | Pre-existing overload not caused by offshore wind solicitations. PJM is not seeking proposals for these facilities at these loading levels.
28-GD-S2-S137 | 218300 | LINDEN | 219046 | TOSCO_3 | 1 | 230 | 231 | 1081 | 1160.3 | 1140.2 | 107.34 | 105.48 | PS_P7-1_H2286+W2249_LT | Tower | Conductor Rating is the same as basecase model | No | Pre-existing overload not caused by offshore wind solicitations. PJM is not seeking proposals for these facilities at these loading levels.
28-GD-S2-S138 | 227945 | LEWIS #2 | 227902 | LEWIS #1 | 1 | 138 | 234 | 286.8 | 301.1 | 294.3 | 105 | 102.62 | AE_P7-1 AE3TOWER | Tower | Conductor Rating is the same as basecase model | Yes
28-GD-S2-S8 | 206302 | 28OYSTER C | 206297 | 28MANITOU | 1 | 230 | 228 | 817 | 853.5 | 833.9 | 104.47 | 102.07 | JC-P2-3-JCC-230-234OD | Breaker | SN/SE = 709/869 | Yes
28-GD-S2-S9 | 206302 | 28OYSTER C | 206297 | 28MANITOU | 1 | 230 | 228 | 817 | 853.3 | 833.7 | 104.45 | 102.05 | JC-P2-3-JCC-230-234OC | Breaker | SN/SE = 709/869 | Yes
28-GD-S2-S11 | 206302 | 28OYSTER C | 206297 | 28MANITOU | 2 | 230 | 228 | 802 | 828.9 | 810.5 | 103.35 | 101.06 | JC-P2-3-JCC-230-11 | Breaker | SN/SE = 709/869 | Yes
28-GD-S2-S139 | 227900 | CARDIFF C | 219100 | NEWFRDM | 1 | 230 | 231/234 | 692 | 714.8 | 698.9 | 103.3 | 101 | JC-P7-1-JCC-230-13 | Tower | Conductor Rating is the same as basecase model | Yes
Informational purposes:
N/A | 217163 | BERGEN_4 | 217157 | BERGEN_R | 1 | 138 | 231 | 350 | 356.5 | 350.5 | 101.86 | 100.14 | PS_P2-3_BERG_1-2 | Breaker | Conductor Rating is the same as basecase model | N/A | The Aldene-Stanley Terrace 230 kV overload in 2035 may be able to be relieved through modification of the Essex PAR flow settings, but participants will need to supply proposals for any additional reliability needs (the Bergen 138 kV line is one such example) created by such an adjustment they assume in their analysis.