## Summary
2035 RTEP PJM Generation Deliverability Result (Summer)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | 2028 FN AC % | 2035 FN AC % | Cont Label | Cont Type | PJM Accepting Proposals | Comment
35-GD-S2-S2 | 218306 | DEANS | 218304 | BRUNSWCK | 1 | 230/230 | 231/231 | 887 | 115.09 | 116.15 | 'PS_P7-1_G2207+W2249_LT' | Tower | Yes
35-GD-S2-S4 | 218306 | DEANS | 218304 | BRUNSWCK | 1 | 230/230 | 231/231 | 887 | 106.83 | 107.81 | 'JC-P7-1-JCC-230-16' | Tower | Yes | Removed as there is OP flowgate at 111.7%, making this violation not valid.
35-GD-S2-S6 | 218307 | ALDENE_2 | 218430 | STANTER_1 | 1 | 230/230 | 231/231 | 558 | 99.71 | 101.52 | 'PS_P1-2_G-2285_LT/* ALDENE TO SPRINGFIELD ROAD' | Single | Yes | Overload may be able to be relieved through modification of the Essex PAR flow settings, but participants will need to supply proposals for any additional reliability needs created by such an adjustment they assume in their analysis.
35-GD-S2-S9 | 218307 | ALDENE_2 | 218430 | STANTER_1 | 1 | 230/230 | 231/231 | 558 | 98.77 | 100.59 | 'PS_P1-2_G-2285/* ALDENE TO SPRINGFIELD ROAD' | Single | Yes | Overload may be able to be relieved through modification of the Essex PAR flow settings, but participants will need to supply proposals for any additional reliability needs created by such an adjustment they assume in their analysis.
35-GD-S2-S8A | 227900 | CARDIFF C | 219100 | NEWFRDM | 1 | 230/230 | 234/231 | 692 | 101 | 102.34 | 'JC-P7-1-JCC-230-13' | Tower | Yes | Previously missed and added on 8/27/2021.
35-GD-S2-S8B | 218345 | ALDENE_6 | 216911 | SPRINGRD_3 | 1 | 230/230 | 231/231 | 479 | 99.2 | 100.83 | BASE CASE | Single | Yes | Previously missed and added on 8/27/2021.