## Summary
2028 RTEP PJM Generation Deliverability Result (Winter)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor Rating (MVA) | PJM Accepting Proposals | Comment
28-GD-S2-W82 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3700 | 4825 | 4687 | 130.4 | 126.68 | TS_P1-2_#T6 | Single | WN/WE = 3592/4290 | Yes
28-GD-S2-W83 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3700 | 4583.6 | 4457.9 | 123.88 | 120.48 | TS_P1-3_#T2_FUR RUN 500_230 | Single | WN/WE = 3592/4290 | Yes
28-GD-S2-W1 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3700 | 4580 | 4425 | 123.78 | 119.59 | TS_P4_#T7_FUR RUN 500_CB 3 | Breaker | WN/WE = 3592/4290 | Yes
28-GD-S2-W2 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3700 | 4578.9 | 4425 | 123.75 | 119.59 | TS_P4_#T6_FUR RUN 500_CB 2 | Breaker | WN/WE = 3592/4290 | Yes
28-GD-S2-W3 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3700 | 4579.5 | 4424.7 | 123.77 | 119.59 | TS_P4_#T5_FUR RUN 500_CB 1 | Breaker | WN/WE = 3592/4290 | Yes
28-GD-S2-W137 | 227900 | CARDIFF C | 219100 | NEWFRDM | 1 | 230 | 231/234 | 692 | 832.7 | 810.4 | 120.33 | 117.11 | JC-P7-1-JCC-230-13 | Tower | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W84 | 270072 | FUR RUN_500 | 270073 | FUR RUN_230 | 1 | 500/230 | 225 | 1348 | 1558.4 | 1559.5 | 115.6 | 115.69 | PECO_P1-2_5012/* $ CHESCO $ PECO_P1-2_5012 $ L | Single | N/A | Yes
28-GD-S2-W85 | 270072 | FUR RUN_500 | 270073 | FUR RUN_230 | 2 | 500/230 | 225 | 1348 | 1558.4 | 1559.5 | 115.6 | 115.69 | PECO_P1-2_5012/* $ CHESCO $ PECO_P1-2_5012 $ L | Single | N/A | Yes
28-GD-S2-W138 | 232104 | MT PLSNT | 232106 | MIDLTNTP | 1 | 138 | 235 | 392 | 428.5 | 450.4 | 109.3 | 114.9 | DPL_P7_1_DBL_1NCB_FSA | Tower | N/A | No | Not resulting from addition of OSW.
28-GD-S2-W7 | 218306 | DEANS | 218304 | BRUNSWCK | 1 | 230 | 231 | 980 | 1086.3 | 1059.4 | 110.85 | 108.1 | PJM500_P2-3_BRBG5_3-4 | Breaker | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W6 | 218306 | DEANS | 218304 | BRUNSWCK | 1 | 230 | 231 | 980 | 1086.3 | 1059.4 | 110.85 | 108.1 | PJM500_PS_P2-3_BRBG5_4-5 | Breaker | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W86 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3700 | 4056.3 | 3963.2 | 109.63 | 107.11 | ME-P1-2-ME-500-007 | Single | WN/WE = 3592/4290 | Yes
28-GD-S2-W14 | 232014 | LSPWR CABLE | 232013 | SILVER RUN | 1 | 230 | 225 | 1150 | 1254.6 | 1218.9 | 109.09 | 105.99 | PJM500_DPL_P4_2_REDLION-HOPE AT51 | Breaker | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W15 | 232014 | LSPWR CABLE | 232013 | SILVER RUN | 1 | 230 | 225 | 1150 | 1252.3 | 1216.4 | 108.9 | 105.77 | PJM500_DPL_P4_2_REDLION-HOPE AT50 | Breaker | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W88 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3700 | 4012.5 | 3911 | 108.44 | 105.7 | TS_P1-2_#T2 | Single | WN/WE = 3592/4290 | Yes
28-GD-S2-W87 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3700 | 4012.5 | 3911 | 108.44 | 105.7 | TS_P1-2_#T3 | Single | WN/WE = 3592/4290 | Yes
28-GD-S2-W89 | 218333 | LNELSN_I | 218301 | MIDDLESEX_I | 1 | 230 | 231 | 819 | 851.3 | 855.1 | 103.94 | 104.41 | PS_P1-2_#2LINE_LT | Single | WN/WE = 805/1031 | Yes
28-GD-S2-W90 | 218345 | ALDENE_6 | 216911 | SPRINGRD_3 | 1 | 230 | 231 | 522 | 529.6 | 541.9 | 101.46 | 103.8 | Base Case | Single | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W91 | 232012 | HOPE CREEK | 232014 | LSPWR CABLE | 1 | 230 | 225 | 575 | 612.5 | 596 | 106.51 | 103.65 | PJM500_PS_P1-2_5015 | Single | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W92 | 232012 | HOPE CREEK | 232014 | LSPWR CABLE | 2 | 230 | 225 | 575 | 612.5 | 596 | 106.51 | 103.65 | PJM500_PS_P1-2_5015 | Single | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W93 | 232014 | LSPWR CABLE | 232013 | SILVER RUN | 1 | 230 | 225 | 1150 | 1224.6 | 1191 | 106.48 | 103.57 | PJM500_PS_P1-2_5015 | Single | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W94 | 218306 | DEANS | 218304 | BRUNSWCK | 1 | 230 | 231 | 980 | 1040.9 | 1013.3 | 106.21 | 103.4 | PS_P1-2_Z-2331_LT | Single | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W95 | 214277 | RICHMOND35 | 214012 | WANEETA3 | 1 | 230 | 230 | 803 | 849.9 | 830 | 105.84 | 103.37 | Base Case | Single | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W96 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3464 | 3662.4 | 3573 | 105.73 | 103.15 | Base Case | Single | WN/WE = 3592/4290 | Yes
28-GD-S2-W97 | 218306 | DEANS | 218304 | BRUNSWCK | 1 | 230 | 231 | 980 | 1027.4 | 1007.2 | 104.84 | 102.78 | PJM500_PS_P1-2_5019 | Single | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W98 | 218306 | DEANS | 218304 | BRUNSWCK | 1 | 230 | 231 | 980 | 1030.3 | 1003 | 105.14 | 102.35 | PS_P1-2_Z-2331 | Single | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W99 | 200066 | PCHBTM1N | 270072 | FUR RUN_500 | 1 | 500 | 230/225 | 4323 | 4516.6 | 4421 | 104.48 | 102.27 | PECO_P1-2_5012/* $ CHESCO $ PECO_P1-2_5012 $ L | Single | WN/WE = 3592/4403 | Yes
28-GD-S2-W140 | 227900 | CARDIFF C | 219100 | NEWFRDM | 1 | 230 | 231/234 | 692 | 716.1 | 700.3 | 103.49 | 101.2 | AE_P7-1 AE15TOWER | Tower | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W100 | 270073 | FUR RUN_230 | 220963 | CONASTON | 2 | 230 | 232/225 | 1534 | 1557.9 | 1551 | 101.56 | 101.11 | PECO_P1-2_5012/* $ CHESCO $ PECO_P1-2_5012 $ L | Single | WN/WE= 1677/1677 | Yes
28-GD-S2-W101 | 270073 | FUR RUN_230 | 220963 | CONASTON | 1 | 230 | 232/225 | 1534 | 1557.9 | 1551 | 101.56 | 101.11 | PECO_P1-2_5012/* $ CHESCO $ PECO_P1-2_5012 $ L | Single | WN/WE= 1677/1677 | Yes
28-GD-S2-W141 | 227900 | CARDIFF C | 219100 | NEWFRDM | 1 | 230 | 231/234 | 692 | 711.3 | 695.7 | 102.78 | 100.53 | AE_P7-1 AE14TOWER | Tower | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W142 | 227900 | CARDIFF C | 219100 | NEWFRDM | 1 | 230 | 231/234 | 692 | 708.3 | 692.9 | 102.36 | 100.12 | AE_P7-1 AE13TOWER | Tower | Conductor Rating is the same as basecase model | Yes
28-GD-S2-W102 | 218333 | LNELSN_I | 218301 | MIDDLESEX_I | 1 | 230 | 231 | 819 | 815.9 | 820 | 99.62 | 100.12 | JC-P1-2-JCC-230-003T | Single | WN/WE = 805/1031 | Yes